## GNA - Bank & Feeder Capacity
PG&E 2023 Grid Needs Assessment (GNA)
Appendix E: GNA Results - Bank & Feeder Capacity Needs
Version Date: 8/15/2023
Public
Facility Information | [5 empty] | Distribution Service |  |  | Peak Deficiency and Loading |  |  | 2023 |  |  |  |  | 2024 |  |  |  |  | 2025 |  |  |  |  | 2026 |  |  |  |  | 2027
GNA NEED ID | Distribution Planning Regions | Division | Facility Name | Facility ID formatted | Facility Type | Primary Driver | Distribution Service Required | Anticipated Need Date | Peak Facility Loading (%) 2023- 2027 | Peak Facility Deficiency (MW) 2023- 2027 | Peak Facility Deficiency (%) 2023- 2027 | Facility Rating (MW) | Facility Loading (MW) | Facility Loading (%) | Deficiency (MW) | Deficiency (%) | Facility Rating (MW) | Facility Loading (MW) | Facility Loading (%) | Deficiency (MW) | Deficiency (%) | Facility Rating (MW) | Facility Loading (MW) | Facility Loading (%) | Deficiency (MW) | Deficiency (%) | Facility Rating (MW) | Facility Loading (MW) | Facility Loading (%) | Deficiency (MW) | Deficiency (%) | Facility Rating (MW) | Facility Loading (MW) | Facility Loading (%) | Deficiency (MW) | Deficiency (%)
GNA_1822901_Capacity | South Bay and Central Coast | Central Coast | HATTON BANK 1 | 1822901 | Bank | None | None | None | 82.39% | 0 | 0% | 15.05 | 11.01 | 73.16% | 0 | 0% | 15.05 | 11.3 | 75.08% | 0 | 0% | 15.05 | 11.58 | 76.94% | 0 | 0% | 15.05 | 12.01 | 79.8% | 0 | 0% | 15.05 | 12.4 | 82.39% | 0 | 0%
GNA_182291101_Capacity | South Bay and Central Coast | Central Coast | HATTON 1101 | 182291101 | Feeder | None | None | None | 69.07% | 0 | 0% | 11.38 | 7.16 | 62.92% | 0 | 0% | 11.38 | 7.3 | 64.15% | 0 | 0% | 11.38 | 7.44 | 65.38% | 0 | 0% | 11.38 | 7.67 | 67.4% | 0 | 0% | 11.38 | 7.86 | 69.07% | 0 | 0%
GNA_182291102_Capacity | South Bay and Central Coast | Central Coast | HATTON 1102 | 182291102 | Feeder | None | None | None | 42.22% | 0 | 0% | 11.82 | 4.28 | 36.21% | 0 | 0% | 11.82 | 4.38 | 37.06% | 0 | 0% | 11.82 | 4.52 | 38.24% | 0 | 0% | 11.82 | 4.76 | 40.27% | 0 | 0% | 11.82 | 4.99 | 42.22% | 0 | 0%
GNA_1823701_Capacity | South Bay and Central Coast | Central Coast | LAURELES BANK 1 | 1823701 | Bank | None | None | None | 100% | 0 | 0% | 6.49 | 6.15 | 94.76% | 0 | 0% | 6.49 | 6.32 | 97.38% | 0 | 0% | 6.49 | 6.49 | 100% | 0 | 0% | 6.49 | 6.15 | 94.76% | 0 | 0% | 6.49 | 6.47 | 99.69% | 0 | 0%
GNA_182371111_Capacity | South Bay and Central Coast | Central Coast | LAURELES 1111 | 182371111 | Feeder | None | None | None | 35.83% | 0 | 0% | 10.16 | 3.1 | 30.51% | 0 | 0% | 10.16 | 3.22 | 31.69% | 0 | 0% | 10.16 | 3.33 | 32.78% | 0 | 0% | 10.16 | 3.48 | 34.25% | 0 | 0% | 10.16 | 3.64 | 35.83% | 0 | 0%
GNA_182371112_Capacity | South Bay and Central Coast | Central Coast | LAURELES 1112 | 182371112 | Feeder | None | None | None | 38.39% | 0 | 0% | 10.16 | 3.74 | 36.81% | 0 | 0% | 10.16 | 3.81 | 37.5% | 0 | 0% | 10.16 | 3.9 | 38.39% | 0 | 0% | 10.16 | 3.39 | 33.37% | 0 | 0% | 10.16 | 3.5 | 34.45% | 0 | 0%
GNA_1829401_Capacity | South Bay and Central Coast | Central Coast | OTTER BANK 1 | 1829401 | Bank | None | None | None | 50.28% | 0 | 0% | 8.99 | 3.59 | 39.93% | 0 | 0% | 8.99 | 4.08 | 45.38% | 0 | 0% | 8.99 | 4.2 | 46.72% | 0 | 0% | 8.99 | 4.36 | 48.5% | 0 | 0% | 8.99 | 4.52 | 50.28% | 0 | 0%
GNA_182941101_Capacity | South Bay and Central Coast | Central Coast | OTTER 1101 | 182941101 | Feeder | None | None | None | 26.15% | 0 | 0% | 6.5 | 1.2 | 18.46% | 0 | 0% | 6.5 | 1.31 | 20.15% | 0 | 0% | 6.5 | 1.42 | 21.85% | 0 | 0% | 6.5 | 1.56 | 24% | 0 | 0% | 6.5 | 1.7 | 26.15% | 0 | 0%
GNA_182941102_Capacity | South Bay and Central Coast | Central Coast | OTTER 1102 | 182941102 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1820702_Capacity | South Bay and Central Coast | Central Coast | CAMPHORA BANK 2 | 1820702 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182071101_Capacity | South Bay and Central Coast | Central Coast | CAMPHORA 1101 | 182071101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1821303_Capacity | South Bay and Central Coast | Central Coast | GONZALES BANK 3 | 1821303 | Bank | None | None | None | 87.88% | 0 | 0% | 6.6 | 5.41 | 81.97% | 0 | 0% | 6.6 | 5.5 | 83.33% | 0 | 0% | 6.6 | 5.6 | 84.85% | 0 | 0% | 6.6 | 5.7 | 86.36% | 0 | 0% | 6.6 | 5.8 | 87.88% | 0 | 0%
GNA_182131101_Capacity | South Bay and Central Coast | Central Coast | GONZALES 1101 | 182131101 | Feeder | None | None | None | 63.16% | 0 | 0% | 8.55 | 5.01 | 58.6% | 0 | 0% | 8.55 | 5.1 | 59.65% | 0 | 0% | 8.55 | 5.2 | 60.82% | 0 | 0% | 8.55 | 5.3 | 61.99% | 0 | 0% | 8.55 | 5.4 | 63.16% | 0 | 0%
GNA_182131102_Capacity | South Bay and Central Coast | Central Coast | GONZALES 1102 | 182131102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1821304_Capacity | South Bay and Central Coast | Central Coast | GONZALES BANK 4 | 1821304 | Bank | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182131103_Capacity | South Bay and Central Coast | Central Coast | GONZALES 1103 | 182131103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182131104_Capacity | South Bay and Central Coast | Central Coast | GONZALES 1104 | 182131104 | Feeder | None | None | None | 71.7% | 0 | 0% | 12.19 | 7.26 | 59.56% | 0 | 0% | 12.19 | 8.5 | 69.73% | 0 | 0% | 12.19 | 8.58 | 70.39% | 0 | 0% | 12.19 | 8.65 | 70.96% | 0 | 0% | 12.19 | 8.74 | 71.7% | 0 | 0%
GNA_1824901_Capacity | South Bay and Central Coast | Central Coast | HOLLISTER BANK 1 | 1824901 | Bank | None | None | None | 71.85% | 0 | 0% | 24.8 | 17.82 | 71.85% | 0 | 0% | 24.8 | 16.96 | 68.39% | 0 | 0% | 24.8 | 16.99 | 68.51% | 0 | 0% | 24.8 | 17.16 | 69.19% | 0 | 0% | 24.8 | 17.4 | 70.16% | 0 | 0%
GNA_182492101_Capacity | South Bay and Central Coast | Central Coast | HOLLISTER 2101 | 182492101 | Feeder | None | None | None | 60.24% | 0 | 0% | 18.11 | 10.91 | 60.24% | 0 | 0% | 18.11 | 10.27 | 56.71% | 0 | 0% | 18.11 | 10.46 | 57.76% | 0 | 0% | 18.11 | 10.64 | 58.75% | 0 | 0% | 18.11 | 10.86 | 59.97% | 0 | 0%
GNA_182492102_Capacity | South Bay and Central Coast | Central Coast | HOLLISTER 2102 | 182492102 | Feeder | None | None | None | 77.78% | 0 | 0% | 12.15 | 9.45 | 77.78% | 0 | 0% | 12.15 | 9.42 | 77.53% | 0 | 0% | 12.15 | 9.37 | 77.12% | 0 | 0% | 12.15 | 9.33 | 76.79% | 0 | 0% | 12.15 | 9.31 | 76.63% | 0 | 0%
GNA_1824902_Capacity | South Bay and Central Coast | Central Coast | HOLLISTER BANK 2 | 1824902 | Bank | None | None | None | 86.13% | 0 | 0% | 24.73 | 18.53 | 74.93% | 0 | 0% | 24.73 | 21.3 | 86.13% | 0 | 0% | 24.73 | 19.59 | 79.22% | 0 | 0% | 24.73 | 19.82 | 80.15% | 0 | 0% | 24.73 | 20.13 | 81.4% | 0 | 0%
GNA_182492103_Capacity | South Bay and Central Coast | Central Coast | HOLLISTER 2103 | 182492103 | Feeder | Demand Growth | Capacity | 2024 | 101.6% | 0.33 | 1.563% | 21.11 | 18.67 | 88.44% | 0 | 0% | 21.11 | 21.44 | 101.6% | 0.33 | 1.563% | 21.11 | 19.73 | 93.46% | 0 | 0% | 21.11 | 19.96 | 94.55% | 0 | 0% | 21.11 | 20.27 | 96.02% | 0 | 0%
GNA_1824903_Capacity | South Bay and Central Coast | Central Coast | HOLLISTER BANK 3 | 1824903 | Bank | Demand Growth | Capacity | 2023 | 156% | 24.97 | 56.05% | 44.55 | 50.11 | 112.5% | 5.56 | 12.48% | 44.55 | 60.6 | 136% | 16.05 | 36.03% | 44.55 | 68.13 | 152.9% | 23.58 | 52.93% | 44.55 | 68.81 | 154.5% | 24.26 | 54.46% | 44.55 | 69.52 | 156% | 24.97 | 56.05%
GNA_182492104_Capacity | South Bay and Central Coast | Central Coast | HOLLISTER 2104 | 182492104 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182492105_Capacity | South Bay and Central Coast | Central Coast | HOLLISTER 2105 | 182492105 | Feeder | None | None | None | 88.73% | 0 | 0% | 21.11 | 14.79 | 70.06% | 0 | 0% | 21.11 | 16.91 | 80.1% | 0 | 0% | 21.11 | 18.2 | 86.22% | 0 | 0% | 21.11 | 18.43 | 87.3% | 0 | 0% | 21.11 | 18.73 | 88.73% | 0 | 0%
GNA_182492106_Capacity | South Bay and Central Coast | Central Coast | HOLLISTER 2106 | 182492106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1827401_Capacity | South Bay and Central Coast | Central Coast | SAN BENITO BANK 1 | 1827401 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182742101_Capacity | South Bay and Central Coast | Central Coast | SAN BENITO 2101 | 182742101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182742102_Capacity | South Bay and Central Coast | Central Coast | SAN BENITO 2102 | 182742102 | Feeder | None | None | None | 41.78% | 0 | 0% | 11.44 | 4.78 | 41.78% | 0 | 0% | 11.44 | 4.71 | 41.17% | 0 | 0% | 11.44 | 4.67 | 40.82% | 0 | 0% | 11.44 | 4.6 | 40.21% | 0 | 0% | 11.44 | 4.54 | 39.69% | 0 | 0%
GNA_182742104_Capacity | South Bay and Central Coast | Central Coast | SAN BENITO 2104 | 182742104 | Feeder | None | None | None | 35.49% | 0 | 0% | 11.44 | 2.66 | 23.25% | 0 | 0% | 11.44 | 3.99 | 34.88% | 0 | 0% | 11.44 | 3.98 | 34.79% | 0 | 0% | 11.44 | 4.01 | 35.05% | 0 | 0% | 11.44 | 4.06 | 35.49% | 0 | 0%
GNA_1829801_Capacity | South Bay and Central Coast | Central Coast | JOLON BANK 1 | 1829801 | Bank | None | None | None | 25.69% | 0 | 0% | 8.64 | 2.21 | 25.58% | 0 | 0% | 8.64 | 2.2 | 25.46% | 0 | 0% | 8.64 | 2.21 | 25.58% | 0 | 0% | 8.64 | 2.22 | 25.69% | 0 | 0% | 8.64 | 2.22 | 25.69% | 0 | 0%
GNA_182981102_Capacity | South Bay and Central Coast | Central Coast | JOLON 1102 | 182981102 | Feeder | None | None | None | 30.41% | 0 | 0% | 8.55 | 2.6 | 30.41% | 0 | 0% | 8.55 | 2.59 | 30.29% | 0 | 0% | 8.55 | 2.6 | 30.41% | 0 | 0% | 8.55 | 2.6 | 30.41% | 0 | 0% | 8.55 | 2.6 | 30.41% | 0 | 0%
GNA_1829802_Capacity | South Bay and Central Coast | Central Coast | JOLON BANK 2 | 1829802 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182981103_Capacity | South Bay and Central Coast | Central Coast | JOLON 1103 | 182981103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1820301_Capacity | South Bay and Central Coast | Central Coast | KING CITY BANK 1 | 1820301 | Bank | None | None | None | 89.7% | 0 | 0% | 10 | 8.67 | 86.7% | 0 | 0% | 10 | 8.75 | 87.5% | 0 | 0% | 10 | 8.83 | 88.3% | 0 | 0% | 10 | 8.9 | 89% | 0 | 0% | 10 | 8.97 | 89.7% | 0 | 0%
GNA_182031105_Capacity | South Bay and Central Coast | Central Coast | KING CITY 1105 | 182031105 | Feeder | None | None | None | 38.51% | 0 | 0% | 10.05 | 3.46 | 34.43% | 0 | 0% | 10.05 | 3.57 | 35.52% | 0 | 0% | 10.05 | 3.67 | 36.52% | 0 | 0% | 10.05 | 3.78 | 37.61% | 0 | 0% | 10.05 | 3.87 | 38.51% | 0 | 0%
GNA_182031106_Capacity | South Bay and Central Coast | Central Coast | KING CITY 1106 | 182031106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1820303_Capacity | South Bay and Central Coast | Central Coast | KING CITY BANK 3 | 1820303 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182031101_Capacity | South Bay and Central Coast | Central Coast | KING CITY 1101 | 182031101 | Feeder | None | None | None | 49.81% | 0 | 0% | 10.46 | 5.17 | 49.43% | 0 | 0% | 10.46 | 5.18 | 49.52% | 0 | 0% | 10.46 | 5.19 | 49.62% | 0 | 0% | 10.46 | 5.2 | 49.71% | 0 | 0% | 10.46 | 5.21 | 49.81% | 0 | 0%
GNA_182031102_Capacity | South Bay and Central Coast | Central Coast | KING CITY 1102 | 182031102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182031103_Capacity | South Bay and Central Coast | Central Coast | KING CITY 1103 | 182031103 | Feeder | None | None | None | 38.89% | 0 | 0% | 12.83 | 4.59 | 35.78% | 0 | 0% | 12.83 | 4.71 | 36.71% | 0 | 0% | 12.83 | 4.8 | 37.41% | 0 | 0% | 12.83 | 4.89 | 38.11% | 0 | 0% | 12.83 | 4.99 | 38.89% | 0 | 0%
GNA_182031104_Capacity | South Bay and Central Coast | Central Coast | KING CITY 1104 | 182031104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1821901_Capacity | South Bay and Central Coast | Central Coast | SAN ARDO BANK 1 | 1821901 | Bank | None | None | None | 89.57% | 0 | 0% | 9.88 | 8.85 | 89.57% | 0 | 0% | 9.88 | 8.84 | 89.47% | 0 | 0% | 9.88 | 8.83 | 89.37% | 0 | 0% | 9.88 | 8.83 | 89.37% | 0 | 0% | 9.88 | 8.81 | 89.17% | 0 | 0%
GNA_182191101_Capacity | South Bay and Central Coast | Central Coast | SAN ARDO 1101 | 182191101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182191102_Capacity | South Bay and Central Coast | Central Coast | SAN ARDO 1102 | 182191102 | Feeder | None | None | None | 49.1% | 0 | 0% | 11.67 | 5.73 | 49.1% | 0 | 0% | 11.67 | 5.72 | 49.01% | 0 | 0% | 11.67 | 5.72 | 49.01% | 0 | 0% | 11.67 | 5.72 | 49.01% | 0 | 0% | 11.67 | 5.71 | 48.93% | 0 | 0%
GNA_1822201_Capacity | South Bay and Central Coast | Central Coast | DEL MONTE BANK 1 | 1822201 | Bank | None | None | None | 64.65% | 0 | 0% | 44.56 | 27.66 | 62.07% | 0 | 0% | 44.56 | 27.84 | 62.48% | 0 | 0% | 44.56 | 28.08 | 63.02% | 0 | 0% | 44.56 | 28.43 | 63.8% | 0 | 0% | 44.56 | 28.81 | 64.65% | 0 | 0%
GNA_1822209_Capacity | South Bay and Central Coast | Central Coast | DEL MONTE BANK 9 | 1822209 | Bank | None | None | None | 47.41% | 0 | 0% | 9.28 | 4.18 | 45.04% | 0 | 0% | 9.28 | 4.22 | 45.47% | 0 | 0% | 9.28 | 4.28 | 46.12% | 0 | 0% | 9.28 | 4.32 | 46.55% | 0 | 0% | 9.28 | 4.4 | 47.41% | 0 | 0%
GNA_182222102_Capacity | South Bay and Central Coast | Central Coast | DEL MONTE 2102 | 182222102 | Feeder | None | None | None | 87.17% | 0 | 0% | 17.3 | 14.92 | 86.24% | 0 | 0% | 17.3 | 14.87 | 85.95% | 0 | 0% | 17.3 | 14.85 | 85.84% | 0 | 0% | 17.3 | 14.98 | 86.59% | 0 | 0% | 17.3 | 15.08 | 87.17% | 0 | 0%
GNA_182222103_Capacity | South Bay and Central Coast | Central Coast | DEL MONTE 2103 | 182222103 | Feeder | None | None | None | 52.79% | 0 | 0% | 20.44 | 10.2 | 49.9% | 0 | 0% | 20.44 | 10.3 | 50.39% | 0 | 0% | 20.44 | 10.41 | 50.93% | 0 | 0% | 20.44 | 10.58 | 51.76% | 0 | 0% | 20.44 | 10.79 | 52.79% | 0 | 0%
GNA_1822202_Capacity | South Bay and Central Coast | Central Coast | DEL MONTE BANK 2 | 1822202 | Bank | Demand Growth | Capacity | 2026 | 108.9% | 2.37 | 8.883% | 26.68 | 25.5 | 95.58% | 0 | 0% | 26.68 | 25.98 | 97.38% | 0 | 0% | 26.68 | 26.54 | 99.48% | 0 | 0% | 26.68 | 28.06 | 105.2% | 1.38 | 5.172% | 26.68 | 29.05 | 108.9% | 2.37 | 8.883%
GNA_182222104_Capacity | South Bay and Central Coast | Central Coast | DEL MONTE 2104 | 182222104 | Feeder | None | None | None | 66.56% | 0 | 0% | 21.11 | 11.82 | 55.99% | 0 | 0% | 21.11 | 12.13 | 57.46% | 0 | 0% | 21.11 | 12.41 | 58.79% | 0 | 0% | 21.11 | 13.54 | 64.14% | 0 | 0% | 21.11 | 14.05 | 66.56% | 0 | 0%
GNA_182222105_Capacity | South Bay and Central Coast | Central Coast | DEL MONTE 2105 | 182222105 | Feeder | None | None | None | 69.98% | 0 | 0% | 22.22 | 14.29 | 64.31% | 0 | 0% | 22.22 | 14.47 | 65.12% | 0 | 0% | 22.22 | 14.69 | 66.11% | 0 | 0% | 22.22 | 15.08 | 67.87% | 0 | 0% | 22.22 | 15.55 | 69.98% | 0 | 0%
GNA_1824401_Capacity | South Bay and Central Coast | Central Coast | PACIFIC GROVE BANK 1 | 1824401 | Bank | None | None | None | 41.01% | 0 | 0% | 4.95 | 1.85 | 37.37% | 0 | 0% | 4.95 | 1.87 | 37.78% | 0 | 0% | 4.95 | 1.91 | 38.59% | 0 | 0% | 4.95 | 1.95 | 39.39% | 0 | 0% | 4.95 | 2.03 | 41.01% | 0 | 0%
GNA_182440421_Capacity | South Bay and Central Coast | Central Coast | PACIFIC GROVE 0421 | 182440421 | Feeder | None | None | None | 43.36% | 0 | 0% | 3.69 | 1.49 | 40.38% | 0 | 0% | 3.69 | 1.5 | 40.65% | 0 | 0% | 3.69 | 1.53 | 41.46% | 0 | 0% | 3.69 | 1.55 | 42.01% | 0 | 0% | 3.69 | 1.6 | 43.36% | 0 | 0%
GNA_182440423_Capacity | South Bay and Central Coast | Central Coast | PACIFIC GROVE 0423 | 182440423 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1824402_Capacity | South Bay and Central Coast | Central Coast | PACIFIC GROVE BANK 2 | 1824402 | Bank | None | None | None | 52.8% | 0 | 0% | 5.53 | 2.56 | 46.29% | 0 | 0% | 5.53 | 2.62 | 47.38% | 0 | 0% | 5.53 | 2.68 | 48.46% | 0 | 0% | 5.53 | 2.78 | 50.27% | 0 | 0% | 5.53 | 2.92 | 52.8% | 0 | 0%
GNA_182440422_Capacity | South Bay and Central Coast | Central Coast | PACIFIC GROVE 0422 | 182440422 | Feeder | None | None | None | 38.44% | 0 | 0% | 3.33 | 1.14 | 34.23% | 0 | 0% | 3.33 | 1.16 | 34.83% | 0 | 0% | 3.33 | 1.18 | 35.44% | 0 | 0% | 3.33 | 1.22 | 36.64% | 0 | 0% | 3.33 | 1.28 | 38.44% | 0 | 0%
GNA_182440424_Capacity | South Bay and Central Coast | Central Coast | PACIFIC GROVE 0424 | 182440424 | Feeder | None | None | None | 48.65% | 0 | 0% | 3.33 | 1.4 | 42.04% | 0 | 0% | 3.33 | 1.44 | 43.24% | 0 | 0% | 3.33 | 1.48 | 44.44% | 0 | 0% | 3.33 | 1.53 | 45.95% | 0 | 0% | 3.33 | 1.62 | 48.65% | 0 | 0%
GNA_1828501_Capacity | South Bay and Central Coast | Central Coast | VIEJO BANK 1 | 1828501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182852201_Capacity | South Bay and Central Coast | Central Coast | VIEJO 2201 | 182852201 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182852202_Capacity | South Bay and Central Coast | Central Coast | VIEJO 2202 | 182852202 | Feeder | None | None | None | 51.92% | 0 | 0% | 21.11 | 9.3 | 44.05% | 0 | 0% | 21.11 | 9.62 | 45.57% | 0 | 0% | 21.11 | 9.93 | 47.04% | 0 | 0% | 21.11 | 10.37 | 49.12% | 0 | 0% | 21.11 | 10.96 | 51.92% | 0 | 0%
GNA_1828502_Capacity | South Bay and Central Coast | Central Coast | VIEJO BANK 2 | 1828502 | Bank | None | None | None | 55.76% | 0 | 0% | 29.7 | 15.27 | 51.41% | 0 | 0% | 29.7 | 15.47 | 52.09% | 0 | 0% | 29.7 | 15.7 | 52.86% | 0 | 0% | 29.7 | 16.02 | 53.94% | 0 | 0% | 29.7 | 16.56 | 55.76% | 0 | 0%
GNA_182852203_Capacity | South Bay and Central Coast | Central Coast | VIEJO 2203 | 182852203 | Feeder | None | None | None | 34.44% | 0 | 0% | 20.44 | 6.31 | 30.87% | 0 | 0% | 20.44 | 6.4 | 31.31% | 0 | 0% | 20.44 | 6.54 | 32% | 0 | 0% | 20.44 | 6.72 | 32.88% | 0 | 0% | 20.44 | 7.04 | 34.44% | 0 | 0%
GNA_182852204_Capacity | South Bay and Central Coast | Central Coast | VIEJO 2204 | 182852204 | Feeder | None | None | None | 51.57% | 0 | 0% | 20.44 | 9.99 | 48.87% | 0 | 0% | 20.44 | 10.1 | 49.41% | 0 | 0% | 20.44 | 10.18 | 49.8% | 0 | 0% | 20.44 | 10.33 | 50.54% | 0 | 0% | 20.44 | 10.54 | 51.57% | 0 | 0%
GNA_1823901_Capacity | South Bay and Central Coast | Central Coast | OILFIELDS BANK 1 | 1823901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182391102_Capacity | South Bay and Central Coast | Central Coast | OILFIELDS 1102 | 182391102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1823902_Capacity | South Bay and Central Coast | Central Coast | OILFIELDS BANK 2 | 1823902 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182391103_Capacity | South Bay and Central Coast | Central Coast | OILFIELDS 1103 | 182391103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182391104_Capacity | South Bay and Central Coast | Central Coast | OILFIELDS 1104 | 182391104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0829301_Capacity | South Bay and Central Coast | Central Coast | POINT MORETTI BANK 1 | 829301 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082931101_Capacity | South Bay and Central Coast | Central Coast | POINT MORETTI 1101 | 82931101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1823501_Capacity | South Bay and Central Coast | Central Coast | CASTROVILLE BANK 1 | 1823501 | Bank | Demand Growth | Capacity | 2024 | 109.4% | 2.64 | 9.378% | 28.15 | 27.46 | 97.55% | 0 | 0% | 28.15 | 30.08 | 106.9% | 1.93 | 6.856% | 28.15 | 30.28 | 107.6% | 2.13 | 7.567% | 28.15 | 30.51 | 108.4% | 2.36 | 8.384% | 28.15 | 30.79 | 109.4% | 2.64 | 9.378%
GNA_182352103_Capacity | South Bay and Central Coast | Central Coast | CASTROVILLE 2103 | 182352103 | Feeder | None | None | None | 68.5% | 0 | 0% | 22.22 | 14.72 | 66.25% | 0 | 0% | 22.22 | 14.8 | 66.61% | 0 | 0% | 22.22 | 14.89 | 67.01% | 0 | 0% | 22.22 | 15.04 | 67.69% | 0 | 0% | 22.22 | 15.22 | 68.5% | 0 | 0%
GNA_182352104_Capacity | South Bay and Central Coast | Central Coast | CASTROVILLE 2104 | 182352104 | Feeder | None | None | None | 91.99% | 0 | 0% | 22.22 | 17.73 | 79.79% | 0 | 0% | 22.22 | 20.23 | 91.04% | 0 | 0% | 22.22 | 20.3 | 91.36% | 0 | 0% | 22.22 | 20.37 | 91.67% | 0 | 0% | 22.22 | 20.44 | 91.99% | 0 | 0%
GNA_1823801_Capacity | South Bay and Central Coast | Central Coast | DOLAN ROAD BANK 1 | 1823801 | Bank | Demand Growth | Capacity | 2023 | 158.7% | 5.81 | 58.69% | 9.9 | 15.43 | 155.9% | 5.53 | 55.86% | 9.9 | 15.46 | 156.2% | 5.56 | 56.16% | 9.9 | 15.49 | 156.5% | 5.59 | 56.46% | 9.9 | 15.58 | 157.4% | 5.68 | 57.37% | 9.9 | 15.71 | 158.7% | 5.81 | 58.69%
GNA_182381101_Capacity | South Bay and Central Coast | Central Coast | DOLAN ROAD 1101 | 182381101 | Feeder | None | None | None | 40.47% | 0 | 0% | 8.13 | 3.02 | 37.15% | 0 | 0% | 8.13 | 3.04 | 37.39% | 0 | 0% | 8.13 | 3.07 | 37.76% | 0 | 0% | 8.13 | 3.15 | 38.75% | 0 | 0% | 8.13 | 3.29 | 40.47% | 0 | 0%
GNA_182381102_Capacity | South Bay and Central Coast | Central Coast | DOLAN ROAD 1102 | 182381102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1823802_Capacity | South Bay and Central Coast | Central Coast | DOLAN ROAD BANK 2 | 1823802 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182381103_Capacity | South Bay and Central Coast | Central Coast | DOLAN ROAD 1103 | 182381103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182381104_Capacity | South Bay and Central Coast | Central Coast | DOLAN ROAD 1104 | 182381104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1829602_Capacity | South Bay and Central Coast | Central Coast | PRUNEDALE BANK 2 | 1829602 | Bank | None | None | None | 74.43% | 0 | 0% | 15.8 | 11.58 | 73.29% | 0 | 0% | 15.8 | 11.58 | 73.29% | 0 | 0% | 15.8 | 11.59 | 73.35% | 0 | 0% | 15.8 | 11.66 | 73.8% | 0 | 0% | 15.8 | 11.76 | 74.43% | 0 | 0%
GNA_182961107_Capacity | South Bay and Central Coast | Central Coast | PRUNEDALE 1107 | 182961107 | Feeder | None | None | None | 96.1% | 0 | 0% | 11.8 | 11.17 | 94.66% | 0 | 0% | 11.8 | 11.17 | 94.66% | 0 | 0% | 11.8 | 11.18 | 94.75% | 0 | 0% | 11.8 | 11.24 | 95.25% | 0 | 0% | 11.8 | 11.34 | 96.1% | 0 | 0%
GNA_1829603_Capacity | South Bay and Central Coast | Central Coast | PRUNEDALE BANK 3 | 1829603 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182961110_Capacity | South Bay and Central Coast | Central Coast | PRUNEDALE 1110 | 182961110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1824601_Capacity | South Bay and Central Coast | Central Coast | BORONDA BANK 1 | 1824601 | Bank | Demand Growth | Capacity | 2026 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182461101_Capacity | South Bay and Central Coast | Central Coast | BORONDA 1101 | 182461101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182461102_Capacity | South Bay and Central Coast | Central Coast | BORONDA 1102 | 182461102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1822601_Capacity | South Bay and Central Coast | Central Coast | BUENA VISTA BANK 1 | 1822601 | Bank | None | None | None | 85.39% | 0 | 0% | 29.7 | 25.36 | 85.39% | 0 | 0% | 29.7 | 25.34 | 85.32% | 0 | 0% | 29.7 | 25.32 | 85.25% | 0 | 0% | 29.7 | 25.3 | 85.19% | 0 | 0% | 29.7 | 25.32 | 85.25% | 0 | 0%
GNA_182261101_Capacity | South Bay and Central Coast | Central Coast | BUENA VISTA 1101 | 182261101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182261102_Capacity | South Bay and Central Coast | Central Coast | BUENA VISTA 1102 | 182261102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182261106_Capacity | South Bay and Central Coast | Central Coast | BUENA VISTA 1106 | 182261106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1822603_Capacity | South Bay and Central Coast | Central Coast | BUENA VISTA BANK 3 | 1822603 | Bank | None | None | None | 64.38% | 0 | 0% | 29.7 | 18.66 | 62.83% | 0 | 0% | 29.7 | 18.76 | 63.16% | 0 | 0% | 29.7 | 18.79 | 63.27% | 0 | 0% | 29.7 | 19.01 | 64.01% | 0 | 0% | 29.7 | 19.12 | 64.38% | 0 | 0%
GNA_182261103_Capacity | South Bay and Central Coast | Central Coast | BUENA VISTA 1103 | 182261103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182261104_Capacity | South Bay and Central Coast | Central Coast | BUENA VISTA 1104 | 182261104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1823301_Capacity | South Bay and Central Coast | Central Coast | GABILAN BANK 1 | 1823301 | Bank | Demand Growth | Capacity | 2027 | 102.4% | 0.38 | 2.399% | 15.84 | 15.31 | 96.65% | 0 | 0% | 15.84 | 15.15 | 95.64% | 0 | 0% | 15.84 | 15.32 | 96.72% | 0 | 0% | 15.84 | 15.7 | 99.12% | 0 | 0% | 15.84 | 16.22 | 102.4% | 0.38 | 2.399%
GNA_182331101_Capacity | South Bay and Central Coast | Central Coast | GABILAN 1101 | 182331101 | Feeder | None | None | None | 89.99% | 0 | 0% | 12.19 | 10.97 | 89.99% | 0 | 0% | 12.19 | 10.94 | 89.75% | 0 | 0% | 12.19 | 10.91 | 89.5% | 0 | 0% | 12.19 | 10.9 | 89.42% | 0 | 0% | 12.19 | 10.95 | 89.83% | 0 | 0%
GNA_182331102_Capacity | South Bay and Central Coast | Central Coast | GABILAN 1102 | 182331102 | Feeder | None | None | None | 52.09% | 0 | 0% | 12.19 | 5.65 | 46.35% | 0 | 0% | 12.19 | 5.76 | 47.25% | 0 | 0% | 12.19 | 5.89 | 48.32% | 0 | 0% | 12.19 | 6.07 | 49.79% | 0 | 0% | 12.19 | 6.35 | 52.09% | 0 | 0%
GNA_1823001_Capacity | South Bay and Central Coast | Central Coast | INDUSTRIAL ACRES BANK 1 | 1823001 | Bank | None | None | None | 55.16% | 0 | 0% | 7.56 | 4.1 | 54.23% | 0 | 0% | 7.56 | 4.11 | 54.37% | 0 | 0% | 7.56 | 4.12 | 54.5% | 0 | 0% | 7.56 | 4.13 | 54.63% | 0 | 0% | 7.56 | 4.17 | 55.16% | 0 | 0%
GNA_182300411_Capacity | South Bay and Central Coast | Central Coast | INDUSTRIAL ACRES 0411 | 182300411 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182300412_Capacity | South Bay and Central Coast | Central Coast | INDUSTRIAL ACRES 0412 | 182300412 | Feeder | None | None | None | 90.65% | 0 | 0% | 2.14 | 1.86 | 86.92% | 0 | 0% | 2.14 | 1.88 | 87.85% | 0 | 0% | 2.14 | 1.9 | 88.79% | 0 | 0% | 2.14 | 1.91 | 89.25% | 0 | 0% | 2.14 | 1.94 | 90.65% | 0 | 0%
GNA_182300413_Capacity | South Bay and Central Coast | Central Coast | INDUSTRIAL ACRES 0413 | 182300413 | Feeder | None | None | None | 38.79% | 0 | 0% | 2.14 | 0.8 | 37.38% | 0 | 0% | 2.14 | 0.81 | 37.85% | 0 | 0% | 2.14 | 0.81 | 37.85% | 0 | 0% | 2.14 | 0.82 | 38.32% | 0 | 0% | 2.14 | 0.83 | 38.79% | 0 | 0%
GNA_182300415_Capacity | South Bay and Central Coast | Central Coast | INDUSTRIAL ACRES 0415 | 182300415 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1827301_Capacity | South Bay and Central Coast | Central Coast | RESERVATION ROAD BANK 1 | 1827301 | Bank | None | None | None | 39.07% | 0 | 0% | 29.69 | 10.6 | 35.7% | 0 | 0% | 29.69 | 10.81 | 36.41% | 0 | 0% | 29.69 | 11.03 | 37.15% | 0 | 0% | 29.69 | 11.29 | 38.03% | 0 | 0% | 29.69 | 11.6 | 39.07% | 0 | 0%
GNA_182731101_Capacity | South Bay and Central Coast | Central Coast | RESERVATION ROAD 1101 | 182731101 | Feeder | None | None | None | 37.18% | 0 | 0% | 12.83 | 4.29 | 33.44% | 0 | 0% | 12.83 | 4.38 | 34.14% | 0 | 0% | 12.83 | 4.5 | 35.07% | 0 | 0% | 12.83 | 4.64 | 36.17% | 0 | 0% | 12.83 | 4.77 | 37.18% | 0 | 0%
GNA_182731102_Capacity | South Bay and Central Coast | Central Coast | RESERVATION ROAD 1102 | 182731102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1820104_Capacity | South Bay and Central Coast | Central Coast | SALINAS BANK 4 | 1820104 | Bank | None | None | None | 72.31% | 0 | 0% | 44.5 | 32.18 | 72.31% | 0 | 0% | 44.5 | 31.81 | 71.48% | 0 | 0% | 44.5 | 31.66 | 71.15% | 0 | 0% | 44.5 | 31.66 | 71.15% | 0 | 0% | 44.5 | 31.85 | 71.57% | 0 | 0%
GNA_182011101_Capacity | South Bay and Central Coast | Central Coast | SALINAS 1101 | 182011101 | Feeder | None | None | None | 22.48% | 0 | 0% | 12.19 | 2.73 | 22.4% | 0 | 0% | 12.19 | 2.71 | 22.23% | 0 | 0% | 12.19 | 2.69 | 22.07% | 0 | 0% | 12.19 | 2.71 | 22.23% | 0 | 0% | 12.19 | 2.74 | 22.48% | 0 | 0%
GNA_182011102_Capacity | South Bay and Central Coast | Central Coast | SALINAS 1102 | 182011102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182011106_Capacity | South Bay and Central Coast | Central Coast | SALINAS 1106 | 182011106 | Feeder | None | None | None | 99.84% | 0 | 0% | 12.19 | 12.17 | 99.84% | 0 | 0% | 12.19 | 12.01 | 98.52% | 0 | 0% | 12.19 | 11.9 | 97.62% | 0 | 0% | 12.19 | 11.86 | 97.29% | 0 | 0% | 12.19 | 11.9 | 97.62% | 0 | 0%
GNA_182011107_Capacity | South Bay and Central Coast | Central Coast | SALINAS 1107 | 182011107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1820106_Capacity | South Bay and Central Coast | Central Coast | SALINAS BANK 6 | 1820106 | Bank | None | None | None | 98.65% | 0 | 0% | 44.54 | 41.12 | 92.32% | 0 | 0% | 44.54 | 41.54 | 93.26% | 0 | 0% | 44.54 | 42.04 | 94.39% | 0 | 0% | 44.54 | 42.86 | 96.23% | 0 | 0% | 44.54 | 43.94 | 98.65% | 0 | 0%
GNA_182011103_Capacity | South Bay and Central Coast | Central Coast | SALINAS 1103 | 182011103 | Feeder | None | None | None | 94.18% | 0 | 0% | 12.19 | 11.06 | 90.73% | 0 | 0% | 12.19 | 11.08 | 90.89% | 0 | 0% | 12.19 | 11.16 | 91.55% | 0 | 0% | 12.19 | 11.3 | 92.7% | 0 | 0% | 12.19 | 11.48 | 94.18% | 0 | 0%
GNA_182011104_Capacity | South Bay and Central Coast | Central Coast | SALINAS 1104 | 182011104 | Feeder | None | None | None | 73.75% | 0 | 0% | 12.19 | 8.57 | 70.3% | 0 | 0% | 12.19 | 8.6 | 70.55% | 0 | 0% | 12.19 | 8.63 | 70.8% | 0 | 0% | 12.19 | 8.78 | 72.03% | 0 | 0% | 12.19 | 8.99 | 73.75% | 0 | 0%
GNA_182011105_Capacity | South Bay and Central Coast | Central Coast | SALINAS 1105 | 182011105 | Feeder | None | None | None | 95.35% | 0 | 0% | 11.82 | 10.25 | 86.72% | 0 | 0% | 11.82 | 10.38 | 87.82% | 0 | 0% | 11.82 | 10.54 | 89.17% | 0 | 0% | 11.82 | 10.82 | 91.54% | 0 | 0% | 11.82 | 11.27 | 95.35% | 0 | 0%
GNA_182011108_Capacity | South Bay and Central Coast | Central Coast | SALINAS 1108 | 182011108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182011109_Capacity | South Bay and Central Coast | Central Coast | SALINAS 1109 | 182011109 | Feeder | None | None | None | 87.53% | 0 | 0% | 12.83 | 10.67 | 83.16% | 0 | 0% | 12.83 | 10.73 | 83.63% | 0 | 0% | 12.83 | 10.89 | 84.88% | 0 | 0% | 12.83 | 11.06 | 86.2% | 0 | 0% | 12.83 | 11.23 | 87.53% | 0 | 0%
GNA_1822001_Capacity | South Bay and Central Coast | Central Coast | SPENCE BANK 1 | 1822001 | Bank | Demand Growth | Capacity | 2024 | 196.8% | 28.75 | 96.8% | 29.7 | 27.51 | 92.63% | 0 | 0% | 29.7 | 42.15 | 141.9% | 12.45 | 41.92% | 29.7 | 42.38 | 142.7% | 12.68 | 42.69% | 29.7 | 42.46 | 143% | 12.76 | 42.96% | 29.7 | 58.45 | 196.8% | 28.75 | 96.8%
GNA_182201102_Capacity | South Bay and Central Coast | Central Coast | SPENCE 1102 | 182201102 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182201103_Capacity | South Bay and Central Coast | Central Coast | SPENCE 1103 | 182201103 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1822002_Capacity | South Bay and Central Coast | Central Coast | SPENCE BANK 2 | 1822002 | Bank | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182201104_Capacity | South Bay and Central Coast | Central Coast | SPENCE 1104 | 182201104 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182201105_Capacity | South Bay and Central Coast | Central Coast | SPENCE 1105 | 182201105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0828401_Capacity | South Bay and Central Coast | Central Coast | BIG BASIN BANK 1 | 828401 | Bank | None | None | None | 66.4% | 0 | 0% | 9.85 | 6.45 | 65.48% | 0 | 0% | 9.85 | 6.43 | 65.28% | 0 | 0% | 9.85 | 6.42 | 65.18% | 0 | 0% | 9.85 | 6.46 | 65.58% | 0 | 0% | 9.85 | 6.54 | 66.4% | 0 | 0%
GNA_082841101_Capacity | South Bay and Central Coast | Central Coast | BIG BASIN 1101 | 82841101 | Feeder | None | None | None | 41.47% | 0 | 0% | 9.79 | 4.02 | 41.06% | 0 | 0% | 9.79 | 4.01 | 40.96% | 0 | 0% | 9.79 | 4 | 40.86% | 0 | 0% | 9.79 | 4.01 | 40.96% | 0 | 0% | 9.79 | 4.06 | 41.47% | 0 | 0%
GNA_082841102_Capacity | South Bay and Central Coast | Central Coast | BIG BASIN 1102 | 82841102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_183582101_Capacity | South Bay and Central Coast | Central Coast | BURNS 2101 | 183582101 | Feeder | None | None | None | 27.57% | 0 | 0% | 15.67 | 4.27 | 27.25% | 0 | 0% | 15.67 | 4.26 | 27.19% | 0 | 0% | 15.67 | 4.25 | 27.12% | 0 | 0% | 15.67 | 4.28 | 27.31% | 0 | 0% | 15.67 | 4.32 | 27.57% | 0 | 0%
GNA_0836201_Capacity | South Bay and Central Coast | Central Coast | CAMP EVERS BANK 1 | 836201 | Bank | None | None | None | 39.51% | 0 | 0% | 44.6 | 17.62 | 39.51% | 0 | 0% | 44.6 | 16.88 | 37.85% | 0 | 0% | 44.6 | 16.25 | 36.43% | 0 | 0% | 44.6 | 15.71 | 35.22% | 0 | 0% | 44.6 | 15.47 | 34.69% | 0 | 0%
GNA_083622103_Capacity | South Bay and Central Coast | Central Coast | CAMP EVERS 2103 | 83622103 | Feeder | None | None | None | 25.34% | 0 | 0% | 22.22 | 5.63 | 25.34% | 0 | 0% | 22.22 | 5.62 | 25.29% | 0 | 0% | 22.22 | 5.61 | 25.25% | 0 | 0% | 22.22 | 5.6 | 25.2% | 0 | 0% | 22.22 | 5.6 | 25.2% | 0 | 0%
GNA_083622104_Capacity | South Bay and Central Coast | Central Coast | CAMP EVERS 2104 | 83622104 | Feeder | None | None | None | 34.02% | 0 | 0% | 37.04 | 12.6 | 34.02% | 0 | 0% | 37.04 | 12.27 | 33.13% | 0 | 0% | 37.04 | 12.01 | 32.42% | 0 | 0% | 37.04 | 11.76 | 31.75% | 0 | 0% | 37.04 | 11.58 | 31.26% | 0 | 0%
GNA_0836202_Capacity | South Bay and Central Coast | Central Coast | CAMP EVERS BANK 2 | 836202 | Bank | None | None | None | 43.34% | 0 | 0% | 44.55 | 19.31 | 43.34% | 0 | 0% | 44.55 | 19.27 | 43.25% | 0 | 0% | 44.55 | 19.24 | 43.19% | 0 | 0% | 44.55 | 19.26 | 43.23% | 0 | 0% | 44.55 | 19.28 | 43.28% | 0 | 0%
GNA_083622105_Capacity | South Bay and Central Coast | Central Coast | CAMP EVERS 2105 | 83622105 | Feeder | None | None | None | 33.48% | 0 | 0% | 20.67 | 6.89 | 33.33% | 0 | 0% | 20.67 | 6.89 | 33.33% | 0 | 0% | 20.67 | 6.89 | 33.33% | 0 | 0% | 20.67 | 6.9 | 33.38% | 0 | 0% | 20.67 | 6.92 | 33.48% | 0 | 0%
GNA_083622106_Capacity | South Bay and Central Coast | Central Coast | CAMP EVERS 2106 | 83622106 | Feeder | None | None | None | 66.13% | 0 | 0% | 20.67 | 13.6 | 65.8% | 0 | 0% | 20.67 | 13.59 | 65.75% | 0 | 0% | 20.67 | 13.6 | 65.8% | 0 | 0% | 20.67 | 13.63 | 65.94% | 0 | 0% | 20.67 | 13.67 | 66.13% | 0 | 0%
GNA_0832501_Capacity | South Bay and Central Coast | Central Coast | PAUL SWEET BANK 1 | 832501 | Bank | None | None | None | 77.13% | 0 | 0% | 44.55 | 34.36 | 77.13% | 0 | 0% | 44.55 | 33.83 | 75.94% | 0 | 0% | 44.55 | 33.4 | 74.97% | 0 | 0% | 44.55 | 33.41 | 74.99% | 0 | 0% | 44.55 | 33.49 | 75.17% | 0 | 0%
GNA_083252101_Capacity | South Bay and Central Coast | Central Coast | PAUL SWEET 2101 | 83252101 | Feeder | None | None | None | 35.71% | 0 | 0% | 21.56 | 7.35 | 34.09% | 0 | 0% | 21.56 | 7.39 | 34.28% | 0 | 0% | 21.56 | 7.44 | 34.51% | 0 | 0% | 21.56 | 7.56 | 35.06% | 0 | 0% | 21.56 | 7.7 | 35.71% | 0 | 0%
GNA_083252102_Capacity | South Bay and Central Coast | Central Coast | PAUL SWEET 2102 | 83252102 | Feeder | None | None | None | 81.46% | 0 | 0% | 21.04 | 17.14 | 81.46% | 0 | 0% | 21.04 | 17.04 | 80.99% | 0 | 0% | 21.04 | 16.93 | 80.47% | 0 | 0% | 21.04 | 16.88 | 80.23% | 0 | 0% | 21.04 | 16.86 | 80.13% | 0 | 0%
GNA_083252103_Capacity | South Bay and Central Coast | Central Coast | PAUL SWEET 2103 | 83252103 | Feeder | None | None | None | 50.86% | 0 | 0% | 22.22 | 11.3 | 50.86% | 0 | 0% | 22.22 | 11.21 | 50.45% | 0 | 0% | 22.22 | 11.13 | 50.09% | 0 | 0% | 22.22 | 11.12 | 50.05% | 0 | 0% | 22.22 | 11.16 | 50.23% | 0 | 0%
GNA_0832502_Capacity | South Bay and Central Coast | Central Coast | PAUL SWEET BANK 2 | 832502 | Bank | None | None | None | 73.42% | 0 | 0% | 44.55 | 30.56 | 68.6% | 0 | 0% | 44.55 | 30.88 | 69.32% | 0 | 0% | 44.55 | 31.17 | 69.97% | 0 | 0% | 44.55 | 31.9 | 71.6% | 0 | 0% | 44.55 | 32.71 | 73.42% | 0 | 0%
GNA_083252104_Capacity | South Bay and Central Coast | Central Coast | PAUL SWEET 2104 | 83252104 | Feeder | None | None | None | 65.48% | 0 | 0% | 22.22 | 14 | 63.01% | 0 | 0% | 22.22 | 14.07 | 63.32% | 0 | 0% | 22.22 | 14.13 | 63.59% | 0 | 0% | 22.22 | 14.35 | 64.58% | 0 | 0% | 22.22 | 14.55 | 65.48% | 0 | 0%
GNA_083252105_Capacity | South Bay and Central Coast | Central Coast | PAUL SWEET 2105 | 83252105 | Feeder | None | None | None | 50.63% | 0 | 0% | 22.22 | 10.51 | 47.3% | 0 | 0% | 22.22 | 10.59 | 47.66% | 0 | 0% | 22.22 | 10.68 | 48.06% | 0 | 0% | 22.22 | 10.95 | 49.28% | 0 | 0% | 22.22 | 11.25 | 50.63% | 0 | 0%
GNA_083252106_Capacity | South Bay and Central Coast | Central Coast | PAUL SWEET 2106 | 83252106 | Feeder | None | None | None | 34.02% | 0 | 0% | 22.22 | 6.72 | 30.24% | 0 | 0% | 22.22 | 6.88 | 30.96% | 0 | 0% | 22.22 | 7.03 | 31.64% | 0 | 0% | 22.22 | 7.27 | 32.72% | 0 | 0% | 22.22 | 7.56 | 34.02% | 0 | 0%
GNA_0832503_Capacity | South Bay and Central Coast | Central Coast | PAUL SWEET BANK 3 | 832503 | Bank | None | None | None | 64.35% | 0 | 0% | 44.55 | 27.8 | 62.4% | 0 | 0% | 44.55 | 27.9 | 62.63% | 0 | 0% | 44.55 | 27.95 | 62.74% | 0 | 0% | 44.55 | 28.25 | 63.41% | 0 | 0% | 44.55 | 28.67 | 64.35% | 0 | 0%
GNA_083252107_Capacity | South Bay and Central Coast | Central Coast | PAUL SWEET 2107 | 83252107 | Feeder | None | None | None | 55.94% | 0 | 0% | 24.33 | 13.3 | 54.67% | 0 | 0% | 24.33 | 13.31 | 54.71% | 0 | 0% | 24.33 | 13.31 | 54.71% | 0 | 0% | 24.33 | 13.41 | 55.12% | 0 | 0% | 24.33 | 13.61 | 55.94% | 0 | 0%
GNA_083252108_Capacity | South Bay and Central Coast | Central Coast | PAUL SWEET 2108 | 83252108 | Feeder | None | None | None | 46.04% | 0 | 0% | 22.22 | 9.88 | 44.46% | 0 | 0% | 22.22 | 9.93 | 44.69% | 0 | 0% | 22.22 | 9.98 | 44.91% | 0 | 0% | 22.22 | 10.11 | 45.5% | 0 | 0% | 22.22 | 10.23 | 46.04% | 0 | 0%
GNA_083252109_Capacity | South Bay and Central Coast | Central Coast | PAUL SWEET 2109 | 83252109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1824001_Capacity | South Bay and Central Coast | Central Coast | FORT ORD BANK 1 | 1824001 | Bank | None | None | None | 39.53% | 0 | 0% | 17.63 | 6.58 | 37.32% | 0 | 0% | 17.63 | 6.66 | 37.78% | 0 | 0% | 17.63 | 6.7 | 38% | 0 | 0% | 17.63 | 6.8 | 38.57% | 0 | 0% | 17.63 | 6.97 | 39.53% | 0 | 0%
GNA_182401101_Capacity | South Bay and Central Coast | Central Coast | FORT ORD 1101 | 182401101 | Feeder | None | None | None | 97.61% | 0 | 0% | 7.1 | 6.54 | 92.11% | 0 | 0% | 7.1 | 6.62 | 93.24% | 0 | 0% | 7.1 | 6.67 | 93.94% | 0 | 0% | 7.1 | 6.76 | 95.21% | 0 | 0% | 7.1 | 6.93 | 97.61% | 0 | 0%
GNA_1824002_Capacity | South Bay and Central Coast | Central Coast | FORT ORD BANK 2 | 1824002 | Bank | None | None | None | 61.14% | 0 | 0% | 44.6 | 25.93 | 58.14% | 0 | 0% | 44.6 | 26.06 | 58.43% | 0 | 0% | 44.6 | 26.38 | 59.15% | 0 | 0% | 44.6 | 26.81 | 60.11% | 0 | 0% | 44.6 | 27.27 | 61.14% | 0 | 0%
GNA_182402105_Capacity | South Bay and Central Coast | Central Coast | FORT ORD 2105 | 182402105 | Feeder | None | None | None | 44.71% | 0 | 0% | 18.52 | 7.76 | 41.9% | 0 | 0% | 18.52 | 7.88 | 42.55% | 0 | 0% | 18.52 | 8.02 | 43.3% | 0 | 0% | 18.52 | 8.15 | 44.01% | 0 | 0% | 18.52 | 8.28 | 44.71% | 0 | 0%
GNA_182402106_Capacity | South Bay and Central Coast | Central Coast | FORT ORD 2106 | 182402106 | Feeder | None | None | None | 47.47% | 0 | 0% | 8.89 | 3.56 | 40.04% | 0 | 0% | 8.89 | 3.7 | 41.62% | 0 | 0% | 8.89 | 3.83 | 43.08% | 0 | 0% | 8.89 | 4.02 | 45.22% | 0 | 0% | 8.89 | 4.22 | 47.47% | 0 | 0%
GNA_182402107_Capacity | South Bay and Central Coast | Central Coast | FORT ORD 2107 | 182402107 | Feeder | None | None | None | 73.92% | 0 | 0% | 18.52 | 13.69 | 73.92% | 0 | 0% | 18.52 | 13.56 | 73.22% | 0 | 0% | 18.52 | 13.48 | 72.79% | 0 | 0% | 18.52 | 13.45 | 72.62% | 0 | 0% | 18.52 | 13.43 | 72.52% | 0 | 0%
GNA_182402108_Capacity | South Bay and Central Coast | Central Coast | FORT ORD 2108 | 182402108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1821502_Capacity | South Bay and Central Coast | Central Coast | LOS COCHES BANK 2 | 1821502 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182151101_Capacity | South Bay and Central Coast | Central Coast | LOS COCHES 1101 | 182151101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182151102_Capacity | South Bay and Central Coast | Central Coast | LOS COCHES 1102 | 182151102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1820801_Capacity | South Bay and Central Coast | Central Coast | LOS OSITOS BANK 1 | 1820801 | Bank | None | None | None | 97% | 0 | 0% | 12.35 | 11.44 | 92.63% | 0 | 0% | 12.35 | 11.59 | 93.85% | 0 | 0% | 12.35 | 11.71 | 94.82% | 0 | 0% | 12.35 | 11.85 | 95.95% | 0 | 0% | 12.35 | 11.98 | 97% | 0 | 0%
GNA_182082101_Capacity | South Bay and Central Coast | Central Coast | LOS OSITOS 2101 | 182082101 | Feeder | None | None | None | 87.14% | 0 | 0% | 14.07 | 11.72 | 83.3% | 0 | 0% | 14.07 | 11.87 | 84.36% | 0 | 0% | 14.07 | 11.99 | 85.22% | 0 | 0% | 14.07 | 12.13 | 86.21% | 0 | 0% | 14.07 | 12.26 | 87.14% | 0 | 0%
GNA_1820802_Capacity | South Bay and Central Coast | Central Coast | LOS OSITOS BANK 2 | 1820802 | Bank | None | None | None | 61.45% | 0 | 0% | 29.7 | 18.08 | 60.88% | 0 | 0% | 29.7 | 18.14 | 61.08% | 0 | 0% | 29.7 | 18.17 | 61.18% | 0 | 0% | 29.7 | 18.21 | 61.31% | 0 | 0% | 29.7 | 18.25 | 61.45% | 0 | 0%
GNA_182082102_Capacity | South Bay and Central Coast | Central Coast | LOS OSITOS 2102 | 182082102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182082103_Capacity | South Bay and Central Coast | Central Coast | LOS OSITOS 2103 | 182082103 | Feeder | None | None | None | 57.03% | 0 | 0% | 21.11 | 11.83 | 56.04% | 0 | 0% | 21.11 | 11.89 | 56.32% | 0 | 0% | 21.11 | 11.93 | 56.51% | 0 | 0% | 21.11 | 11.99 | 56.8% | 0 | 0% | 21.11 | 12.04 | 57.03% | 0 | 0%
GNA_1820503_Capacity | South Bay and Central Coast | Central Coast | SOLEDAD BANK 3 | 1820503 | Bank | None | None | None | 36.82% | 0 | 0% | 44.57 | 15 | 33.65% | 0 | 0% | 44.57 | 15.33 | 34.4% | 0 | 0% | 44.57 | 15.65 | 35.11% | 0 | 0% | 44.57 | 16.04 | 35.99% | 0 | 0% | 44.57 | 16.41 | 36.82% | 0 | 0%
GNA_182052101_Capacity | South Bay and Central Coast | Central Coast | SOLEDAD 2101 | 182052101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182052102_Capacity | South Bay and Central Coast | Central Coast | SOLEDAD 2102 | 182052102 | Feeder | None | None | None | 44.78% | 0 | 0% | 22.22 | 9.61 | 43.25% | 0 | 0% | 22.22 | 9.67 | 43.52% | 0 | 0% | 22.22 | 9.77 | 43.97% | 0 | 0% | 22.22 | 9.85 | 44.33% | 0 | 0% | 22.22 | 9.95 | 44.78% | 0 | 0%
GNA_1820507_Capacity | South Bay and Central Coast | Central Coast | SOLEDAD BANK 7 | 1820507 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182052104_Capacity | South Bay and Central Coast | Central Coast | SOLEDAD 2104 | 182052104 | Feeder | None | None | None | 26.15% | 0 | 0% | 22.22 | 5.16 | 23.22% | 0 | 0% | 22.22 | 5.29 | 23.81% | 0 | 0% | 22.22 | 5.43 | 24.44% | 0 | 0% | 22.22 | 5.63 | 25.34% | 0 | 0% | 22.22 | 5.81 | 26.15% | 0 | 0%
GNA_182052105_Capacity | South Bay and Central Coast | Central Coast | SOLEDAD 2105 | 182052105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0831902_Capacity | South Bay and Central Coast | Central Coast | GREEN VALLEY BANK 2 | 831902 | Bank | Demand Growth | Capacity | 2025 | 108.3% | 2.47 | 8.316% | 29.7 | 27.32 | 91.99% | 0 | 0% | 29.7 | 29.03 | 97.74% | 0 | 0% | 29.7 | 31.72 | 106.8% | 2.02 | 6.801% | 29.7 | 31.89 | 107.4% | 2.19 | 7.374% | 29.7 | 32.17 | 108.3% | 2.47 | 8.316%
GNA_083192102_Capacity | South Bay and Central Coast | Central Coast | GREEN VALLEY 2102 | 83192102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083192103_Capacity | South Bay and Central Coast | Central Coast | GREEN VALLEY 2103 | 83192103 | Feeder | None | None | None | 88.63% | 0 | 0% | 21.11 | 14.65 | 69.4% | 0 | 0% | 21.11 | 16.3 | 77.21% | 0 | 0% | 21.11 | 18.69 | 88.54% | 0 | 0% | 21.11 | 18.62 | 88.2% | 0 | 0% | 21.11 | 18.71 | 88.63% | 0 | 0%
GNA_0831903_Capacity | South Bay and Central Coast | Central Coast | GREEN VALLEY BANK 3 | 831903 | Bank | Demand Growth | Capacity | 2026 | 101.9% | 0.57 | 1.919% | 29.7 | 29.79 | 100.3% | 0.09 | 0.303% | 29.7 | 29.69 | 99.97% | 0 | 0% | 29.7 | 29.67 | 99.9% | 0 | 0% | 29.7 | 29.96 | 100.9% | 0.26 | 0.8754% | 29.7 | 30.27 | 101.9% | 0.57 | 1.919%
GNA_083192101_Capacity | South Bay and Central Coast | Central Coast | GREEN VALLEY 2101 | 83192101 | Feeder | None | None | None | 83.75% | 0 | 0% | 21.11 | 17.68 | 83.75% | 0 | 0% | 21.11 | 16.96 | 80.34% | 0 | 0% | 21.11 | 16.79 | 79.54% | 0 | 0% | 21.11 | 16.68 | 79.01% | 0 | 0% | 21.11 | 16.58 | 78.54% | 0 | 0%
GNA_0831102_Capacity | South Bay and Central Coast | Central Coast | CASSERLY BANK 1 | 831102 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083110401_Capacity | South Bay and Central Coast | Central Coast | CASSERLY 0401 | 83110401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083192104_Capacity | South Bay and Central Coast | Central Coast | GREEN VALLEY 2104 | 83192104 | Feeder | None | None | None | 74.94% | 0 | 0% | 21.11 | 14.99 | 71.01% | 0 | 0% | 21.11 | 15.3 | 72.48% | 0 | 0% | 21.11 | 15.38 | 72.86% | 0 | 0% | 21.11 | 15.6 | 73.9% | 0 | 0% | 21.11 | 15.82 | 74.94% | 0 | 0%
GNA_0836901_Capacity | South Bay and Central Coast | Central Coast | ROB ROY BANK 1 | 836901 | Bank | None | None | None | 77.09% | 0 | 0% | 22.3 | 15.5 | 69.51% | 0 | 0% | 22.3 | 17.19 | 77.09% | 0 | 0% | 22.3 | 14.75 | 66.14% | 0 | 0% | 22.3 | 15.21 | 68.21% | 0 | 0% | 22.3 | 15.88 | 71.21% | 0 | 0%
GNA_083692104_Capacity | South Bay and Central Coast | Central Coast | ROB ROY 2104 | 83692104 | Feeder | None | None | None | 53.04% | 0 | 0% | 20.04 | 9.07 | 45.26% | 0 | 0% | 20.04 | 10.63 | 53.04% | 0 | 0% | 20.04 | 8.12 | 40.52% | 0 | 0% | 20.04 | 8.31 | 41.47% | 0 | 0% | 20.04 | 8.6 | 42.91% | 0 | 0%
GNA_083692105_Capacity | South Bay and Central Coast | Central Coast | ROB ROY 2105 | 83692105 | Feeder | None | None | None | 34.71% | 0 | 0% | 22.04 | 6.97 | 31.62% | 0 | 0% | 22.04 | 7.08 | 32.12% | 0 | 0% | 22.04 | 7.13 | 32.35% | 0 | 0% | 22.04 | 7.35 | 33.35% | 0 | 0% | 22.04 | 7.65 | 34.71% | 0 | 0%
GNA_0833301_Capacity | South Bay and Central Coast | Central Coast | WATSONVILLE BANK 1 | 833301 | Bank | Demand Growth | Capacity | 2025 | 114.6% | 2.31 | 14.62% | 15.8 | 10.38 | 65.7% | 0 | 0% | 15.8 | 11.99 | 75.89% | 0 | 0% | 15.8 | 17.87 | 113.1% | 2.07 | 13.1% | 15.8 | 17.92 | 113.4% | 2.12 | 13.42% | 15.8 | 18.11 | 114.6% | 2.31 | 14.62%
GNA_083332101_Capacity | South Bay and Central Coast | Central Coast | WATSONVILLE 2101 | 83332101 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0835102_Capacity | South Bay and Central Coast | Central Coast | ERTA BANK 2 | 835102 | Bank | None | None | None | 26.96% | 0 | 0% | 4.97 | 1.29 | 25.96% | 0 | 0% | 4.97 | 1.29 | 25.96% | 0 | 0% | 4.97 | 1.3 | 26.16% | 0 | 0% | 4.97 | 1.32 | 26.56% | 0 | 0% | 4.97 | 1.34 | 26.96% | 0 | 0%
GNA_083510403_Capacity | South Bay and Central Coast | Central Coast | ERTA 0403 | 83510403 | Feeder | None | None | None | 17.19% | 0 | 0% | 2.85 | 0.47 | 16.49% | 0 | 0% | 2.85 | 0.47 | 16.49% | 0 | 0% | 2.85 | 0.47 | 16.49% | 0 | 0% | 2.85 | 0.48 | 16.84% | 0 | 0% | 2.85 | 0.49 | 17.19% | 0 | 0%
GNA_083510404_Capacity | South Bay and Central Coast | Central Coast | ERTA 0404 | 83510404 | Feeder | None | None | None | 27.72% | 0 | 0% | 2.85 | 0.75 | 26.32% | 0 | 0% | 2.85 | 0.76 | 26.67% | 0 | 0% | 2.85 | 0.76 | 26.67% | 0 | 0% | 2.85 | 0.77 | 27.02% | 0 | 0% | 2.85 | 0.79 | 27.72% | 0 | 0%
GNA_0833302_Capacity | South Bay and Central Coast | Central Coast | WATSONVILLE BANK 2 | 833302 | Bank | None | None | None | 32.34% | 0 | 0% | 8.35 | 1.24 | 14.85% | 0 | 0% | 8.35 | 2.7 | 32.34% | 0 | 0% | 8.35 | 2.69 | 32.22% | 0 | 0% | 8.35 | 2.7 | 32.34% | 0 | 0% | 8.35 | 2.7 | 32.34% | 0 | 0%
GNA_083330411_Capacity | South Bay and Central Coast | Central Coast | WATSONVILLE 0411 | 83330411 | Feeder | None | None | None | 32.79% | 0 | 0% | 2.44 | 0.79 | 32.38% | 0 | 0% | 2.44 | 0.79 | 32.38% | 0 | 0% | 2.44 | 0.78 | 31.97% | 0 | 0% | 2.44 | 0.79 | 32.38% | 0 | 0% | 2.44 | 0.8 | 32.79% | 0 | 0%
GNA_083330413_Capacity | South Bay and Central Coast | Central Coast | WATSONVILLE 0413 | 83330413 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083330414_Capacity | South Bay and Central Coast | Central Coast | WATSONVILLE 0414 | 83330414 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0833701_Capacity | South Bay and Central Coast | De Anza | SARATOGA BANK 1 | 833701 | Bank | None | None | None | 56.62% | 0 | 0% | 57.67 | 29.29 | 50.79% | 0 | 0% | 57.67 | 31.39 | 54.43% | 0 | 0% | 57.67 | 32.65 | 56.62% | 0 | 0% | 57.67 | 32.41 | 56.2% | 0 | 0% | 57.67 | 32.61 | 56.55% | 0 | 0%
GNA_083371103_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1103 | 83371103 | Feeder | None | None | None | 62.02% | 0 | 0% | 12.06 | 7.48 | 62.02% | 0 | 0% | 12.06 | 7.39 | 61.28% | 0 | 0% | 12.06 | 7.29 | 60.45% | 0 | 0% | 12.06 | 7.25 | 60.12% | 0 | 0% | 12.06 | 7.25 | 60.12% | 0 | 0%
GNA_083371104_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1104 | 83371104 | Feeder | Demand Growth | Capacity | 2023 | 134.4% | 3.98 | 34.4% | 11.57 | 11.78 | 101.8% | 0.21 | 1.815% | 11.57 | 14.09 | 121.8% | 2.52 | 21.78% | 11.57 | 15.55 | 134.4% | 3.98 | 34.4% | 11.57 | 15.48 | 133.8% | 3.91 | 33.79% | 11.57 | 15.55 | 134.4% | 3.98 | 34.4%
GNA_083371105_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1105 | 83371105 | Feeder | None | None | None | 52.9% | 0 | 0% | 11.57 | 6.12 | 52.9% | 0 | 0% | 11.57 | 6.05 | 52.29% | 0 | 0% | 11.57 | 5.98 | 51.69% | 0 | 0% | 11.57 | 5.96 | 51.51% | 0 | 0% | 11.57 | 5.97 | 51.6% | 0 | 0%
GNA_083371106_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1106 | 83371106 | Feeder | None | None | None | 94.82% | 0 | 0% | 11.4 | 10.54 | 92.46% | 0 | 0% | 11.4 | 10.57 | 92.72% | 0 | 0% | 11.4 | 10.63 | 93.25% | 0 | 0% | 11.4 | 10.7 | 93.86% | 0 | 0% | 11.4 | 10.81 | 94.82% | 0 | 0%
GNA_0833702_Capacity | South Bay and Central Coast | De Anza | SARATOGA BANK 2 | 833702 | Bank | None | None | None | 95.98% | 0 | 0% | 56.02 | 52.44 | 93.61% | 0 | 0% | 56.02 | 52.11 | 93.02% | 0 | 0% | 56.02 | 52.3 | 93.36% | 0 | 0% | 56.02 | 52.87 | 94.38% | 0 | 0% | 56.02 | 53.77 | 95.98% | 0 | 0%
GNA_083371107_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1107 | 83371107 | Feeder | None | None | None | 81.76% | 0 | 0% | 11.57 | 9.46 | 81.76% | 0 | 0% | 11.57 | 9.32 | 80.55% | 0 | 0% | 11.57 | 9.24 | 79.86% | 0 | 0% | 11.57 | 9.2 | 79.52% | 0 | 0% | 11.57 | 9.22 | 79.69% | 0 | 0%
GNA_083371108_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1108 | 83371108 | Feeder | None | None | None | 83.75% | 0 | 0% | 11.57 | 9.56 | 82.63% | 0 | 0% | 11.57 | 9.45 | 81.68% | 0 | 0% | 11.57 | 9.42 | 81.42% | 0 | 0% | 11.57 | 9.51 | 82.2% | 0 | 0% | 11.57 | 9.69 | 83.75% | 0 | 0%
GNA_083371109_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1109 | 83371109 | Feeder | Demand Growth | Capacity | 2023 | 113.4% | 1.55 | 13.4% | 11.57 | 12.4 | 107.2% | 0.83 | 7.174% | 11.57 | 12.38 | 107% | 0.81 | 7.001% | 11.57 | 12.52 | 108.2% | 0.95 | 8.211% | 11.57 | 12.81 | 110.7% | 1.24 | 10.72% | 11.57 | 13.12 | 113.4% | 1.55 | 13.4%
GNA_083371110_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1110 | 83371110 | Feeder | Demand Growth | Capacity | 2023 | 116.5% | 2.01 | 16.49% | 12.19 | 13.7 | 112.4% | 1.51 | 12.39% | 12.19 | 13.77 | 113% | 1.58 | 12.96% | 12.19 | 13.85 | 113.6% | 1.66 | 13.62% | 12.19 | 13.99 | 114.8% | 1.8 | 14.77% | 12.19 | 14.2 | 116.5% | 2.01 | 16.49%
GNA_083371111_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1111 | 83371111 | Feeder | None | None | None | 91.22% | 0 | 0% | 12.19 | 10.61 | 87.04% | 0 | 0% | 12.19 | 10.67 | 87.53% | 0 | 0% | 12.19 | 10.71 | 87.86% | 0 | 0% | 12.19 | 10.85 | 89.01% | 0 | 0% | 12.19 | 11.12 | 91.22% | 0 | 0%
GNA_0833703_Capacity | South Bay and Central Coast | De Anza | SARATOGA BANK 3 | 833703 | Bank | None | None | None | 99.75% | 0 | 0% | 44.6 | 42.14 | 94.48% | 0 | 0% | 44.6 | 44.17 | 99.04% | 0 | 0% | 44.6 | 43.93 | 98.5% | 0 | 0% | 44.6 | 44.07 | 98.81% | 0 | 0% | 44.6 | 44.49 | 99.75% | 0 | 0%
GNA_083371112_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1112 | 83371112 | Feeder | None | None | None | 80.76% | 0 | 0% | 12.06 | 9.74 | 80.76% | 0 | 0% | 12.06 | 9.7 | 80.43% | 0 | 0% | 12.06 | 9.66 | 80.1% | 0 | 0% | 12.06 | 9.64 | 79.93% | 0 | 0% | 12.06 | 9.65 | 80.02% | 0 | 0%
GNA_083371113_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1113 | 83371113 | Feeder | Demand Growth | Capacity | 2024 | 110.1% | 1.22 | 10.12% | 12.06 | 11.69 | 96.93% | 0 | 0% | 12.06 | 12.99 | 107.7% | 0.93 | 7.711% | 12.06 | 12.95 | 107.4% | 0.89 | 7.38% | 12.06 | 13.05 | 108.2% | 0.99 | 8.209% | 12.06 | 13.28 | 110.1% | 1.22 | 10.12%
GNA_083371114_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1114 | 83371114 | Feeder | Demand Growth | Capacity | 2023 | 117.1% | 2.09 | 17.15% | 12.19 | 13.38 | 109.8% | 1.19 | 9.762% | 12.19 | 14.19 | 116.4% | 2 | 16.41% | 12.19 | 14.11 | 115.8% | 1.92 | 15.75% | 12.19 | 14.16 | 116.2% | 1.97 | 16.16% | 12.19 | 14.28 | 117.1% | 2.09 | 17.15%
GNA_083371115_Capacity | South Bay and Central Coast | De Anza | SARATOGA 1115 | 83371115 | Feeder | None | None | None | 94.91% | 0 | 0% | 12.19 | 11.57 | 94.91% | 0 | 0% | 12.19 | 11.36 | 93.19% | 0 | 0% | 12.19 | 11.22 | 92.04% | 0 | 0% | 12.19 | 11.18 | 91.71% | 0 | 0% | 12.19 | 11.18 | 91.71% | 0 | 0%
GNA_0836701_Capacity | South Bay and Central Coast | De Anza | WOLFE BANK 1 | 836701 | Bank | None | None | None | 100.2% | 0.09 | 0.2018% | 44.6 | 34.71 | 77.83% | 0 | 0% | 44.6 | 33.89 | 75.99% | 0 | 0% | 44.6 | 34.43 | 77.2% | 0 | 0% | 44.6 | 35.52 | 79.64% | 0 | 0% | 44.6 | 44.69 | 100.2% | 0.09 | 0.2018%
GNA_083671104_Capacity | South Bay and Central Coast | De Anza | WOLFE 1104 | 83671104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083671105_Capacity | South Bay and Central Coast | De Anza | WOLFE 1105 | 83671105 | Feeder | Demand Growth | Capacity | 2026 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083671106_Capacity | South Bay and Central Coast | De Anza | WOLFE 1106 | 83671106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0836702_Capacity | South Bay and Central Coast | De Anza | WOLFE BANK 2 | 836702 | Bank | Demand Growth | Capacity | 2026 | 138.4% | 11.4 | 38.38% | 29.7 | 27.96 | 94.14% | 0 | 0% | 29.7 | 28.49 | 95.93% | 0 | 0% | 29.7 | 28.91 | 97.34% | 0 | 0% | 29.7 | 32.63 | 109.9% | 2.93 | 9.865% | 29.7 | 41.1 | 138.4% | 11.4 | 38.38%
GNA_083671107_Capacity | South Bay and Central Coast | De Anza | WOLFE 1107 | 83671107 | Feeder | None | None | None | 75.29% | 0 | 0% | 12.06 | 5.84 | 48.42% | 0 | 0% | 12.06 | 5.98 | 49.59% | 0 | 0% | 12.06 | 6.17 | 51.16% | 0 | 0% | 12.06 | 9.01 | 74.71% | 0 | 0% | 12.06 | 9.08 | 75.29% | 0 | 0%
GNA_083671109_Capacity | South Bay and Central Coast | De Anza | WOLFE 1109 | 83671109 | Feeder | Demand Growth | Capacity | 2026 | 188.4% | 10.23 | 88.42% | 11.57 | 10.23 | 88.42% | 0 | 0% | 11.57 | 10.81 | 93.43% | 0 | 0% | 11.57 | 11.15 | 96.37% | 0 | 0% | 11.57 | 12.17 | 105.2% | 0.6 | 5.186% | 11.57 | 21.8 | 188.4% | 10.23 | 88.42%
GNA_083671110_Capacity | South Bay and Central Coast | De Anza | WOLFE 1110 | 83671110 | Feeder | None | None | None | 90.67% | 0 | 0% | 11.57 | 10.49 | 90.67% | 0 | 0% | 11.57 | 10.4 | 89.89% | 0 | 0% | 11.57 | 10.33 | 89.28% | 0 | 0% | 11.57 | 10.37 | 89.63% | 0 | 0% | 11.57 | 10.42 | 90.06% | 0 | 0%
GNA_0836703_Capacity | South Bay and Central Coast | De Anza | WOLFE BANK 3 | 836703 | Bank | None | None | None | 38.77% | 0 | 0% | 44.6 | 14.83 | 33.25% | 0 | 0% | 44.6 | 15.97 | 35.81% | 0 | 0% | 44.6 | 16.29 | 36.52% | 0 | 0% | 44.6 | 16.83 | 37.74% | 0 | 0% | 44.6 | 17.29 | 38.77% | 0 | 0%
GNA_083671113_Capacity | South Bay and Central Coast | De Anza | WOLFE 1113 | 83671113 | Feeder | None | None | None | 71.63% | 0 | 0% | 12.83 | 7.7 | 60.02% | 0 | 0% | 12.83 | 8.07 | 62.9% | 0 | 0% | 12.83 | 8.42 | 65.63% | 0 | 0% | 12.83 | 8.86 | 69.06% | 0 | 0% | 12.83 | 9.19 | 71.63% | 0 | 0%
GNA_083671114_Capacity | South Bay and Central Coast | De Anza | WOLFE 1114 | 83671114 | Feeder | None | None | None | 79.97% | 0 | 0% | 12.83 | 8.78 | 68.43% | 0 | 0% | 12.83 | 9.82 | 76.54% | 0 | 0% | 12.83 | 9.93 | 77.4% | 0 | 0% | 12.83 | 10.08 | 78.57% | 0 | 0% | 12.83 | 10.26 | 79.97% | 0 | 0%
GNA_0822401_Capacity | South Bay and Central Coast | De Anza | LOS ALTOS BANK 1 | 822401 | Bank | None | None | None | 51.58% | 0 | 0% | 29.7 | 14.79 | 49.8% | 0 | 0% | 29.7 | 14.87 | 50.07% | 0 | 0% | 29.7 | 14.97 | 50.4% | 0 | 0% | 29.7 | 15.11 | 50.88% | 0 | 0% | 29.7 | 15.32 | 51.58% | 0 | 0%
GNA_082241103_Capacity | South Bay and Central Coast | De Anza | LOS ALTOS 1103 | 82241103 | Feeder | None | None | None | 58.74% | 0 | 0% | 3.66 | 2.04 | 55.74% | 0 | 0% | 3.66 | 2.06 | 56.28% | 0 | 0% | 3.66 | 2.07 | 56.56% | 0 | 0% | 3.66 | 2.11 | 57.65% | 0 | 0% | 3.66 | 2.15 | 58.74% | 0 | 0%
GNA_082241104_Capacity | South Bay and Central Coast | De Anza | LOS ALTOS 1104 | 82241104 | Feeder | None | None | None | 65% | 0 | 0% | 11.8 | 7.36 | 62.37% | 0 | 0% | 11.8 | 7.38 | 62.54% | 0 | 0% | 11.8 | 7.45 | 63.14% | 0 | 0% | 11.8 | 7.54 | 63.9% | 0 | 0% | 11.8 | 7.67 | 65% | 0 | 0%
GNA_082241105_Capacity | South Bay and Central Coast | De Anza | LOS ALTOS 1105 | 82241105 | Feeder | None | None | None | 53.57% | 0 | 0% | 12.19 | 6.5 | 53.32% | 0 | 0% | 12.19 | 6.5 | 53.32% | 0 | 0% | 12.19 | 6.49 | 53.24% | 0 | 0% | 12.19 | 6.5 | 53.32% | 0 | 0% | 12.19 | 6.53 | 53.57% | 0 | 0%
GNA_0822402_Capacity | South Bay and Central Coast | De Anza | LOS ALTOS BANK 2 | 822402 | Bank | None | None | None | 82.95% | 0 | 0% | 9.5 | 6 | 63.16% | 0 | 0% | 9.5 | 7.58 | 79.79% | 0 | 0% | 9.5 | 7.68 | 80.84% | 0 | 0% | 9.5 | 7.79 | 82% | 0 | 0% | 9.5 | 7.88 | 82.95% | 0 | 0%
GNA_082241107_Capacity | South Bay and Central Coast | De Anza | LOS ALTOS 1107 | 82241107 | Feeder | None | None | None | 94.45% | 0 | 0% | 8.47 | 6.13 | 72.37% | 0 | 0% | 8.47 | 7.7 | 90.91% | 0 | 0% | 8.47 | 7.8 | 92.09% | 0 | 0% | 8.47 | 7.91 | 93.39% | 0 | 0% | 8.47 | 8 | 94.45% | 0 | 0%
GNA_0822403_Capacity | South Bay and Central Coast | De Anza | LOS ALTOS BANK 3 | 822403 | Bank | None | None | None | 63.26% | 0 | 0% | 9.5 | 6.01 | 63.26% | 0 | 0% | 9.5 | 5.97 | 62.84% | 0 | 0% | 9.5 | 5.93 | 62.42% | 0 | 0% | 9.5 | 5.92 | 62.32% | 0 | 0% | 9.5 | 5.91 | 62.21% | 0 | 0%
GNA_082241106_Capacity | South Bay and Central Coast | De Anza | LOS ALTOS 1106 | 82241106 | Feeder | None | None | None | 49.66% | 0 | 0% | 10.39 | 5.16 | 49.66% | 0 | 0% | 10.39 | 5.12 | 49.28% | 0 | 0% | 10.39 | 5.07 | 48.8% | 0 | 0% | 10.39 | 5.06 | 48.7% | 0 | 0% | 10.39 | 5.06 | 48.7% | 0 | 0%
GNA_0821602_Capacity | South Bay and Central Coast | De Anza | LOYOLA BANK 2 | 821602 | Bank | None | None | None | 98.12% | 0 | 0% | 20.79 | 20.02 | 96.3% | 0 | 0% | 20.79 | 20.08 | 96.58% | 0 | 0% | 20.79 | 20.17 | 97.02% | 0 | 0% | 20.79 | 20.26 | 97.45% | 0 | 0% | 20.79 | 20.4 | 98.12% | 0 | 0%
GNA_082161101_Capacity | South Bay and Central Coast | De Anza | LOYOLA 1101 | 82161101 | Feeder | None | None | None | 99.11% | 0 | 0% | 10.16 | 9.85 | 96.95% | 0 | 0% | 10.16 | 9.89 | 97.34% | 0 | 0% | 10.16 | 9.95 | 97.93% | 0 | 0% | 10.16 | 9.99 | 98.33% | 0 | 0% | 10.16 | 10.07 | 99.11% | 0 | 0%
GNA_082161102_Capacity | South Bay and Central Coast | De Anza | LOYOLA 1102 | 82161102 | Feeder | Demand Growth | Capacity | 2023 | 100.9% | 0.11 | 0.9024% | 12.19 | 12.3 | 100.9% | 0.11 | 0.9024% | 12.19 | 12.26 | 100.6% | 0.07 | 0.5742% | 12.19 | 12.23 | 100.3% | 0.04 | 0.3281% | 12.19 | 12.2 | 100.1% | 0.01 | 0.08203% | 12.19 | 12.22 | 100.2% | 0.03 | 0.2461%
GNA_0834801_Capacity | South Bay and Central Coast | De Anza | STELLING BANK 1 | 834801 | Bank | None | None | None | 78.97% | 0 | 0% | 42.03 | 33.19 | 78.97% | 0 | 0% | 42.03 | 33.01 | 78.54% | 0 | 0% | 42.03 | 32.9 | 78.28% | 0 | 0% | 42.03 | 32.87 | 78.21% | 0 | 0% | 42.03 | 32.95 | 78.4% | 0 | 0%
GNA_083481102_Capacity | South Bay and Central Coast | De Anza | STELLING 1102 | 83481102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083481103_Capacity | South Bay and Central Coast | De Anza | STELLING 1103 | 83481103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083481104_Capacity | South Bay and Central Coast | De Anza | STELLING 1104 | 83481104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083481105_Capacity | South Bay and Central Coast | De Anza | STELLING 1105 | 83481105 | Feeder | None | None | None | 43.61% | 0 | 0% | 9.54 | 4.16 | 43.61% | 0 | 0% | 9.54 | 4.14 | 43.4% | 0 | 0% | 9.54 | 4.14 | 43.4% | 0 | 0% | 9.54 | 4.13 | 43.29% | 0 | 0% | 9.54 | 4.13 | 43.29% | 0 | 0%
GNA_0834802_Capacity | South Bay and Central Coast | De Anza | STELLING BANK 2 | 834802 | Bank | None | None | None | 92.9% | 0 | 0% | 29.7 | 27.59 | 92.9% | 0 | 0% | 29.7 | 27.3 | 91.92% | 0 | 0% | 29.7 | 27.21 | 91.62% | 0 | 0% | 29.7 | 27.28 | 91.85% | 0 | 0% | 29.7 | 27.42 | 92.32% | 0 | 0%
GNA_083481106_Capacity | South Bay and Central Coast | De Anza | STELLING 1106 | 83481106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083481107_Capacity | South Bay and Central Coast | De Anza | STELLING 1107 | 83481107 | Feeder | None | None | None | 68.09% | 0 | 0% | 12.19 | 8.3 | 68.09% | 0 | 0% | 12.19 | 8.25 | 67.68% | 0 | 0% | 12.19 | 8.22 | 67.43% | 0 | 0% | 12.19 | 8.22 | 67.43% | 0 | 0% | 12.19 | 8.26 | 67.76% | 0 | 0%
GNA_083481108_Capacity | South Bay and Central Coast | De Anza | STELLING 1108 | 83481108 | Feeder | None | None | None | 98.31% | 0 | 0% | 11.8 | 11.37 | 96.36% | 0 | 0% | 11.8 | 11.44 | 96.95% | 0 | 0% | 11.8 | 11.51 | 97.54% | 0 | 0% | 11.8 | 11.58 | 98.14% | 0 | 0% | 11.8 | 11.6 | 98.31% | 0 | 0%
GNA_083481109_Capacity | South Bay and Central Coast | De Anza | STELLING 1109 | 83481109 | Feeder | None | None | None | 82.69% | 0 | 0% | 12.19 | 10.08 | 82.69% | 0 | 0% | 12.19 | 9.93 | 81.46% | 0 | 0% | 12.19 | 9.78 | 80.23% | 0 | 0% | 12.19 | 9.77 | 80.15% | 0 | 0% | 12.19 | 9.89 | 81.13% | 0 | 0%
GNA_0834803_Capacity | South Bay and Central Coast | De Anza | STELLING BANK 3 | 834803 | Bank | Demand Growth | Capacity | 2026 | 103% | 0.9 | 3.03% | 29.7 | 28.47 | 95.86% | 0 | 0% | 29.7 | 29.22 | 98.38% | 0 | 0% | 29.7 | 29.84 | 100.5% | 0.14 | 0.4714% | 29.7 | 30.17 | 101.6% | 0.47 | 1.582% | 29.7 | 30.6 | 103% | 0.9 | 3.03%
GNA_083481110_Capacity | South Bay and Central Coast | De Anza | STELLING 1110 | 83481110 | Feeder | None | None | None | 97.23% | 0 | 0% | 11.57 | 11.09 | 95.85% | 0 | 0% | 11.57 | 10.95 | 94.64% | 0 | 0% | 11.57 | 10.94 | 94.55% | 0 | 0% | 11.57 | 11.05 | 95.51% | 0 | 0% | 11.57 | 11.25 | 97.23% | 0 | 0%
GNA_083481111_Capacity | South Bay and Central Coast | De Anza | STELLING 1111 | 83481111 | Feeder | None | None | None | 97.93% | 0 | 0% | 11.57 | 11.31 | 97.75% | 0 | 0% | 11.57 | 11.23 | 97.06% | 0 | 0% | 11.57 | 11.2 | 96.8% | 0 | 0% | 11.57 | 11.26 | 97.32% | 0 | 0% | 11.57 | 11.33 | 97.93% | 0 | 0%
GNA_083481112_Capacity | South Bay and Central Coast | De Anza | STELLING 1112 | 83481112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083481113_Capacity | South Bay and Central Coast | De Anza | STELLING 1113 | 83481113 | Feeder | None | None | None | 71.48% | 0 | 0% | 11.57 | 7.45 | 64.39% | 0 | 0% | 11.57 | 7.63 | 65.95% | 0 | 0% | 11.57 | 7.81 | 67.5% | 0 | 0% | 11.57 | 8.01 | 69.23% | 0 | 0% | 11.57 | 8.27 | 71.48% | 0 | 0%
GNA_0821601_Capacity | South Bay and Central Coast | De Anza | LOYOLA BANK 1 | 821601 | Bank | Demand Growth | Capacity | 2023 | 118% | 0.85 | 18.05% | 4.71 | 5.38 | 114.2% | 0.67 | 14.23% | 4.71 | 5.42 | 115.1% | 0.71 | 15.07% | 4.71 | 5.46 | 115.9% | 0.75 | 15.92% | 4.71 | 5.51 | 117% | 0.8 | 16.99% | 4.71 | 5.56 | 118% | 0.85 | 18.05%
GNA_082160401_Capacity | South Bay and Central Coast | De Anza | LOYOLA 0401 | 82160401 | Feeder | Demand Growth | Capacity | 2023 | 106.8% | 0.16 | 6.809% | 2.35 | 2.51 | 106.8% | 0.16 | 6.809% | 2.35 | 2.5 | 106.4% | 0.15 | 6.383% | 2.35 | 2.49 | 106% | 0.14 | 5.957% | 2.35 | 2.48 | 105.5% | 0.13 | 5.532% | 2.35 | 2.51 | 106.8% | 0.16 | 6.809%
GNA_082160403_Capacity | South Bay and Central Coast | De Anza | LOYOLA 0403 | 82160403 | Feeder | Demand Growth | Capacity | 2023 | 116.6% | 0.39 | 16.6% | 2.35 | 2.56 | 108.9% | 0.21 | 8.936% | 2.35 | 2.6 | 110.6% | 0.25 | 10.64% | 2.35 | 2.66 | 113.2% | 0.31 | 13.19% | 2.35 | 2.71 | 115.3% | 0.36 | 15.32% | 2.35 | 2.74 | 116.6% | 0.39 | 16.6%
GNA_0820201_Capacity | South Bay and Central Coast | De Anza | LOS GATOS BANK 1 | 820201 | Bank | Demand Growth | Capacity | 2023 | 118.5% | 2.92 | 18.48% | 15.8 | 18.72 | 118.5% | 2.92 | 18.48% | 15.8 | 18.65 | 118% | 2.85 | 18.04% | 15.8 | 18.59 | 117.7% | 2.79 | 17.66% | 15.8 | 18.51 | 117.2% | 2.71 | 17.15% | 15.8 | 18.5 | 117.1% | 2.7 | 17.09%
GNA_082021106_Capacity | South Bay and Central Coast | De Anza | LOS GATOS 1106 | 82021106 | Feeder | None | None | None | 48.54% | 0 | 0% | 10.63 | 5.16 | 48.54% | 0 | 0% | 10.63 | 5.15 | 48.45% | 0 | 0% | 10.63 | 5.13 | 48.26% | 0 | 0% | 10.63 | 5.11 | 48.07% | 0 | 0% | 10.63 | 5.12 | 48.17% | 0 | 0%
GNA_082021107_Capacity | South Bay and Central Coast | De Anza | LOS GATOS 1107 | 82021107 | Feeder | None | None | None | 84.24% | 0 | 0% | 9.71 | 8.18 | 84.24% | 0 | 0% | 9.71 | 8.14 | 83.83% | 0 | 0% | 9.71 | 8.1 | 83.42% | 0 | 0% | 9.71 | 8.06 | 83.01% | 0 | 0% | 9.71 | 8.04 | 82.8% | 0 | 0%
GNA_082021108_Capacity | South Bay and Central Coast | De Anza | LOS GATOS 1108 | 82021108 | Feeder | None | None | None | 53.15% | 0 | 0% | 10.01 | 5.32 | 53.15% | 0 | 0% | 10.01 | 5.29 | 52.85% | 0 | 0% | 10.01 | 5.27 | 52.65% | 0 | 0% | 10.01 | 5.24 | 52.35% | 0 | 0% | 10.01 | 5.23 | 52.25% | 0 | 0%
GNA_0820202_Capacity | South Bay and Central Coast | De Anza | LOS GATOS BANK 2 | 820202 | Bank | Demand Growth | Capacity | 2023 | 122.9% | 3.57 | 22.93% | 15.57 | 19.14 | 122.9% | 3.57 | 22.93% | 15.57 | 19.11 | 122.7% | 3.54 | 22.74% | 15.57 | 19.1 | 122.7% | 3.53 | 22.67% | 15.57 | 19.09 | 122.6% | 3.52 | 22.61% | 15.57 | 19.12 | 122.8% | 3.55 | 22.8%
GNA_082021101_Capacity | South Bay and Central Coast | De Anza | LOS GATOS 1101 | 82021101 | Feeder | None | None | None | 100.1% | 0.01 | 0.08203% | 12.19 | 12.2 | 100.1% | 0.01 | 0.08203% | 12.19 | 12.08 | 99.1% | 0 | 0% | 12.19 | 11.99 | 98.36% | 0 | 0% | 12.19 | 11.92 | 97.79% | 0 | 0% | 12.19 | 11.84 | 97.13% | 0 | 0%
GNA_082021102_Capacity | South Bay and Central Coast | De Anza | LOS GATOS 1102 | 82021102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0837701_Capacity | South Bay and Central Coast | De Anza | VASONA BANK 1 | 837701 | Bank | Demand Growth | Capacity | 2023 | 102.4% | 1.09 | 2.444% | 44.6 | 45.03 | 101% | 0.43 | 0.9641% | 44.6 | 45.69 | 102.4% | 1.09 | 2.444% | 44.6 | 45.45 | 101.9% | 0.85 | 1.906% | 44.6 | 45.5 | 102% | 0.9 | 2.018% | 44.6 | 45.64 | 102.3% | 1.04 | 2.332%
GNA_083771101_Capacity | South Bay and Central Coast | De Anza | VASONA 1101 | 83771101 | Feeder | None | None | None | 94.59% | 0 | 0% | 12.19 | 11.36 | 93.19% | 0 | 0% | 12.19 | 11.35 | 93.11% | 0 | 0% | 12.19 | 11.37 | 93.27% | 0 | 0% | 12.19 | 11.44 | 93.85% | 0 | 0% | 12.19 | 11.53 | 94.59% | 0 | 0%
GNA_083771102_Capacity | South Bay and Central Coast | De Anza | VASONA 1102 | 83771102 | Feeder | Demand Growth | Capacity | 2023 | 102.9% | 0.34 | 2.881% | 11.8 | 12.14 | 102.9% | 0.34 | 2.881% | 11.8 | 12.04 | 102% | 0.24 | 2.034% | 11.8 | 11.93 | 101.1% | 0.13 | 1.102% | 11.8 | 11.87 | 100.6% | 0.07 | 0.5932% | 11.8 | 11.83 | 100.3% | 0.03 | 0.2542%
GNA_083771103_Capacity | South Bay and Central Coast | De Anza | VASONA 1103 | 83771103 | Feeder | Demand Growth | Capacity | 2023 | 106.5% | 0.79 | 6.481% | 12.19 | 12.98 | 106.5% | 0.79 | 6.481% | 12.19 | 12.05 | 98.85% | 0 | 0% | 12.19 | 11.97 | 98.2% | 0 | 0% | 12.19 | 11.98 | 98.28% | 0 | 0% | 12.19 | 12.01 | 98.52% | 0 | 0%
GNA_083771104_Capacity | South Bay and Central Coast | De Anza | VASONA 1104 | 83771104 | Feeder | None | None | None | 94.26% | 0 | 0% | 12.19 | 9.45 | 77.52% | 0 | 0% | 12.19 | 11.49 | 94.26% | 0 | 0% | 12.19 | 11.46 | 94.01% | 0 | 0% | 12.19 | 11.44 | 93.85% | 0 | 0% | 12.19 | 11.44 | 93.85% | 0 | 0%
GNA_0837702_Capacity | South Bay and Central Coast | De Anza | VASONA BANK 2 | 837702 | Bank | None | None | None | 65.17% | 0 | 0% | 44.53 | 24.31 | 54.59% | 0 | 0% | 44.53 | 24.2 | 54.35% | 0 | 0% | 44.53 | 28.89 | 64.88% | 0 | 0% | 44.53 | 28.93 | 64.97% | 0 | 0% | 44.53 | 29.02 | 65.17% | 0 | 0%
GNA_083771105_Capacity | South Bay and Central Coast | De Anza | VASONA 1105 | 83771105 | Feeder | Demand Growth | Capacity | 2023 | 101.6% | 0.2 | 1.559% | 12.83 | 13.03 | 101.6% | 0.2 | 1.559% | 12.83 | 12.88 | 100.4% | 0.05 | 0.3897% | 12.83 | 12.79 | 99.69% | 0 | 0% | 12.83 | 12.74 | 99.3% | 0 | 0% | 12.83 | 12.74 | 99.3% | 0 | 0%
GNA_083771108_Capacity | South Bay and Central Coast | De Anza | VASONA 1108 | 83771108 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0839001_Capacity | South Bay and Central Coast | De Anza | AMES BANK 1 | 839001 | Bank | None | None | None | 90.13% | 0 | 0% | 29.7 | 23.82 | 80.2% | 0 | 0% | 29.7 | 26.77 | 90.13% | 0 | 0% | 29.7 | 26.76 | 90.1% | 0 | 0% | 29.7 | 26.74 | 90.03% | 0 | 0% | 29.7 | 26.75 | 90.07% | 0 | 0%
GNA_083901101_Capacity | South Bay and Central Coast | De Anza | AMES 1101 | 83901101 | Feeder | Demand Growth | Capacity | 2024 | 105% | 0.61 | 5.004% | 12.19 | 11.78 | 96.64% | 0 | 0% | 12.19 | 12.8 | 105% | 0.61 | 5.004% | 12.19 | 12.8 | 105% | 0.61 | 5.004% | 12.19 | 12.78 | 104.8% | 0.59 | 4.84% | 12.19 | 12.78 | 104.8% | 0.59 | 4.84%
GNA_083901102_Capacity | South Bay and Central Coast | De Anza | AMES 1102 | 83901102 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0820301_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW BANK 1 | 820301 | Bank | None | None | None | 92.49% | 0 | 0% | 29.7 | 27.47 | 92.49% | 0 | 0% | 29.7 | 25.78 | 86.8% | 0 | 0% | 29.7 | 25.78 | 86.8% | 0 | 0% | 29.7 | 26.24 | 88.35% | 0 | 0% | 29.7 | 26.84 | 90.37% | 0 | 0%
GNA_082031106_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1106 | 82031106 | Feeder | None | None | None | 82.26% | 0 | 0% | 12.06 | 9.49 | 78.69% | 0 | 0% | 12.06 | 9.55 | 79.19% | 0 | 0% | 12.06 | 9.64 | 79.93% | 0 | 0% | 12.06 | 9.76 | 80.93% | 0 | 0% | 12.06 | 9.92 | 82.26% | 0 | 0%
GNA_082031107_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1107 | 82031107 | Feeder | None | None | None | 98.53% | 0 | 0% | 11.57 | 11.4 | 98.53% | 0 | 0% | 11.57 | 10.57 | 91.36% | 0 | 0% | 11.57 | 10.73 | 92.74% | 0 | 0% | 11.57 | 10.95 | 94.64% | 0 | 0% | 11.57 | 11.09 | 95.85% | 0 | 0%
GNA_082031108_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1108 | 82031108 | Feeder | None | None | None | 84.99% | 0 | 0% | 12.06 | 10.25 | 84.99% | 0 | 0% | 12.06 | 8.56 | 70.98% | 0 | 0% | 12.06 | 8.63 | 71.56% | 0 | 0% | 12.06 | 8.8 | 72.97% | 0 | 0% | 12.06 | 8.97 | 74.38% | 0 | 0%
GNA_082031109_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1109 | 82031109 | Feeder | None | None | None | 19.62% | 0 | 0% | 11.57 | 1.31 | 11.32% | 0 | 0% | 11.57 | 2.27 | 19.62% | 0 | 0% | 11.57 | 2.27 | 19.62% | 0 | 0% | 11.57 | 2.27 | 19.62% | 0 | 0% | 11.57 | 2.27 | 19.62% | 0 | 0%
GNA_0820302_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW BANK 2 | 820302 | Bank | None | None | None | 85.96% | 0 | 0% | 39.6 | 31.36 | 79.19% | 0 | 0% | 39.6 | 31.64 | 79.9% | 0 | 0% | 39.6 | 32.24 | 81.41% | 0 | 0% | 39.6 | 33.1 | 83.59% | 0 | 0% | 39.6 | 34.04 | 85.96% | 0 | 0%
GNA_082031102_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1102 | 82031102 | Feeder | None | None | None | 98.53% | 0 | 0% | 11.57 | 10.15 | 87.73% | 0 | 0% | 11.57 | 10.76 | 93% | 0 | 0% | 11.57 | 10.96 | 94.73% | 0 | 0% | 11.57 | 11.21 | 96.89% | 0 | 0% | 11.57 | 11.4 | 98.53% | 0 | 0%
GNA_082031103_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1103 | 82031103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082031104_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1104 | 82031104 | Feeder | None | None | None | 96.11% | 0 | 0% | 11.57 | 11.12 | 96.11% | 0 | 0% | 11.57 | 10.23 | 88.42% | 0 | 0% | 11.57 | 10.27 | 88.76% | 0 | 0% | 11.57 | 10.4 | 89.89% | 0 | 0% | 11.57 | 10.78 | 93.17% | 0 | 0%
GNA_082031105_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1105 | 82031105 | Feeder | None | None | None | 84.96% | 0 | 0% | 11.57 | 9.1 | 78.65% | 0 | 0% | 11.57 | 9.28 | 80.21% | 0 | 0% | 11.57 | 9.39 | 81.16% | 0 | 0% | 11.57 | 9.6 | 82.97% | 0 | 0% | 11.57 | 9.83 | 84.96% | 0 | 0%
GNA_0820303_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW BANK 3 | 820303 | Bank | None | None | None | 99.31% | 0 | 0% | 42.03 | 37.99 | 90.39% | 0 | 0% | 42.03 | 40.44 | 96.22% | 0 | 0% | 42.03 | 40.76 | 96.98% | 0 | 0% | 42.03 | 41.2 | 98.03% | 0 | 0% | 42.03 | 41.74 | 99.31% | 0 | 0%
GNA_082031110_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1110 | 82031110 | Feeder | None | None | None | 71.82% | 0 | 0% | 11.57 | 7.79 | 67.33% | 0 | 0% | 11.57 | 7.84 | 67.76% | 0 | 0% | 11.57 | 7.99 | 69.06% | 0 | 0% | 11.57 | 8.16 | 70.53% | 0 | 0% | 11.57 | 8.31 | 71.82% | 0 | 0%
GNA_082031111_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1111 | 82031111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082031112_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1112 | 82031112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082031113_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1113 | 82031113 | Feeder | None | None | None | 91.36% | 0 | 0% | 11.57 | 9.33 | 80.64% | 0 | 0% | 11.57 | 10.06 | 86.95% | 0 | 0% | 11.57 | 10.14 | 87.64% | 0 | 0% | 11.57 | 10.32 | 89.2% | 0 | 0% | 11.57 | 10.57 | 91.36% | 0 | 0%
GNA_082031114_Capacity | South Bay and Central Coast | De Anza | MOUNTAIN VIEW 1114 | 82031114 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0836301_Capacity | South Bay and Central Coast | De Anza | WHISMAN BANK 1 | 836301 | Bank | Demand Growth | Capacity | 2024 | 104.8% | 1.43 | 4.815% | 29.7 | 23.07 | 77.68% | 0 | 0% | 29.7 | 30.9 | 104% | 1.2 | 4.04% | 29.7 | 30.95 | 104.2% | 1.25 | 4.209% | 29.7 | 31 | 104.4% | 1.3 | 4.377% | 29.7 | 31.13 | 104.8% | 1.43 | 4.815%
GNA_083631101_Capacity | South Bay and Central Coast | De Anza | WHISMAN 1101 | 83631101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083631102_Capacity | South Bay and Central Coast | De Anza | WHISMAN 1102 | 83631102 | Feeder | None | None | None | 78.91% | 0 | 0% | 11.57 | 6.78 | 58.6% | 0 | 0% | 11.57 | 9.12 | 78.82% | 0 | 0% | 11.57 | 9.12 | 78.82% | 0 | 0% | 11.57 | 9.12 | 78.82% | 0 | 0% | 11.57 | 9.13 | 78.91% | 0 | 0%
GNA_083631103_Capacity | South Bay and Central Coast | De Anza | WHISMAN 1103 | 83631103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083631104_Capacity | South Bay and Central Coast | De Anza | WHISMAN 1104 | 83631104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0836302_Capacity | South Bay and Central Coast | De Anza | WHISMAN BANK 2 | 836302 | Bank | None | None | None | 80.03% | 0 | 0% | 29.7 | 22.22 | 74.81% | 0 | 0% | 29.7 | 23.16 | 77.98% | 0 | 0% | 29.7 | 23.17 | 78.01% | 0 | 0% | 29.7 | 23.59 | 79.43% | 0 | 0% | 29.7 | 23.77 | 80.03% | 0 | 0%
GNA_083631105_Capacity | South Bay and Central Coast | De Anza | WHISMAN 1105 | 83631105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083631106_Capacity | South Bay and Central Coast | De Anza | WHISMAN 1106 | 83631106 | Feeder | None | None | None | 97.75% | 0 | 0% | 11.57 | 10.85 | 93.78% | 0 | 0% | 11.57 | 10.94 | 94.55% | 0 | 0% | 11.57 | 11.02 | 95.25% | 0 | 0% | 11.57 | 11.18 | 96.63% | 0 | 0% | 11.57 | 11.31 | 97.75% | 0 | 0%
GNA_083631108_Capacity | South Bay and Central Coast | De Anza | WHISMAN 1108 | 83631108 | Feeder | None | None | None | 53.33% | 0 | 0% | 11.57 | 5.28 | 45.64% | 0 | 0% | 11.57 | 5.39 | 46.59% | 0 | 0% | 11.57 | 5.5 | 47.54% | 0 | 0% | 11.57 | 6.01 | 51.94% | 0 | 0% | 11.57 | 6.17 | 53.33% | 0 | 0%
GNA_0836303_Capacity | South Bay and Central Coast | De Anza | WHISMAN BANK 3 | 836303 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083631109_Capacity | South Bay and Central Coast | De Anza | WHISMAN 1109 | 83631109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083631110_Capacity | South Bay and Central Coast | De Anza | WHISMAN 1110 | 83631110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083631111_Capacity | South Bay and Central Coast | De Anza | WHISMAN 1111 | 83631111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083631112_Capacity | South Bay and Central Coast | De Anza | WHISMAN 1112 | 83631112 | Feeder | Demand Growth | Capacity | 2027 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0836101_Capacity | South Bay and Central Coast | De Anza | BRITTON BANK 1 | 836101 | Bank | Demand Growth | Capacity | 2025 | 103.2% | 0.94 | 3.165% | 29.7 | 27.88 | 93.87% | 0 | 0% | 29.7 | 29.56 | 99.53% | 0 | 0% | 29.7 | 30.64 | 103.2% | 0.94 | 3.165% | 29.7 | 29.57 | 99.56% | 0 | 0% | 29.7 | 30.03 | 101.1% | 0.33 | 1.111%
GNA_083611104_Capacity | South Bay and Central Coast | De Anza | BRITTON 1104 | 83611104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083611105_Capacity | South Bay and Central Coast | De Anza | BRITTON 1105 | 83611105 | Feeder | None | None | None | 93.26% | 0 | 0% | 11.57 | 8.35 | 72.17% | 0 | 0% | 11.57 | 9.12 | 78.82% | 0 | 0% | 11.57 | 10.52 | 90.92% | 0 | 0% | 11.57 | 10.66 | 92.13% | 0 | 0% | 11.57 | 10.79 | 93.26% | 0 | 0%
GNA_083611106_Capacity | South Bay and Central Coast | De Anza | BRITTON 1106 | 83611106 | Feeder | None | None | None | 84.25% | 0 | 0% | 12.19 | 9.18 | 75.31% | 0 | 0% | 12.19 | 10.27 | 84.25% | 0 | 0% | 12.19 | 9.86 | 80.89% | 0 | 0% | 12.19 | 8.37 | 68.66% | 0 | 0% | 12.19 | 8.6 | 70.55% | 0 | 0%
GNA_0836102_Capacity | South Bay and Central Coast | De Anza | BRITTON BANK 2 | 836102 | Bank | None | None | None | 91.93% | 0 | 0% | 44.6 | 37.95 | 85.09% | 0 | 0% | 44.6 | 39.83 | 89.3% | 0 | 0% | 44.6 | 31.69 | 71.05% | 0 | 0% | 44.6 | 36.31 | 81.41% | 0 | 0% | 44.6 | 41 | 91.93% | 0 | 0%
GNA_083611107_Capacity | South Bay and Central Coast | De Anza | BRITTON 1107 | 83611107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083611108_Capacity | South Bay and Central Coast | De Anza | BRITTON 1108 | 83611108 | Feeder | None | None | None | 92.83% | 0 | 0% | 11.57 | 9.47 | 81.85% | 0 | 0% | 11.57 | 10.26 | 88.68% | 0 | 0% | 11.57 | 7.6 | 65.69% | 0 | 0% | 11.57 | 8.95 | 77.36% | 0 | 0% | 11.57 | 10.74 | 92.83% | 0 | 0%
GNA_083611109_Capacity | South Bay and Central Coast | De Anza | BRITTON 1109 | 83611109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083611110_Capacity | South Bay and Central Coast | De Anza | BRITTON 1110 | 83611110 | Feeder | None | None | None | 86.43% | 0 | 0% | 11.57 | 8.84 | 76.4% | 0 | 0% | 11.57 | 9.13 | 78.91% | 0 | 0% | 11.57 | 9.39 | 81.16% | 0 | 0% | 11.57 | 9.7 | 83.84% | 0 | 0% | 11.57 | 10 | 86.43% | 0 | 0%
GNA_083611111_Capacity | South Bay and Central Coast | De Anza | BRITTON 1111 | 83611111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0836103_Capacity | South Bay and Central Coast | De Anza | BRITTON BANK 3 | 836103 | Bank | None | None | None | 99.97% | 0 | 0% | 37.4 | 34.15 | 91.31% | 0 | 0% | 37.4 | 36.44 | 97.43% | 0 | 0% | 37.4 | 36.91 | 98.69% | 0 | 0% | 37.4 | 36.98 | 98.88% | 0 | 0% | 37.4 | 37.39 | 99.97% | 0 | 0%
GNA_083611112_Capacity | South Bay and Central Coast | De Anza | BRITTON 1112 | 83611112 | Feeder | None | None | None | 99.05% | 0 | 0% | 11.57 | 8.8 | 76.06% | 0 | 0% | 11.57 | 10.92 | 94.38% | 0 | 0% | 11.57 | 10.98 | 94.9% | 0 | 0% | 11.57 | 11.06 | 95.59% | 0 | 0% | 11.57 | 11.46 | 99.05% | 0 | 0%
GNA_083611113_Capacity | South Bay and Central Coast | De Anza | BRITTON 1113 | 83611113 | Feeder | None | None | None | 97.23% | 0 | 0% | 11.57 | 10.84 | 93.69% | 0 | 0% | 11.57 | 10.82 | 93.52% | 0 | 0% | 11.57 | 11.25 | 97.23% | 0 | 0% | 11.57 | 11.24 | 97.15% | 0 | 0% | 11.57 | 11.22 | 96.97% | 0 | 0%
GNA_083611114_Capacity | South Bay and Central Coast | De Anza | BRITTON 1114 | 83611114 | Feeder | None | None | None | 91.36% | 0 | 0% | 11.57 | 10.35 | 89.46% | 0 | 0% | 11.57 | 10.55 | 91.18% | 0 | 0% | 11.57 | 10.53 | 91.01% | 0 | 0% | 11.57 | 10.54 | 91.1% | 0 | 0% | 11.57 | 10.57 | 91.36% | 0 | 0%
GNA_083611115_Capacity | South Bay and Central Coast | De Anza | BRITTON 1115 | 83611115 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0834201_Capacity | South Bay and Central Coast | De Anza | LAWRENCE BANK 1 | 834201 | Bank | None | None | None | 93.68% | 0 | 0% | 44.6 | 39.87 | 89.39% | 0 | 0% | 44.6 | 41.47 | 92.98% | 0 | 0% | 44.6 | 41.5 | 93.05% | 0 | 0% | 44.6 | 41.65 | 93.39% | 0 | 0% | 44.6 | 41.78 | 93.68% | 0 | 0%
GNA_083421102_Capacity | South Bay and Central Coast | De Anza | LAWRENCE 1102 | 83421102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083421103_Capacity | South Bay and Central Coast | De Anza | LAWRENCE 1103 | 83421103 | Feeder | None | None | None | 66.64% | 0 | 0% | 11.57 | 7.71 | 66.64% | 0 | 0% | 11.57 | 7.71 | 66.64% | 0 | 0% | 11.57 | 7.7 | 66.55% | 0 | 0% | 11.57 | 7.7 | 66.55% | 0 | 0% | 11.57 | 7.69 | 66.46% | 0 | 0%
GNA_083421104_Capacity | South Bay and Central Coast | De Anza | LAWRENCE 1104 | 83421104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083421105_Capacity | South Bay and Central Coast | De Anza | LAWRENCE 1105 | 83421105 | Feeder | None | None | None | 99.65% | 0 | 0% | 11.57 | 9.48 | 81.94% | 0 | 0% | 11.57 | 11.13 | 96.2% | 0 | 0% | 11.57 | 11.2 | 96.8% | 0 | 0% | 11.57 | 11.36 | 98.18% | 0 | 0% | 11.57 | 11.53 | 99.65% | 0 | 0%
GNA_0834202_Capacity | South Bay and Central Coast | De Anza | LAWRENCE BANK 2 | 834202 | Bank | None | None | None | 64.15% | 0 | 0% | 44.6 | 23.48 | 52.65% | 0 | 0% | 44.6 | 24.35 | 54.6% | 0 | 0% | 44.6 | 28.61 | 64.15% | 0 | 0% | 44.6 | 28.55 | 64.01% | 0 | 0% | 44.6 | 28.5 | 63.9% | 0 | 0%
GNA_083421106_Capacity | South Bay and Central Coast | De Anza | LAWRENCE 1106 | 83421106 | Feeder | None | None | None | 86.96% | 0 | 0% | 12.19 | 9.61 | 78.84% | 0 | 0% | 12.19 | 10.6 | 86.96% | 0 | 0% | 12.19 | 10.58 | 86.79% | 0 | 0% | 12.19 | 10.55 | 86.55% | 0 | 0% | 12.19 | 10.53 | 86.38% | 0 | 0%
GNA_083421107_Capacity | South Bay and Central Coast | De Anza | LAWRENCE 1107 | 83421107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083421108_Capacity | South Bay and Central Coast | De Anza | LAWRENCE 1108 | 83421108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083421109_Capacity | South Bay and Central Coast | De Anza | LAWRENCE 1109 | 83421109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0834203_Capacity | South Bay and Central Coast | De Anza | LAWRENCE BANK 3 | 834203 | Bank | None | None | None | 66.72% | 0 | 0% | 47.53 | 24.62 | 51.8% | 0 | 0% | 47.53 | 26.61 | 55.99% | 0 | 0% | 47.53 | 31.69 | 66.67% | 0 | 0% | 47.53 | 31.31 | 65.87% | 0 | 0% | 47.53 | 31.71 | 66.72% | 0 | 0%
GNA_083421110_Capacity | South Bay and Central Coast | De Anza | LAWRENCE 1110 | 83421110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083421111_Capacity | South Bay and Central Coast | De Anza | LAWRENCE 1111 | 83421111 | Feeder | None | None | None | 77.86% | 0 | 0% | 9.71 | 6.96 | 71.68% | 0 | 0% | 9.71 | 7.54 | 77.65% | 0 | 0% | 9.71 | 7.52 | 77.45% | 0 | 0% | 9.71 | 7.54 | 77.65% | 0 | 0% | 9.71 | 7.56 | 77.86% | 0 | 0%
GNA_083421112_Capacity | South Bay and Central Coast | De Anza | LAWRENCE 1112 | 83421112 | Feeder | Demand Growth | Capacity | 2025 | 141.5% | 4.8 | 41.49% | 11.57 | 10.16 | 87.81% | 0 | 0% | 11.57 | 11.07 | 95.68% | 0 | 0% | 11.57 | 16.33 | 141.1% | 4.76 | 41.14% | 11.57 | 16 | 138.3% | 4.43 | 38.29% | 11.57 | 16.37 | 141.5% | 4.8 | 41.49%
GNA_083421113_Capacity | South Bay and Central Coast | De Anza | LAWRENCE 1113 | 83421113 | Feeder | None | None | None | 88.02% | 0 | 0% | 12.19 | 10.71 | 87.86% | 0 | 0% | 12.19 | 10.69 | 87.69% | 0 | 0% | 12.19 | 10.66 | 87.45% | 0 | 0% | 12.19 | 10.69 | 87.69% | 0 | 0% | 12.19 | 10.73 | 88.02% | 0 | 0%
GNA_0829901_Capacity | South Bay and Central Coast | De Anza | LOCKHEED NO.1 BANK 1 | 829901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082991105_Capacity | South Bay and Central Coast | De Anza | LOCKHEED NO 1 1105 | 82991105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0829902_Capacity | South Bay and Central Coast | De Anza | LOCKHEED NO.1 BANK 2 | 829902 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082991107_Capacity | South Bay and Central Coast | De Anza | LOCKHEED NO 1 1107 | 82991107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0830001_Capacity | South Bay and Central Coast | De Anza | LOCKHEED NO.2 BANK 1 | 830001 | Bank | None | None | None | 77.41% | 0 | 0% | 29.7 | 12.28 | 41.35% | 0 | 0% | 29.7 | 12.7 | 42.76% | 0 | 0% | 29.7 | 18.23 | 61.38% | 0 | 0% | 29.7 | 18.23 | 61.38% | 0 | 0% | 29.7 | 22.99 | 77.41% | 0 | 0%
GNA_083001106_Capacity | South Bay and Central Coast | De Anza | LOCKHEED NO 2 1106 | 83001106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083001107_Capacity | South Bay and Central Coast | De Anza | LOCKHEED NO 2 1107 | 83001107 | Feeder | None | None | None | 80.56% | 0 | 0% | 12.19 | 8.45 | 69.32% | 0 | 0% | 12.19 | 8.61 | 70.63% | 0 | 0% | 12.19 | 9.82 | 80.56% | 0 | 0% | 12.19 | 9.82 | 80.56% | 0 | 0% | 12.19 | 9.82 | 80.56% | 0 | 0%
GNA_083001108_Capacity | South Bay and Central Coast | De Anza | LOCKHEED NO 2 1108 | 83001108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0141001_Capacity | Bay Area | Diablo | ALHAMBRA BANK 1 | 141001 | Bank | None | None | None | 94.81% | 0 | 0% | 15.8 | 14.98 | 94.81% | 0 | 0% | 15.8 | 14.91 | 94.37% | 0 | 0% | 15.8 | 14.87 | 94.11% | 0 | 0% | 15.8 | 14.9 | 94.3% | 0 | 0% | 15.8 | 14.97 | 94.75% | 0 | 0%
GNA_014101101_Capacity | Bay Area | Diablo | ALHAMBRA 1101 | 14101101 | Feeder | None | None | None | 52.49% | 0 | 0% | 10.46 | 5.49 | 52.49% | 0 | 0% | 10.46 | 5.44 | 52.01% | 0 | 0% | 10.46 | 5.41 | 51.72% | 0 | 0% | 10.46 | 5.43 | 51.91% | 0 | 0% | 10.46 | 5.48 | 52.39% | 0 | 0%
GNA_014101102_Capacity | Bay Area | Diablo | ALHAMBRA 1102 | 14101102 | Feeder | None | None | None | 76.46% | 0 | 0% | 12.19 | 9.32 | 76.46% | 0 | 0% | 12.19 | 9.23 | 75.72% | 0 | 0% | 12.19 | 9.19 | 75.39% | 0 | 0% | 12.19 | 9.2 | 75.47% | 0 | 0% | 12.19 | 9.21 | 75.55% | 0 | 0%
GNA_0141002_Capacity | Bay Area | Diablo | ALHAMBRA BANK 2 | 141002 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014101105_Capacity | Bay Area | Diablo | ALHAMBRA 1105 | 14101105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0143201_Capacity | Bay Area | Diablo | BALFOUR BANK 1 | 143201 | Bank | None | None | None | 47.88% | 0 | 0% | 5.2 | 2.49 | 47.88% | 0 | 0% | 5.2 | 2.48 | 47.69% | 0 | 0% | 5.2 | 2.48 | 47.69% | 0 | 0% | 5.2 | 2.49 | 47.88% | 0 | 0% | 5.2 | 2.49 | 47.88% | 0 | 0%
GNA_014321101_Capacity | Bay Area | Diablo | BALFOUR 1101 | 14321101 | Feeder | None | None | None | 49.9% | 0 | 0% | 5.15 | 2.57 | 49.9% | 0 | 0% | 5.15 | 2.56 | 49.71% | 0 | 0% | 5.15 | 2.56 | 49.71% | 0 | 0% | 5.15 | 2.56 | 49.71% | 0 | 0% | 5.15 | 2.57 | 49.9% | 0 | 0%
GNA_0145901_Capacity | Bay Area | Diablo | BRENTWOOD BANK 1 | 145901 | Bank | None | None | None | 75.73% | 0 | 0% | 67.98 | 47.5 | 69.87% | 0 | 0% | 67.98 | 50.94 | 74.93% | 0 | 0% | 67.98 | 50.98 | 74.99% | 0 | 0% | 67.98 | 51.15 | 75.24% | 0 | 0% | 67.98 | 51.48 | 75.73% | 0 | 0%
GNA_014592104_Capacity | Bay Area | Diablo | BRENTWOOD 2104 | 14592104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014592105_Capacity | Bay Area | Diablo | BRENTWOOD 2105 | 14592105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014592106_Capacity | Bay Area | Diablo | BRENTWOOD 2106 | 14592106 | Feeder | None | None | None | 99.11% | 0 | 0% | 21.41 | 21.22 | 99.11% | 0 | 0% | 21.41 | 20.96 | 97.9% | 0 | 0% | 21.41 | 20.77 | 97.01% | 0 | 0% | 21.41 | 20.79 | 97.1% | 0 | 0% | 21.41 | 21.01 | 98.13% | 0 | 0%
GNA_0145902_Capacity | Bay Area | Diablo | BRENTWOOD BANK 2 | 145902 | Bank | None | None | None | 84.86% | 0 | 0% | 67.98 | 57.16 | 84.08% | 0 | 0% | 67.98 | 57.41 | 84.45% | 0 | 0% | 67.98 | 57.31 | 84.3% | 0 | 0% | 67.98 | 57.46 | 84.52% | 0 | 0% | 67.98 | 57.69 | 84.86% | 0 | 0%
GNA_014592108_Capacity | Bay Area | Diablo | BRENTWOOD 2108 | 14592108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014592109_Capacity | Bay Area | Diablo | BRENTWOOD 2109 | 14592109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014592110_Capacity | Bay Area | Diablo | BRENTWOOD 2110 | 14592110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014592111_Capacity | Bay Area | Diablo | BRENTWOOD 2111 | 14592111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0145903_Capacity | Bay Area | Diablo | BRENTWOOD BANK 3 | 145903 | Bank | None | None | None | 67.53% | 0 | 0% | 58.8 | 38.39 | 65.29% | 0 | 0% | 58.8 | 37.53 | 63.83% | 0 | 0% | 58.8 | 37.79 | 64.27% | 0 | 0% | 58.8 | 39.71 | 67.53% | 0 | 0% | 58.8 | 39.69 | 67.5% | 0 | 0%
GNA_014592112_Capacity | Bay Area | Diablo | BRENTWOOD 2112 | 14592112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_018150401_Capacity | Bay Area | Diablo | BETHEL BANK 0401 | 18150401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_018320401_Capacity | Bay Area | Diablo | JERSEY ISLAND 0401 | 18320401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_018120401_Capacity | Bay Area | Diablo | PIPER BANK 0401 | 18120401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014592113_Capacity | Bay Area | Diablo | BRENTWOOD 2113 | 14592113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0136508_Capacity | Bay Area | Diablo | CONTRA COSTA BANK 8 | 136508 | Bank | None | None | None | 49.49% | 0 | 0% | 74.3 | 35.77 | 48.14% | 0 | 0% | 74.3 | 36.4 | 48.99% | 0 | 0% | 74.3 | 36.46 | 49.07% | 0 | 0% | 74.3 | 36.58 | 49.23% | 0 | 0% | 74.3 | 36.77 | 49.49% | 0 | 0%
GNA_013652107_Capacity | Bay Area | Diablo | CONTRA COSTA 2107 | 13652107 | Feeder | Demand Growth | Capacity | 2024 | 101.9% | 0.4 | 1.885% | 21.22 | 21.01 | 99.01% | 0 | 0% | 21.22 | 21.62 | 101.9% | 0.4 | 1.885% | 21.22 | 21.56 | 101.6% | 0.34 | 1.602% | 21.22 | 21.52 | 101.4% | 0.3 | 1.414% | 21.22 | 21.49 | 101.3% | 0.27 | 1.272%
GNA_013652110_Capacity | Bay Area | Diablo | CONTRA COSTA 2110 | 13652110 | Feeder | None | None | None | 95.01% | 0 | 0% | 18.63 | 17.7 | 95.01% | 0 | 0% | 18.63 | 17.5 | 93.93% | 0 | 0% | 18.63 | 17.31 | 92.91% | 0 | 0% | 18.63 | 17.05 | 91.52% | 0 | 0% | 18.63 | 17.1 | 91.79% | 0 | 0%
GNA_0136509_Capacity | Bay Area | Diablo | CONTRA COSTA BANK 9 | 136509 | Bank | None | None | None | 87.56% | 0 | 0% | 74.3 | 63.51 | 85.48% | 0 | 0% | 74.3 | 64.84 | 87.27% | 0 | 0% | 74.3 | 65.06 | 87.56% | 0 | 0% | 74.3 | 63.4 | 85.33% | 0 | 0% | 74.3 | 63.92 | 86.03% | 0 | 0%
GNA_013652109_Capacity | Bay Area | Diablo | CONTRA COSTA 2109 | 13652109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013652112_Capacity | Bay Area | Diablo | CONTRA COSTA 2112 | 13652112 | Feeder | Demand Growth | Capacity | 2024 | 103% | 0.64 | 2.989% | 21.41 | 21.15 | 98.79% | 0 | 0% | 21.41 | 21.74 | 101.5% | 0.33 | 1.541% | 21.41 | 21.8 | 101.8% | 0.39 | 1.822% | 21.41 | 21.91 | 102.3% | 0.5 | 2.335% | 21.41 | 22.05 | 103% | 0.64 | 2.989%
GNA_013652113_Capacity | Bay Area | Diablo | CONTRA COSTA 2113 | 13652113 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0132301_Capacity | Bay Area | Diablo | LONE TREE BANK 1 | 132301 | Bank | Demand Growth | Capacity | 2023 | 115.2% | 6.79 | 15.22% | 44.6 | 48.71 | 109.2% | 4.11 | 9.215% | 44.6 | 51.03 | 114.4% | 6.43 | 14.42% | 44.6 | 51.1 | 114.6% | 6.5 | 14.57% | 44.6 | 51.2 | 114.8% | 6.6 | 14.8% | 44.6 | 51.39 | 115.2% | 6.79 | 15.22%
GNA_013232101_Capacity | Bay Area | Diablo | LONE TREE 2101 | 13232101 | Feeder | None | None | None | 92.89% | 0 | 0% | 21.11 | 19.36 | 91.71% | 0 | 0% | 21.11 | 19.42 | 91.99% | 0 | 0% | 21.11 | 19.47 | 92.23% | 0 | 0% | 21.11 | 19.56 | 92.66% | 0 | 0% | 21.11 | 19.61 | 92.89% | 0 | 0%
GNA_013232102_Capacity | Bay Area | Diablo | LONE TREE 2102 | 13232102 | Feeder | Demand Growth | Capacity | 2023 | 150% | 10.55 | 49.98% | 21.11 | 29.23 | 138.5% | 8.12 | 38.47% | 21.11 | 31.49 | 149.2% | 10.38 | 49.17% | 21.11 | 31.5 | 149.2% | 10.39 | 49.22% | 21.11 | 31.53 | 149.4% | 10.42 | 49.36% | 21.11 | 31.66 | 150% | 10.55 | 49.98%
GNA_0132302_Capacity | Bay Area | Diablo | LONE TREE BANK 2 | 132302 | Bank | None | None | None | 45.63% | 0 | 0% | 44.6 | 20.15 | 45.18% | 0 | 0% | 44.6 | 20.16 | 45.2% | 0 | 0% | 44.6 | 20.21 | 45.31% | 0 | 0% | 44.6 | 20.23 | 45.36% | 0 | 0% | 44.6 | 20.35 | 45.63% | 0 | 0%
GNA_013232105_Capacity | Bay Area | Diablo | LONE TREE 2105 | 13232105 | Feeder | None | None | None | 97.39% | 0 | 0% | 21.11 | 20.36 | 96.45% | 0 | 0% | 21.11 | 20.37 | 96.49% | 0 | 0% | 21.11 | 20.42 | 96.73% | 0 | 0% | 21.11 | 20.44 | 96.83% | 0 | 0% | 21.11 | 20.56 | 97.39% | 0 | 0%
GNA_0120205_Capacity | Bay Area | Diablo | CLAYTON BANK 5 | 120205 | Bank | None | None | None | 63.67% | 0 | 0% | 15.8 | 10.06 | 63.67% | 0 | 0% | 15.8 | 9.97 | 63.1% | 0 | 0% | 15.8 | 9.9 | 62.66% | 0 | 0% | 15.8 | 9.94 | 62.91% | 0 | 0% | 15.8 | 10.03 | 63.48% | 0 | 0%
GNA_012021103_Capacity | Bay Area | Diablo | CLAYTON 1103 | 12021103 | Feeder | None | None | None | 57.94% | 0 | 0% | 5.73 | 3.32 | 57.94% | 0 | 0% | 5.73 | 3.28 | 57.24% | 0 | 0% | 5.73 | 3.26 | 56.89% | 0 | 0% | 5.73 | 3.25 | 56.72% | 0 | 0% | 5.73 | 3.27 | 57.07% | 0 | 0%
GNA_012021104_Capacity | Bay Area | Diablo | CLAYTON 1104 | 12021104 | Feeder | None | None | None | 76.5% | 0 | 0% | 9.02 | 6.79 | 75.28% | 0 | 0% | 9.02 | 6.79 | 75.28% | 0 | 0% | 9.02 | 6.8 | 75.39% | 0 | 0% | 9.02 | 6.83 | 75.72% | 0 | 0% | 9.02 | 6.9 | 76.5% | 0 | 0%
GNA_0139101_Capacity | Bay Area | Diablo | WILLOW PASS BANK 1 | 139101 | Bank | None | None | None | 99.09% | 0 | 0% | 9.85 | 9.51 | 96.55% | 0 | 0% | 9.85 | 9.58 | 97.26% | 0 | 0% | 9.85 | 9.65 | 97.97% | 0 | 0% | 9.85 | 9.69 | 98.38% | 0 | 0% | 9.85 | 9.76 | 99.09% | 0 | 0%
GNA_013911101_Capacity | Bay Area | Diablo | WILLOW PASS 1101 | 13911101 | Feeder | None | None | None | 56.03% | 0 | 0% | 10.69 | 5.71 | 53.41% | 0 | 0% | 10.69 | 5.79 | 54.16% | 0 | 0% | 10.69 | 5.86 | 54.82% | 0 | 0% | 10.69 | 5.92 | 55.38% | 0 | 0% | 10.69 | 5.99 | 56.03% | 0 | 0%
GNA_013911102_Capacity | Bay Area | Diablo | WILLOW PASS 1102 | 13911102 | Feeder | None | None | None | 41.35% | 0 | 0% | 10.69 | 4.42 | 41.35% | 0 | 0% | 10.69 | 4.41 | 41.25% | 0 | 0% | 10.69 | 4.41 | 41.25% | 0 | 0% | 10.69 | 4.39 | 41.07% | 0 | 0% | 10.69 | 4.38 | 40.97% | 0 | 0%
GNA_0120201_Capacity | Bay Area | Diablo | CLAYTON BANK 1 | 120201 | Bank | None | None | None | 91.08% | 0 | 0% | 44.6 | 40.62 | 91.08% | 0 | 0% | 44.6 | 40.22 | 90.18% | 0 | 0% | 44.6 | 40.01 | 89.71% | 0 | 0% | 44.6 | 39.95 | 89.57% | 0 | 0% | 44.6 | 40.04 | 89.78% | 0 | 0%
GNA_012022213_Capacity | Bay Area | Diablo | CLAYTON 2213 | 12022213 | Feeder | None | None | None | 78.37% | 0 | 0% | 18.63 | 14.6 | 78.37% | 0 | 0% | 18.63 | 14.39 | 77.24% | 0 | 0% | 18.63 | 14.25 | 76.49% | 0 | 0% | 18.63 | 14.23 | 76.38% | 0 | 0% | 18.63 | 14.25 | 76.49% | 0 | 0%
GNA_012022216_Capacity | Bay Area | Diablo | CLAYTON 2216 | 12022216 | Feeder | None | None | None | 88.29% | 0 | 0% | 23.56 | 20.8 | 88.29% | 0 | 0% | 23.56 | 20.53 | 87.14% | 0 | 0% | 23.56 | 20.31 | 86.21% | 0 | 0% | 23.56 | 20.15 | 85.53% | 0 | 0% | 23.56 | 20.1 | 85.31% | 0 | 0%
GNA_012022218_Capacity | Bay Area | Diablo | CLAYTON 2218 | 12022218 | Feeder | None | None | None | 30.45% | 0 | 0% | 21.41 | 6.52 | 30.45% | 0 | 0% | 21.41 | 6.47 | 30.22% | 0 | 0% | 21.41 | 6.43 | 30.03% | 0 | 0% | 21.41 | 6.42 | 29.99% | 0 | 0% | 21.41 | 6.43 | 30.03% | 0 | 0%
GNA_0120202_Capacity | Bay Area | Diablo | CLAYTON BANK 2 | 120202 | Bank | None | None | None | 88.74% | 0 | 0% | 44.6 | 39.58 | 88.74% | 0 | 0% | 44.6 | 38.8 | 87% | 0 | 0% | 44.6 | 38.79 | 86.97% | 0 | 0% | 44.6 | 38.98 | 87.4% | 0 | 0% | 44.6 | 39.37 | 88.27% | 0 | 0%
GNA_012022215_Capacity | Bay Area | Diablo | CLAYTON 2215 | 12022215 | Feeder | None | None | None | 94.4% | 0 | 0% | 23.56 | 22.24 | 94.4% | 0 | 0% | 23.56 | 21.68 | 92.02% | 0 | 0% | 23.56 | 21.59 | 91.64% | 0 | 0% | 23.56 | 21.78 | 92.44% | 0 | 0% | 23.56 | 22.14 | 93.97% | 0 | 0%
GNA_012022217_Capacity | Bay Area | Diablo | CLAYTON 2217 | 12022217 | Feeder | None | None | None | 93.61% | 0 | 0% | 18.63 | 17.44 | 93.61% | 0 | 0% | 18.63 | 17.18 | 92.22% | 0 | 0% | 18.63 | 17 | 91.25% | 0 | 0% | 18.63 | 16.84 | 90.39% | 0 | 0% | 18.63 | 16.85 | 90.45% | 0 | 0%
GNA_0120203_Capacity | Bay Area | Diablo | CLAYTON BANK 3 | 120203 | Bank | None | None | None | 96.41% | 0 | 0% | 44.6 | 43 | 96.41% | 0 | 0% | 44.6 | 42.74 | 95.83% | 0 | 0% | 44.6 | 42.49 | 95.27% | 0 | 0% | 44.6 | 42.36 | 94.98% | 0 | 0% | 44.6 | 42.38 | 95.02% | 0 | 0%
GNA_012022211_Capacity | Bay Area | Diablo | CLAYTON 2211 | 12022211 | Feeder | None | None | None | 71.96% | 0 | 0% | 21.11 | 15.19 | 71.96% | 0 | 0% | 21.11 | 15.15 | 71.77% | 0 | 0% | 21.11 | 15.09 | 71.48% | 0 | 0% | 21.11 | 15.04 | 71.25% | 0 | 0% | 21.11 | 15.02 | 71.15% | 0 | 0%
GNA_012022212_Capacity | Bay Area | Diablo | CLAYTON 2212 | 12022212 | Feeder | None | None | None | 70.3% | 0 | 0% | 25.93 | 18.23 | 70.3% | 0 | 0% | 25.93 | 17.83 | 68.76% | 0 | 0% | 25.93 | 17.71 | 68.3% | 0 | 0% | 25.93 | 17.67 | 68.15% | 0 | 0% | 25.93 | 17.74 | 68.41% | 0 | 0%
GNA_012022214_Capacity | Bay Area | Diablo | CLAYTON 2214 | 12022214 | Feeder | None | None | None | 53.46% | 0 | 0% | 18.63 | 9.96 | 53.46% | 0 | 0% | 18.63 | 9.91 | 53.19% | 0 | 0% | 18.63 | 9.85 | 52.87% | 0 | 0% | 18.63 | 9.81 | 52.66% | 0 | 0% | 18.63 | 9.82 | 52.71% | 0 | 0%
GNA_0138501_Capacity | Bay Area | Diablo | BABEL BANK 1 | 138501 | Bank | None | None | None | 76.32% | 0 | 0% | 2.28 | 1.74 | 76.32% | 0 | 0% | 2.28 | 1.71 | 75% | 0 | 0% | 2.28 | 1.67 | 73.25% | 0 | 0% | 2.28 | 1.64 | 71.93% | 0 | 0% | 2.28 | 1.64 | 71.93% | 0 | 0%
GNA_013850401_Capacity | Bay Area | Diablo | BABEL 0401 | 13850401 | Feeder | None | None | None | 63.84% | 0 | 0% | 2.71 | 1.73 | 63.84% | 0 | 0% | 2.71 | 1.7 | 62.73% | 0 | 0% | 2.71 | 1.66 | 61.25% | 0 | 0% | 2.71 | 1.64 | 60.52% | 0 | 0% | 2.71 | 1.64 | 60.52% | 0 | 0%
GNA_0134305_Capacity | Bay Area | Diablo | FAIRVIEW BANK 5 | 134305 | Bank | None | None | None | 84.98% | 0 | 0% | 47 | 39.94 | 84.98% | 0 | 0% | 47 | 39.53 | 84.11% | 0 | 0% | 47 | 39.17 | 83.34% | 0 | 0% | 47 | 39.16 | 83.32% | 0 | 0% | 47 | 39.35 | 83.72% | 0 | 0%
GNA_013432206_Capacity | Bay Area | Diablo | FAIRVIEW 2206 | 13432206 | Feeder | None | None | None | 80.58% | 0 | 0% | 21.11 | 16.49 | 78.11% | 0 | 0% | 21.11 | 16.47 | 78.02% | 0 | 0% | 21.11 | 16.57 | 78.49% | 0 | 0% | 21.11 | 16.75 | 79.35% | 0 | 0% | 21.11 | 17.01 | 80.58% | 0 | 0%
GNA_013432207_Capacity | Bay Area | Diablo | FAIRVIEW 2207 | 13432207 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013432208_Capacity | Bay Area | Diablo | FAIRVIEW 2208 | 13432208 | Feeder | None | None | None | 65.84% | 0 | 0% | 22.22 | 14.63 | 65.84% | 0 | 0% | 22.22 | 14.51 | 65.3% | 0 | 0% | 22.22 | 14.36 | 64.63% | 0 | 0% | 22.22 | 14.25 | 64.13% | 0 | 0% | 22.22 | 14.24 | 64.09% | 0 | 0%
GNA_0135301_Capacity | Bay Area | Diablo | LAKEWOOD BANK 1 | 135301 | Bank | None | None | None | 88.95% | 0 | 0% | 44.6 | 38.15 | 85.54% | 0 | 0% | 44.6 | 39.64 | 88.88% | 0 | 0% | 44.6 | 39.55 | 88.68% | 0 | 0% | 44.6 | 39.54 | 88.65% | 0 | 0% | 44.6 | 39.67 | 88.95% | 0 | 0%
GNA_013532225_Capacity | Bay Area | Diablo | LAKEWOOD 2225 | 13532225 | Feeder | None | None | None | 92.32% | 0 | 0% | 18.11 | 15.15 | 83.66% | 0 | 0% | 18.11 | 16.72 | 92.32% | 0 | 0% | 18.11 | 16.7 | 92.21% | 0 | 0% | 18.11 | 16.68 | 92.1% | 0 | 0% | 18.11 | 16.7 | 92.21% | 0 | 0%
GNA_013532226_Capacity | Bay Area | Diablo | LAKEWOOD 2226 | 13532226 | Feeder | None | None | None | 89.03% | 0 | 0% | 18.59 | 16.55 | 89.03% | 0 | 0% | 18.59 | 16.5 | 88.76% | 0 | 0% | 18.59 | 16.45 | 88.49% | 0 | 0% | 18.59 | 16.44 | 88.43% | 0 | 0% | 18.59 | 16.51 | 88.81% | 0 | 0%
GNA_0122003_Capacity | Bay Area | Diablo | WALNUT CREEK BANK 3 | 122003 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012200404_Capacity | Bay Area | Diablo | WALNUT CREEK 0404 | 12200404 | Feeder | None | None | None | 93.7% | 0 | 0% | 2.38 | 2.23 | 93.7% | 0 | 0% | 2.38 | 2.17 | 91.18% | 0 | 0% | 2.38 | 2.17 | 91.18% | 0 | 0% | 2.38 | 2.17 | 91.18% | 0 | 0% | 2.38 | 2.2 | 92.44% | 0 | 0%
GNA_013532227_Capacity | Bay Area | Diablo | LAKEWOOD 2227 | 13532227 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0135304_Capacity | Bay Area | Diablo | LAKEWOOD BANK 4 | 135304 | Bank | None | None | None | 72.44% | 0 | 0% | 49.5 | 35.49 | 71.7% | 0 | 0% | 49.5 | 35.4 | 71.52% | 0 | 0% | 49.5 | 35.39 | 71.49% | 0 | 0% | 49.5 | 35.55 | 71.82% | 0 | 0% | 49.5 | 35.86 | 72.44% | 0 | 0%
GNA_013532107_Capacity | Bay Area | Diablo | LAKEWOOD 2107 | 13532107 | Feeder | None | None | None | 97.71% | 0 | 0% | 19.63 | 18.79 | 95.72% | 0 | 0% | 19.63 | 18.76 | 95.57% | 0 | 0% | 19.63 | 18.78 | 95.67% | 0 | 0% | 19.63 | 18.9 | 96.28% | 0 | 0% | 19.63 | 19.18 | 97.71% | 0 | 0%
GNA_013532108_Capacity | Bay Area | Diablo | LAKEWOOD 2108 | 13532108 | Feeder | None | None | None | 61.3% | 0 | 0% | 18.63 | 11.42 | 61.3% | 0 | 0% | 18.63 | 11.42 | 61.3% | 0 | 0% | 18.63 | 11.41 | 61.25% | 0 | 0% | 18.63 | 11.41 | 61.25% | 0 | 0% | 18.63 | 11.42 | 61.3% | 0 | 0%
GNA_0122004_Capacity | Bay Area | Diablo | WALNUT CREEK BANK 4 | 122004 | Bank | None | None | None | 7.443% | 0 | 0% | 6.18 | 0.46 | 7.443% | 0 | 0% | 6.18 | 0.46 | 7.443% | 0 | 0% | 6.18 | 0.46 | 7.443% | 0 | 0% | 6.18 | 0.46 | 7.443% | 0 | 0% | 6.18 | 0.45 | 7.282% | 0 | 0%
GNA_012200403_Capacity | Bay Area | Diablo | WALNUT CREEK 0403 | 12200403 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013532109_Capacity | Bay Area | Diablo | LAKEWOOD 2109 | 13532109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0143001_Capacity | Bay Area | Diablo | MEADOW LANE BANK 1 | 143001 | Bank | None | None | None | 80.31% | 0 | 0% | 44.6 | 35.82 | 80.31% | 0 | 0% | 44.6 | 35.5 | 79.6% | 0 | 0% | 44.6 | 35.2 | 78.92% | 0 | 0% | 44.6 | 35.71 | 80.07% | 0 | 0% | 44.6 | 35.52 | 79.64% | 0 | 0%
GNA_014302102_Capacity | Bay Area | Diablo | MEADOW LANE 2102 | 14302102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014302103_Capacity | Bay Area | Diablo | MEADOW LANE 2103 | 14302103 | Feeder | None | None | None | 89.65% | 0 | 0% | 20 | 17.93 | 89.65% | 0 | 0% | 20 | 17.66 | 88.3% | 0 | 0% | 20 | 17.43 | 87.15% | 0 | 0% | 20 | 17.31 | 86.55% | 0 | 0% | 20 | 17.18 | 85.9% | 0 | 0%
GNA_014302104_Capacity | Bay Area | Diablo | MEADOW LANE 2104 | 14302104 | Feeder | None | None | None | 76.06% | 0 | 0% | 18.63 | 13.66 | 73.32% | 0 | 0% | 18.63 | 13.61 | 73.05% | 0 | 0% | 18.63 | 13.55 | 72.73% | 0 | 0% | 18.63 | 14.17 | 76.06% | 0 | 0% | 18.63 | 14.11 | 75.74% | 0 | 0%
GNA_0143002_Capacity | Bay Area | Diablo | MEADOW LANE BANK 2 | 143002 | Bank | None | None | None | 54.24% | 0 | 0% | 74.23 | 39.89 | 53.74% | 0 | 0% | 74.23 | 39.84 | 53.67% | 0 | 0% | 74.23 | 39.83 | 53.66% | 0 | 0% | 74.23 | 40.04 | 53.94% | 0 | 0% | 74.23 | 40.26 | 54.24% | 0 | 0%
GNA_014302105_Capacity | Bay Area | Diablo | MEADOW LANE 2105 | 14302105 | Feeder | None | None | None | 71.01% | 0 | 0% | 18.11 | 12.86 | 71.01% | 0 | 0% | 18.11 | 12.81 | 70.73% | 0 | 0% | 18.11 | 12.81 | 70.73% | 0 | 0% | 18.11 | 12.8 | 70.68% | 0 | 0% | 18.11 | 12.8 | 70.68% | 0 | 0%
GNA_014302106_Capacity | Bay Area | Diablo | MEADOW LANE 2106 | 14302106 | Feeder | None | None | None | 97.68% | 0 | 0% | 18.11 | 17.31 | 95.58% | 0 | 0% | 18.11 | 17.23 | 95.14% | 0 | 0% | 18.11 | 17.23 | 95.14% | 0 | 0% | 18.11 | 17.45 | 96.36% | 0 | 0% | 18.11 | 17.69 | 97.68% | 0 | 0%
GNA_014302107_Capacity | Bay Area | Diablo | MEADOW LANE 2107 | 14302107 | Feeder | None | None | None | 53.69% | 0 | 0% | 16.93 | 9.09 | 53.69% | 0 | 0% | 16.93 | 9.06 | 53.51% | 0 | 0% | 16.93 | 9.05 | 53.46% | 0 | 0% | 16.93 | 9.02 | 53.28% | 0 | 0% | 16.93 | 8.99 | 53.1% | 0 | 0%
GNA_0143003_Capacity | Bay Area | Diablo | MEADOW LANE BANK 3 | 143003 | Bank | None | None | None | 93.96% | 0 | 0% | 49.5 | 46.29 | 93.52% | 0 | 0% | 49.5 | 46.51 | 93.96% | 0 | 0% | 49.5 | 46.08 | 93.09% | 0 | 0% | 49.5 | 45.74 | 92.4% | 0 | 0% | 49.5 | 45.61 | 92.14% | 0 | 0%
GNA_014302108_Capacity | Bay Area | Diablo | MEADOW LANE 2108 | 14302108 | Feeder | None | None | None | 97.13% | 0 | 0% | 18.11 | 17.57 | 97.02% | 0 | 0% | 18.11 | 17.59 | 97.13% | 0 | 0% | 18.11 | 17.28 | 95.42% | 0 | 0% | 18.11 | 17.26 | 95.31% | 0 | 0% | 18.11 | 17.4 | 96.08% | 0 | 0%
GNA_014302109_Capacity | Bay Area | Diablo | MEADOW LANE 2109 | 14302109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014302110_Capacity | Bay Area | Diablo | MEADOW LANE 2110 | 14302110 | Feeder | None | None | None | 81.64% | 0 | 0% | 18.63 | 15.21 | 81.64% | 0 | 0% | 18.63 | 15.18 | 81.48% | 0 | 0% | 18.63 | 15.16 | 81.37% | 0 | 0% | 18.63 | 15.14 | 81.27% | 0 | 0% | 18.63 | 15.13 | 81.21% | 0 | 0%
GNA_0146501_Capacity | Bay Area | Diablo | TIDEWATER BANK 1 | 146501 | Bank | None | None | None | 85.63% | 0 | 0% | 74.3 | 56.46 | 75.99% | 0 | 0% | 74.3 | 57.15 | 76.92% | 0 | 0% | 74.3 | 57.14 | 76.9% | 0 | 0% | 74.3 | 57.1 | 76.85% | 0 | 0% | 74.3 | 63.62 | 85.63% | 0 | 0%
GNA_014652104_Capacity | Bay Area | Diablo | TIDEWATER 2104 | 14652104 | Feeder | None | None | None | 92.4% | 0 | 0% | 23.56 | 18.08 | 76.74% | 0 | 0% | 23.56 | 18.08 | 76.74% | 0 | 0% | 23.56 | 21.77 | 92.4% | 0 | 0% | 23.56 | 21.71 | 92.15% | 0 | 0% | 23.56 | 21.62 | 91.77% | 0 | 0%
GNA_014652105_Capacity | Bay Area | Diablo | TIDEWATER 2105 | 14652105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0135501_Capacity | Bay Area | Diablo | GILL BANK 1 | 135501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013550401_Capacity | Bay Area | Diablo | GILL 0401 | 13550401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0135502_Capacity | Bay Area | Diablo | GILL BANK 2 | 135502 | Bank | None | None | None | 82.82% | 0 | 0% | 2.27 | 1.87 | 82.38% | 0 | 0% | 2.27 | 1.86 | 81.94% | 0 | 0% | 2.27 | 1.87 | 82.38% | 0 | 0% | 2.27 | 1.87 | 82.38% | 0 | 0% | 2.27 | 1.88 | 82.82% | 0 | 0%
GNA_013550402_Capacity | Bay Area | Diablo | GILL 0402 | 13550402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014652106_Capacity | Bay Area | Diablo | TIDEWATER 2106 | 14652106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0146502_Capacity | Bay Area | Diablo | TIDEWATER BANK 2 | 146502 | Bank | None | None | None | 93.92% | 0 | 0% | 74.3 | 69.13 | 93.04% | 0 | 0% | 74.3 | 69.4 | 93.41% | 0 | 0% | 74.3 | 69.73 | 93.85% | 0 | 0% | 74.3 | 69.7 | 93.81% | 0 | 0% | 74.3 | 69.78 | 93.92% | 0 | 0%
GNA_014652107_Capacity | Bay Area | Diablo | TIDEWATER 2107 | 14652107 | Feeder | None | None | None | 81.81% | 0 | 0% | 26.22 | 21.45 | 81.81% | 0 | 0% | 26.22 | 21.39 | 81.58% | 0 | 0% | 26.22 | 21.34 | 81.39% | 0 | 0% | 26.22 | 21.38 | 81.54% | 0 | 0% | 26.22 | 21.45 | 81.81% | 0 | 0%
GNA_014652108_Capacity | Bay Area | Diablo | TIDEWATER 2108 | 14652108 | Feeder | None | None | None | 81.92% | 0 | 0% | 21.41 | 16.58 | 77.44% | 0 | 0% | 21.41 | 17 | 79.4% | 0 | 0% | 21.41 | 17.54 | 81.92% | 0 | 0% | 21.41 | 17.53 | 81.88% | 0 | 0% | 21.41 | 17.5 | 81.74% | 0 | 0%
GNA_0129601_Capacity | Bay Area | Diablo | CONCORD NO 1 BANK 1 | 129601 | Bank | None | None | None | 96.37% | 0 | 0% | 2.48 | 2.38 | 95.97% | 0 | 0% | 2.48 | 2.37 | 95.56% | 0 | 0% | 2.48 | 2.37 | 95.56% | 0 | 0% | 2.48 | 2.38 | 95.97% | 0 | 0% | 2.48 | 2.39 | 96.37% | 0 | 0%
GNA_012960401_Capacity | Bay Area | Diablo | CONCORD NO 1 0401 | 12960401 | Feeder | None | None | None | 90.34% | 0 | 0% | 2.38 | 2.14 | 89.92% | 0 | 0% | 2.38 | 2.13 | 89.5% | 0 | 0% | 2.38 | 2.13 | 89.5% | 0 | 0% | 2.38 | 2.15 | 90.34% | 0 | 0% | 2.38 | 2.15 | 90.34% | 0 | 0%
GNA_0129602_Capacity | Bay Area | Diablo | CONCORD NO 1 BANK 2 | 129602 | Bank | None | None | None | 58.06% | 0 | 0% | 2.48 | 1.44 | 58.06% | 0 | 0% | 2.48 | 1.43 | 57.66% | 0 | 0% | 2.48 | 1.42 | 57.26% | 0 | 0% | 2.48 | 1.41 | 56.85% | 0 | 0% | 2.48 | 1.41 | 56.85% | 0 | 0%
GNA_012960402_Capacity | Bay Area | Diablo | CONCORD NO 1 0402 | 12960402 | Feeder | None | None | None | 60.08% | 0 | 0% | 2.38 | 1.43 | 60.08% | 0 | 0% | 2.38 | 1.42 | 59.66% | 0 | 0% | 2.38 | 1.41 | 59.24% | 0 | 0% | 2.38 | 1.4 | 58.82% | 0 | 0% | 2.38 | 1.4 | 58.82% | 0 | 0%
GNA_014652109_Capacity | Bay Area | Diablo | TIDEWATER 2109 | 14652109 | Feeder | None | None | None | 88.88% | 0 | 0% | 21.41 | 19.03 | 88.88% | 0 | 0% | 21.41 | 18.89 | 88.23% | 0 | 0% | 21.41 | 18.79 | 87.76% | 0 | 0% | 21.41 | 18.72 | 87.44% | 0 | 0% | 21.41 | 18.73 | 87.48% | 0 | 0%
GNA_014652110_Capacity | Bay Area | Diablo | TIDEWATER 2110 | 14652110 | Feeder | None | None | None | 50.72% | 0 | 0% | 21.41 | 10.75 | 50.21% | 0 | 0% | 21.41 | 10.75 | 50.21% | 0 | 0% | 21.41 | 10.74 | 50.16% | 0 | 0% | 21.41 | 10.79 | 50.4% | 0 | 0% | 21.41 | 10.86 | 50.72% | 0 | 0%
GNA_0136504_Capacity | Bay Area | Diablo | CONTRA COSTA BANK 4 | 136504 | Bank | None | None | None | 84.24% | 0 | 0% | 74.22 | 60.14 | 81.03% | 0 | 0% | 74.22 | 62.52 | 84.24% | 0 | 0% | 74.22 | 62.43 | 84.11% | 0 | 0% | 74.22 | 62.28 | 83.91% | 0 | 0% | 74.22 | 62.2 | 83.8% | 0 | 0%
GNA_013652103_Capacity | Bay Area | Diablo | CONTRA COSTA 2103 | 13652103 | Feeder | Demand Growth | Capacity | 2023 | 134.5% | 7.38 | 34.47% | 21.41 | 26.02 | 121.5% | 4.61 | 21.53% | 21.41 | 28.78 | 134.4% | 7.37 | 34.42% | 21.41 | 28.79 | 134.5% | 7.38 | 34.47% | 21.41 | 28.73 | 134.2% | 7.32 | 34.19% | 21.41 | 28.66 | 133.9% | 7.25 | 33.86%
GNA_013652104_Capacity | Bay Area | Diablo | CONTRA COSTA 2104 | 13652104 | Feeder | None | None | None | 78.08% | 0 | 0% | 18.11 | 14.14 | 78.08% | 0 | 0% | 18.11 | 14.13 | 78.02% | 0 | 0% | 18.11 | 14.11 | 77.91% | 0 | 0% | 18.11 | 14.09 | 77.8% | 0 | 0% | 18.11 | 14.03 | 77.47% | 0 | 0%
GNA_013652105_Capacity | Bay Area | Diablo | CONTRA COSTA 2105 | 13652105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013652108_Capacity | Bay Area | Diablo | CONTRA COSTA 2108 | 13652108 | Feeder | Demand Growth | Capacity | 2023 | 103.3% | 0.61 | 3.274% | 18.63 | 19.24 | 103.3% | 0.61 | 3.274% | 18.63 | 19.15 | 102.8% | 0.52 | 2.791% | 18.63 | 19.06 | 102.3% | 0.43 | 2.308% | 18.63 | 18.96 | 101.8% | 0.33 | 1.771% | 18.63 | 18.96 | 101.8% | 0.33 | 1.771%
GNA_0136510_Capacity | Bay Area | Diablo | CONTRA COSTA BANK 10 | 136510 | Bank | None | None | None | 85.64% | 0 | 0% | 74.3 | 63.62 | 85.63% | 0 | 0% | 74.3 | 63.57 | 85.56% | 0 | 0% | 74.3 | 63.63 | 85.64% | 0 | 0% | 74.3 | 63.56 | 85.55% | 0 | 0% | 74.3 | 63.53 | 85.5% | 0 | 0%
GNA_013652114_Capacity | Bay Area | Diablo | CONTRA COSTA 2114 (Previously CONTRA COSTA 2111) | 13652114 | Feeder | Demand Growth | Capacity | 2023 | 101.6% | 0.29 | 1.557% | 18.63 | 18.88 | 101.3% | 0.25 | 1.342% | 18.63 | 18.89 | 101.4% | 0.26 | 1.396% | 18.63 | 18.92 | 101.6% | 0.29 | 1.557% | 18.63 | 18.89 | 101.4% | 0.26 | 1.396% | 18.63 | 18.87 | 101.3% | 0.24 | 1.288%
GNA_013652115_Capacity | Bay Area | Diablo | CONTRA COSTA 2115 (Previously CONTRA COSTA 2106) | 13652115 | Feeder | None | None | None | 99.61% | 0 | 0% | 18.11 | 18.04 | 99.61% | 0 | 0% | 18.11 | 17.94 | 99.06% | 0 | 0% | 18.11 | 17.86 | 98.62% | 0 | 0% | 18.11 | 17.73 | 97.9% | 0 | 0% | 18.11 | 17.57 | 97.02% | 0 | 0%
GNA_013652116_Capacity | Bay Area | Diablo | CONTRA COSTA 2116 (Previously CONTRA COSTA 2205) | 13652116 | Feeder | Demand Growth | Capacity | 2023 | 130.1% | 6.44 | 30.08% | 21.41 | 27.82 | 129.9% | 6.41 | 29.94% | 21.41 | 27.81 | 129.9% | 6.4 | 29.89% | 21.41 | 27.84 | 130% | 6.43 | 30.03% | 21.41 | 27.83 | 130% | 6.42 | 29.99% | 21.41 | 27.85 | 130.1% | 6.44 | 30.08%
GNA_0144501_Capacity | Bay Area | Diablo | KIRKER BANK 1 | 144501 | Bank | None | None | None | 59.28% | 0 | 0% | 74.29 | 43.66 | 58.77% | 0 | 0% | 74.29 | 44.04 | 59.28% | 0 | 0% | 74.29 | 43.9 | 59.09% | 0 | 0% | 74.29 | 43.78 | 58.93% | 0 | 0% | 74.29 | 43.65 | 58.76% | 0 | 0%
GNA_014452103_Capacity | Bay Area | Diablo | KIRKER 2103 | 14452103 | Feeder | None | None | None | 66.56% | 0 | 0% | 33.07 | 21.42 | 64.77% | 0 | 0% | 33.07 | 21.88 | 66.16% | 0 | 0% | 33.07 | 21.91 | 66.25% | 0 | 0% | 33.07 | 21.95 | 66.37% | 0 | 0% | 33.07 | 22.01 | 66.56% | 0 | 0%
GNA_014452104_Capacity | Bay Area | Diablo | KIRKER 2104 | 14452104 | Feeder | None | None | None | 99.81% | 0 | 0% | 21.41 | 21.37 | 99.81% | 0 | 0% | 21.41 | 21.29 | 99.44% | 0 | 0% | 21.41 | 21.2 | 99.02% | 0 | 0% | 21.41 | 21.13 | 98.69% | 0 | 0% | 21.41 | 21.08 | 98.46% | 0 | 0%
GNA_0144502_Capacity | Bay Area | Diablo | KIRKER BANK 2 | 144502 | Bank | None | None | None | 98.03% | 0 | 0% | 44.6 | 43.07 | 96.57% | 0 | 0% | 44.6 | 43.66 | 97.89% | 0 | 0% | 44.6 | 43.67 | 97.91% | 0 | 0% | 44.6 | 43.61 | 97.78% | 0 | 0% | 44.6 | 43.72 | 98.03% | 0 | 0%
GNA_014452105_Capacity | Bay Area | Diablo | KIRKER 2105 | 14452105 | Feeder | Demand Growth | Capacity | 2023 | 106% | 1.41 | 5.985% | 23.56 | 24.35 | 103.4% | 0.79 | 3.353% | 23.56 | 24.89 | 105.6% | 1.33 | 5.645% | 23.56 | 24.92 | 105.8% | 1.36 | 5.772% | 23.56 | 24.92 | 105.8% | 1.36 | 5.772% | 23.56 | 24.97 | 106% | 1.41 | 5.985%
GNA_014452106_Capacity | Bay Area | Diablo | KIRKER 2106 | 14452106 | Feeder | None | None | None | 77.29% | 0 | 0% | 21.22 | 16.19 | 76.3% | 0 | 0% | 21.22 | 16.26 | 76.63% | 0 | 0% | 21.22 | 16.32 | 76.91% | 0 | 0% | 21.22 | 16.36 | 77.1% | 0 | 0% | 21.22 | 16.4 | 77.29% | 0 | 0%
GNA_0132402_Capacity | Bay Area | Diablo | WHITNEY BANK 2 | 132402 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013240402_Capacity | Bay Area | Diablo | WHITNEY 0402 | 13240402 | Feeder | None | None | None | 43.17% | 0 | 0% | 2.71 | 1.16 | 42.8% | 0 | 0% | 2.71 | 1.16 | 42.8% | 0 | 0% | 2.71 | 1.17 | 43.17% | 0 | 0% | 2.71 | 1.16 | 42.8% | 0 | 0% | 2.71 | 1.16 | 42.8% | 0 | 0%
GNA_0144503_Capacity | Bay Area | Diablo | KIRKER BANK 3 | 144503 | Bank | Demand Growth | Capacity | 2023 | 107.5% | 3.34 | 7.489% | 44.6 | 47.34 | 106.1% | 2.74 | 6.143% | 44.6 | 47.94 | 107.5% | 3.34 | 7.489% | 44.6 | 47.83 | 107.2% | 3.23 | 7.242% | 44.6 | 47.64 | 106.8% | 3.04 | 6.816% | 44.6 | 47.42 | 106.3% | 2.82 | 6.323%
GNA_014452107_Capacity | Bay Area | Diablo | KIRKER 2107 | 14452107 | Feeder | None | None | None | 65.41% | 0 | 0% | 21.22 | 13.67 | 64.42% | 0 | 0% | 21.22 | 13.88 | 65.41% | 0 | 0% | 21.22 | 13.82 | 65.13% | 0 | 0% | 21.22 | 13.74 | 64.75% | 0 | 0% | 21.22 | 13.63 | 64.23% | 0 | 0%
GNA_014452108_Capacity | Bay Area | Diablo | KIRKER 2108 | 14452108 | Feeder | None | None | None | 88.08% | 0 | 0% | 18.63 | 15.97 | 85.72% | 0 | 0% | 18.63 | 16.41 | 88.08% | 0 | 0% | 18.63 | 16.39 | 87.98% | 0 | 0% | 18.63 | 16.34 | 87.71% | 0 | 0% | 18.63 | 16.33 | 87.65% | 0 | 0%
GNA_014452109_Capacity | Bay Area | Diablo | KIRKER 2109 | 14452109 | Feeder | None | None | None | 72.67% | 0 | 0% | 21.22 | 15.42 | 72.67% | 0 | 0% | 21.22 | 15.4 | 72.57% | 0 | 0% | 21.22 | 15.38 | 72.48% | 0 | 0% | 21.22 | 15.37 | 72.43% | 0 | 0% | 21.22 | 15.35 | 72.34% | 0 | 0%
GNA_0121601_Capacity | Bay Area | Diablo | PITTSBURG BANK 1 | 121601 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012160401_Capacity | Bay Area | Diablo | PITTSBURG 0401 | 12160401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012160402_Capacity | Bay Area | Diablo | PITTSBURG 0402 | 12160402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0139103_Capacity | Bay Area | Diablo | WILLOW PASS BANK 3 | 139103 | Bank | Demand Growth | Capacity | 2024 | 111.9% | 3.53 | 11.89% | 29.68 | 27.27 | 91.88% | 0 | 0% | 29.68 | 30.6 | 103.1% | 0.92 | 3.1% | 29.68 | 32.78 | 110.4% | 3.1 | 10.44% | 29.68 | 32.95 | 111% | 3.27 | 11.02% | 29.68 | 33.21 | 111.9% | 3.53 | 11.89%
GNA_013912107_Capacity | Bay Area | Diablo | WILLOW PASS 2107 | 13912107 | Feeder | None | None | None | 87.3% | 0 | 0% | 21.41 | 13.48 | 62.96% | 0 | 0% | 21.41 | 16.36 | 76.41% | 0 | 0% | 21.41 | 18.46 | 86.22% | 0 | 0% | 21.41 | 18.54 | 86.6% | 0 | 0% | 21.41 | 18.69 | 87.3% | 0 | 0%
GNA_013912108_Capacity | Bay Area | Diablo | WILLOW PASS 2108 | 13912108 | Feeder | None | None | None | 80.66% | 0 | 0% | 21.41 | 16.63 | 77.67% | 0 | 0% | 21.41 | 17.05 | 79.64% | 0 | 0% | 21.41 | 17.1 | 79.87% | 0 | 0% | 21.41 | 17.18 | 80.24% | 0 | 0% | 21.41 | 17.27 | 80.66% | 0 | 0%
GNA_0135305_Capacity | Bay Area | Diablo | LAKEWOOD BANK 5 | 135305 | Bank | None | None | None | 70.19% | 0 | 0% | 44.52 | 29.11 | 65.39% | 0 | 0% | 44.52 | 29.07 | 65.3% | 0 | 0% | 44.52 | 30.95 | 69.52% | 0 | 0% | 44.52 | 31.07 | 69.79% | 0 | 0% | 44.52 | 31.25 | 70.19% | 0 | 0%
GNA_013531101_Capacity | Bay Area | Diablo | LAKEWOOD 1101 | 13531101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013531102_Capacity | Bay Area | Diablo | LAKEWOOD 1102 | 13531102 | Feeder | None | None | None | 80.49% | 0 | 0% | 9.02 | 6.5 | 72.06% | 0 | 0% | 9.02 | 6.48 | 71.84% | 0 | 0% | 9.02 | 7.21 | 79.93% | 0 | 0% | 9.02 | 7.24 | 80.27% | 0 | 0% | 9.02 | 7.26 | 80.49% | 0 | 0%
GNA_013531103_Capacity | Bay Area | Diablo | LAKEWOOD 1103 | 13531103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013531104_Capacity | Bay Area | Diablo | LAKEWOOD 1104 | 13531104 | Feeder | None | None | None | 87.73% | 0 | 0% | 10.76 | 8.29 | 77.04% | 0 | 0% | 10.76 | 8.25 | 76.67% | 0 | 0% | 10.76 | 9.04 | 84.01% | 0 | 0% | 10.76 | 9.19 | 85.41% | 0 | 0% | 10.76 | 9.44 | 87.73% | 0 | 0%
GNA_0138005_Capacity | Bay Area | Diablo | MORAGA BANK 5 | 138005 | Bank | None | None | None | 99.73% | 0 | 0% | 40.6 | 38.3 | 94.33% | 0 | 0% | 40.6 | 38.56 | 94.98% | 0 | 0% | 40.6 | 39.36 | 96.95% | 0 | 0% | 40.6 | 39.96 | 98.42% | 0 | 0% | 40.6 | 40.49 | 99.73% | 0 | 0%
GNA_013801101_Capacity | Bay Area | Diablo | MORAGA 1101 | 13801101 | Feeder | None | None | None | 87.18% | 0 | 0% | 9.75 | 7.68 | 78.77% | 0 | 0% | 9.75 | 7.86 | 80.62% | 0 | 0% | 9.75 | 8.05 | 82.56% | 0 | 0% | 9.75 | 8.29 | 85.03% | 0 | 0% | 9.75 | 8.5 | 87.18% | 0 | 0%
GNA_013801102_Capacity | Bay Area | Diablo | MORAGA 1102 | 13801102 | Feeder | None | None | None | 82.84% | 0 | 0% | 8.45 | 6.84 | 80.95% | 0 | 0% | 8.45 | 6.82 | 80.71% | 0 | 0% | 8.45 | 6.85 | 81.07% | 0 | 0% | 8.45 | 6.92 | 81.89% | 0 | 0% | 8.45 | 7 | 82.84% | 0 | 0%
GNA_013801103_Capacity | Bay Area | Diablo | MORAGA 1103 | 13801103 | Feeder | None | None | None | 78.92% | 0 | 0% | 11.67 | 8.95 | 76.69% | 0 | 0% | 11.67 | 8.97 | 76.86% | 0 | 0% | 11.67 | 8.97 | 76.86% | 0 | 0% | 11.67 | 9.09 | 77.89% | 0 | 0% | 11.67 | 9.21 | 78.92% | 0 | 0%
GNA_013801104_Capacity | Bay Area | Diablo | MORAGA 1104 | 13801104 | Feeder | None | None | None | 86.15% | 0 | 0% | 10.18 | 8.6 | 84.48% | 0 | 0% | 10.18 | 8.61 | 84.58% | 0 | 0% | 10.18 | 8.65 | 84.97% | 0 | 0% | 10.18 | 8.71 | 85.56% | 0 | 0% | 10.18 | 8.77 | 86.15% | 0 | 0%
GNA_013801105_Capacity | Bay Area | Diablo | MORAGA 1105 | 13801105 | Feeder | None | None | None | 67.15% | 0 | 0% | 12.36 | 7.57 | 61.25% | 0 | 0% | 12.36 | 7.59 | 61.41% | 0 | 0% | 12.36 | 8.13 | 65.78% | 0 | 0% | 12.36 | 8.22 | 66.5% | 0 | 0% | 12.36 | 8.3 | 67.15% | 0 | 0%
GNA_0141601_Capacity | Bay Area | Diablo | ROSSMOOR BANK 1 | 141601 | Bank | None | None | None | 81.76% | 0 | 0% | 44.2 | 36.14 | 81.76% | 0 | 0% | 44.2 | 35.97 | 81.38% | 0 | 0% | 44.2 | 35.82 | 81.04% | 0 | 0% | 44.2 | 35.78 | 80.95% | 0 | 0% | 44.2 | 35.83 | 81.06% | 0 | 0%
GNA_014161101_Capacity | Bay Area | Diablo | ROSSMOOR 1101 | 14161101 | Feeder | None | None | None | 84.15% | 0 | 0% | 14.13 | 11.89 | 84.15% | 0 | 0% | 14.13 | 11.81 | 83.58% | 0 | 0% | 14.13 | 11.76 | 83.23% | 0 | 0% | 14.13 | 11.77 | 83.3% | 0 | 0% | 14.13 | 11.77 | 83.3% | 0 | 0%
GNA_014161102_Capacity | Bay Area | Diablo | ROSSMOOR 1102 | 14161102 | Feeder | None | None | None | 61.17% | 0 | 0% | 11.33 | 6.93 | 61.17% | 0 | 0% | 11.33 | 6.89 | 60.81% | 0 | 0% | 11.33 | 6.84 | 60.37% | 0 | 0% | 11.33 | 6.81 | 60.11% | 0 | 0% | 11.33 | 6.83 | 60.28% | 0 | 0%
GNA_014161103_Capacity | Bay Area | Diablo | ROSSMOOR 1103 | 14161103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014161104_Capacity | Bay Area | Diablo | ROSSMOOR 1104 | 14161104 | Feeder | None | None | None | 73.35% | 0 | 0% | 15.12 | 11.09 | 73.35% | 0 | 0% | 15.12 | 11.06 | 73.15% | 0 | 0% | 15.12 | 11.01 | 72.82% | 0 | 0% | 15.12 | 11 | 72.75% | 0 | 0% | 15.12 | 11.03 | 72.95% | 0 | 0%
GNA_0141602_Capacity | Bay Area | Diablo | ROSSMOOR BANK 2 | 141602 | Bank | None | None | None | 92.08% | 0 | 0% | 44.2 | 40.7 | 92.08% | 0 | 0% | 44.2 | 40.05 | 90.61% | 0 | 0% | 44.2 | 39.62 | 89.64% | 0 | 0% | 44.2 | 39.53 | 89.43% | 0 | 0% | 44.2 | 39.8 | 90.05% | 0 | 0%
GNA_014161105_Capacity | Bay Area | Diablo | ROSSMOOR 1105 | 14161105 | Feeder | None | None | None | 67.55% | 0 | 0% | 8.66 | 5.85 | 67.55% | 0 | 0% | 8.66 | 5.82 | 67.21% | 0 | 0% | 8.66 | 5.8 | 66.97% | 0 | 0% | 8.66 | 5.79 | 66.86% | 0 | 0% | 8.66 | 5.76 | 66.51% | 0 | 0%
GNA_014161106_Capacity | Bay Area | Diablo | ROSSMOOR 1106 | 14161106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014161107_Capacity | Bay Area | Diablo | ROSSMOOR 1107 | 14161107 | Feeder | None | None | None | 96.76% | 0 | 0% | 9.58 | 9.27 | 96.76% | 0 | 0% | 9.58 | 9.14 | 95.41% | 0 | 0% | 9.58 | 9.06 | 94.57% | 0 | 0% | 9.58 | 9.01 | 94.05% | 0 | 0% | 9.58 | 9.02 | 94.15% | 0 | 0%
GNA_014161108_Capacity | Bay Area | Diablo | ROSSMOOR 1108 | 14161108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014161109_Capacity | Bay Area | Diablo | ROSSMOOR 1109 | 14161109 | Feeder | None | None | None | 37.57% | 0 | 0% | 12.83 | 4.81 | 37.49% | 0 | 0% | 12.83 | 4.78 | 37.26% | 0 | 0% | 12.83 | 4.78 | 37.26% | 0 | 0% | 12.83 | 4.79 | 37.33% | 0 | 0% | 12.83 | 4.82 | 37.57% | 0 | 0%
GNA_0146703_Capacity | Bay Area | Diablo | SOBRANTE BANK 3 | 146703 | Bank | None | None | None | 91.99% | 0 | 0% | 29.7 | 27.32 | 91.99% | 0 | 0% | 29.7 | 26.9 | 90.57% | 0 | 0% | 29.7 | 26.76 | 90.1% | 0 | 0% | 29.7 | 26.91 | 90.61% | 0 | 0% | 29.7 | 27.13 | 91.35% | 0 | 0%
GNA_014671101_Capacity | Bay Area | Diablo | SOBRANTE 1101 | 14671101 | Feeder | None | None | None | 96.47% | 0 | 0% | 10.76 | 10.33 | 96% | 0 | 0% | 10.76 | 10.2 | 94.8% | 0 | 0% | 10.76 | 10.38 | 96.47% | 0 | 0% | 10.76 | 10.34 | 96.1% | 0 | 0% | 10.76 | 10.31 | 95.82% | 0 | 0%
GNA_014671102_Capacity | Bay Area | Diablo | SOBRANTE 1102 | 14671102 | Feeder | None | None | None | 87.64% | 0 | 0% | 11.33 | 9.93 | 87.64% | 0 | 0% | 11.33 | 9.7 | 85.61% | 0 | 0% | 11.33 | 9.51 | 83.94% | 0 | 0% | 11.33 | 9.6 | 84.73% | 0 | 0% | 11.33 | 9.73 | 85.88% | 0 | 0%
GNA_014671103_Capacity | Bay Area | Diablo | SOBRANTE 1103 | 14671103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0135302_Capacity | Bay Area | Diablo | LAKEWOOD BANK 2 | 135302 | Bank | None | None | None | 49.63% | 0 | 0% | 74.23 | 35.54 | 47.88% | 0 | 0% | 74.23 | 36.55 | 49.24% | 0 | 0% | 74.23 | 36.55 | 49.24% | 0 | 0% | 74.23 | 36.68 | 49.41% | 0 | 0% | 74.23 | 36.84 | 49.63% | 0 | 0%
GNA_013532223_Capacity | Bay Area | Diablo | LAKEWOOD 2223 | 13532223 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0135601_Capacity | Bay Area | Diablo | SARANAP BANK 1 | 135601 | Bank | None | None | None | 55.95% | 0 | 0% | 2.27 | 1.24 | 54.63% | 0 | 0% | 2.27 | 1.24 | 54.63% | 0 | 0% | 2.27 | 1.25 | 55.07% | 0 | 0% | 2.27 | 1.26 | 55.51% | 0 | 0% | 2.27 | 1.27 | 55.95% | 0 | 0%
GNA_013560401_Capacity | Bay Area | Diablo | SARANAP 0401 | 13560401 | Feeder | None | None | None | 54.74% | 0 | 0% | 2.32 | 1.24 | 53.45% | 0 | 0% | 2.32 | 1.24 | 53.45% | 0 | 0% | 2.32 | 1.25 | 53.88% | 0 | 0% | 2.32 | 1.26 | 54.31% | 0 | 0% | 2.32 | 1.27 | 54.74% | 0 | 0%
GNA_013532224_Capacity | Bay Area | Diablo | LAKEWOOD 2224 | 13532224 | Feeder | None | None | None | 77.12% | 0 | 0% | 21.11 | 16.2 | 76.74% | 0 | 0% | 21.11 | 16.12 | 76.36% | 0 | 0% | 21.11 | 16.11 | 76.31% | 0 | 0% | 21.11 | 16.21 | 76.79% | 0 | 0% | 21.11 | 16.28 | 77.12% | 0 | 0%
GNA_0135306_Capacity | Bay Area | Diablo | LAKEWOOD BANK 6 | 135306 | Bank | None | None | None | 97.38% | 0 | 0% | 44.6 | 42.97 | 96.35% | 0 | 0% | 44.6 | 42.89 | 96.17% | 0 | 0% | 44.6 | 42.91 | 96.21% | 0 | 0% | 44.6 | 43.1 | 96.64% | 0 | 0% | 44.6 | 43.43 | 97.38% | 0 | 0%
GNA_013532110_Capacity | Bay Area | Diablo | LAKEWOOD 2110 | 13532110 | Feeder | None | None | None | 98.58% | 0 | 0% | 21.11 | 19.72 | 93.42% | 0 | 0% | 21.11 | 19.91 | 94.32% | 0 | 0% | 21.11 | 20.13 | 95.36% | 0 | 0% | 21.11 | 20.42 | 96.73% | 0 | 0% | 21.11 | 20.81 | 98.58% | 0 | 0%
GNA_013532111_Capacity | Bay Area | Diablo | LAKEWOOD 2111 | 13532111 | Feeder | None | None | None | 36.8% | 0 | 0% | 21.22 | 7.81 | 36.8% | 0 | 0% | 21.22 | 7.78 | 36.66% | 0 | 0% | 21.22 | 7.75 | 36.52% | 0 | 0% | 21.22 | 7.72 | 36.38% | 0 | 0% | 21.22 | 7.74 | 36.48% | 0 | 0%
GNA_013532112_Capacity | Bay Area | Diablo | LAKEWOOD 2112 | 13532112 | Feeder | None | None | None | 96.83% | 0 | 0% | 18.63 | 18.04 | 96.83% | 0 | 0% | 18.63 | 17.97 | 96.46% | 0 | 0% | 18.63 | 17.94 | 96.3% | 0 | 0% | 18.63 | 17.98 | 96.51% | 0 | 0% | 18.63 | 17.99 | 96.56% | 0 | 0%
GNA_0146901_Capacity | Bay Area | Diablo | RESEARCH BANK 1 | 146901 | Bank | None | None | None | 79.96% | 0 | 0% | 44.6 | 35.66 | 79.96% | 0 | 0% | 44.6 | 34.84 | 78.12% | 0 | 0% | 44.6 | 34.13 | 76.52% | 0 | 0% | 44.6 | 34.45 | 77.24% | 0 | 0% | 44.6 | 35.02 | 78.52% | 0 | 0%
GNA_014692101_Capacity | Bay Area | Diablo | RESEARCH 2101 | 14692101 | Feeder | None | None | None | 87.16% | 0 | 0% | 21.41 | 18.66 | 87.16% | 0 | 0% | 21.41 | 18.27 | 85.33% | 0 | 0% | 21.41 | 17.97 | 83.93% | 0 | 0% | 21.41 | 18.17 | 84.87% | 0 | 0% | 21.41 | 18.49 | 86.36% | 0 | 0%
GNA_014692102_Capacity | Bay Area | Diablo | RESEARCH 2102 | 14692102 | Feeder | None | None | None | 92.27% | 0 | 0% | 21.22 | 19.58 | 92.27% | 0 | 0% | 21.22 | 19.15 | 90.25% | 0 | 0% | 21.22 | 18.75 | 88.36% | 0 | 0% | 21.22 | 18.74 | 88.31% | 0 | 0% | 21.22 | 19 | 89.54% | 0 | 0%
GNA_0146601_Capacity | Bay Area | Diablo | TASSAJARA BANK 1 | 146601 | Bank | None | None | None | 63.08% | 0 | 0% | 74.3 | 44.11 | 59.37% | 0 | 0% | 74.3 | 44.65 | 60.09% | 0 | 0% | 74.3 | 45.21 | 60.85% | 0 | 0% | 74.3 | 46.01 | 61.92% | 0 | 0% | 74.3 | 46.87 | 63.08% | 0 | 0%
GNA_014662103_Capacity | Bay Area | Diablo | TASSAJARA 2103 | 14662103 | Feeder | None | None | None | 95.1% | 0 | 0% | 21.22 | 19.69 | 92.79% | 0 | 0% | 21.22 | 19.69 | 92.79% | 0 | 0% | 21.22 | 19.76 | 93.12% | 0 | 0% | 21.22 | 19.93 | 93.92% | 0 | 0% | 21.22 | 20.18 | 95.1% | 0 | 0%
GNA_014662104_Capacity | Bay Area | Diablo | TASSAJARA 2104 | 14662104 | Feeder | None | None | None | 69.76% | 0 | 0% | 21.63 | 14.2 | 65.65% | 0 | 0% | 21.63 | 14.37 | 66.44% | 0 | 0% | 21.63 | 14.56 | 67.31% | 0 | 0% | 21.63 | 14.83 | 68.56% | 0 | 0% | 21.63 | 15.09 | 69.76% | 0 | 0%
GNA_014662106_Capacity | Bay Area | Diablo | TASSAJARA 2106 | 14662106 | Feeder | None | None | None | 66.42% | 0 | 0% | 21.41 | 13.41 | 62.63% | 0 | 0% | 21.41 | 13.56 | 63.33% | 0 | 0% | 21.41 | 13.72 | 64.08% | 0 | 0% | 21.41 | 13.96 | 65.2% | 0 | 0% | 21.41 | 14.22 | 66.42% | 0 | 0%
GNA_0146602_Capacity | Bay Area | Diablo | TASSAJARA BANK 2 | 146602 | Bank | None | None | None | 61.43% | 0 | 0% | 74.3 | 43.07 | 57.97% | 0 | 0% | 74.3 | 43.6 | 58.68% | 0 | 0% | 74.3 | 44.15 | 59.42% | 0 | 0% | 74.3 | 44.86 | 60.38% | 0 | 0% | 74.3 | 45.64 | 61.43% | 0 | 0%
GNA_014662107_Capacity | Bay Area | Diablo | TASSAJARA 2107 | 14662107 | Feeder | None | None | None | 82.3% | 0 | 0% | 21.41 | 17.16 | 80.15% | 0 | 0% | 21.41 | 16.85 | 78.7% | 0 | 0% | 21.41 | 17.05 | 79.64% | 0 | 0% | 21.41 | 17.3 | 80.8% | 0 | 0% | 21.41 | 17.62 | 82.3% | 0 | 0%
GNA_014662108_Capacity | Bay Area | Diablo | TASSAJARA 2108 | 14662108 | Feeder | None | None | None | 80.67% | 0 | 0% | 22.19 | 17.9 | 80.67% | 0 | 0% | 22.19 | 17.61 | 79.36% | 0 | 0% | 22.19 | 17.51 | 78.91% | 0 | 0% | 22.19 | 17.68 | 79.68% | 0 | 0% | 22.19 | 17.82 | 80.31% | 0 | 0%
GNA_014662109_Capacity | Bay Area | Diablo | TASSAJARA 2109 | 14662109 | Feeder | None | None | None | 53.39% | 0 | 0% | 21.41 | 10.6 | 49.51% | 0 | 0% | 21.41 | 10.85 | 50.68% | 0 | 0% | 21.41 | 11.04 | 51.56% | 0 | 0% | 21.41 | 11.23 | 52.45% | 0 | 0% | 21.41 | 11.43 | 53.39% | 0 | 0%
GNA_0146603_Capacity | Bay Area | Diablo | TASSAJARA BANK 3 | 146603 | Bank | None | None | None | 55.79% | 0 | 0% | 74.3 | 40.04 | 53.89% | 0 | 0% | 74.3 | 40.27 | 54.2% | 0 | 0% | 74.3 | 40.56 | 54.59% | 0 | 0% | 74.3 | 40.97 | 55.14% | 0 | 0% | 74.3 | 41.45 | 55.79% | 0 | 0%
GNA_014662112_Capacity | Bay Area | Diablo | TASSAJARA 2112 | 14662112 | Feeder | None | None | None | 76.36% | 0 | 0% | 21.11 | 16.06 | 76.08% | 0 | 0% | 21.11 | 15.59 | 73.85% | 0 | 0% | 21.11 | 15.61 | 73.95% | 0 | 0% | 21.11 | 15.87 | 75.18% | 0 | 0% | 21.11 | 16.12 | 76.36% | 0 | 0%
GNA_014662113_Capacity | Bay Area | Diablo | TASSAJARA 2113 | 14662113 | Feeder | None | None | None | 97.9% | 0 | 0% | 21.41 | 20.54 | 95.94% | 0 | 0% | 21.41 | 20.59 | 96.17% | 0 | 0% | 21.41 | 20.67 | 96.54% | 0 | 0% | 21.41 | 20.77 | 97.01% | 0 | 0% | 21.41 | 20.96 | 97.9% | 0 | 0%
GNA_014662114_Capacity | Bay Area | Diablo | TASSAJARA 2114 | 14662114 | Feeder | None | None | None | 10.7% | 0 | 0% | 21.41 | 2.27 | 10.6% | 0 | 0% | 21.41 | 2.27 | 10.6% | 0 | 0% | 21.41 | 2.26 | 10.56% | 0 | 0% | 21.41 | 2.28 | 10.65% | 0 | 0% | 21.41 | 2.29 | 10.7% | 0 | 0%
GNA_0121002_Capacity | Bay Area | East Bay | OAKLAND K BANK 2 | 121002 | Bank | None | None | None | 60.95% | 0 | 0% | 35.26 | 20.05 | 56.86% | 0 | 0% | 35.26 | 21.49 | 60.95% | 0 | 0% | 44.96 | 21.84 | 48.58% | 0 | 0% | 44.96 | 22.48 | 50% | 0 | 0% | 44.96 | 24.15 | 53.71% | 0 | 0%
GNA_012101101_Capacity | Bay Area | East Bay | OAKLAND K 1101 | 12101101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012101102_Capacity | Bay Area | East Bay | OAKLAND K 1102 | 12101102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012101103_Capacity | Bay Area | East Bay | OAKLAND K 1103 | 12101103 | Feeder | None | None | None | 82.88% | 0 | 0% | 7.36 | 5.16 | 70.11% | 0 | 0% | 7.36 | 5.31 | 72.15% | 0 | 0% | 7.36 | 5.48 | 74.46% | 0 | 0% | 7.36 | 5.77 | 78.4% | 0 | 0% | 7.36 | 6.1 | 82.88% | 0 | 0%
GNA_0126901_Capacity | Bay Area | East Bay | FLORENCE BANK 1 | 126901 | Bank | None | None | None | 42.54% | 0 | 0% | 2.28 | 0.86 | 37.72% | 0 | 0% | 2.28 | 0.87 | 38.16% | 0 | 0% | 2.28 | 0.9 | 39.47% | 0 | 0% | 2.28 | 0.93 | 40.79% | 0 | 0% | 2.28 | 0.97 | 42.54% | 0 | 0%
GNA_012690401_Capacity | Bay Area | East Bay | FLORENCE 0401 | 12690401 | Feeder | None | None | None | 35.88% | 0 | 0% | 2.62 | 0.83 | 31.68% | 0 | 0% | 2.62 | 0.84 | 32.06% | 0 | 0% | 2.62 | 0.86 | 32.82% | 0 | 0% | 2.62 | 0.9 | 34.35% | 0 | 0% | 2.62 | 0.94 | 35.88% | 0 | 0%
GNA_012101104_Capacity | Bay Area | East Bay | OAKLAND K 1104 | 12101104 | Feeder | None | None | None | 75% | 0 | 0% | 10.16 | 6.03 | 59.35% | 0 | 0% | 10.16 | 7.2 | 70.87% | 0 | 0% | 10.16 | 7.28 | 71.65% | 0 | 0% | 10.16 | 7.42 | 73.03% | 0 | 0% | 10.16 | 7.62 | 75% | 0 | 0%
GNA_0125402_Capacity | Bay Area | East Bay | OAKLAND X BANK 2 | 125402 | Bank | None | None | None | 57.18% | 0 | 0% | 29.68 | 12.71 | 42.82% | 0 | 0% | 29.68 | 14.57 | 49.09% | 0 | 0% | 29.68 | 14.7 | 49.53% | 0 | 0% | 29.68 | 16.7 | 56.27% | 0 | 0% | 29.68 | 16.97 | 57.18% | 0 | 0%
GNA_012541102_Capacity | Bay Area | East Bay | OAKLAND X 1102 | 12541102 | Feeder | None | None | None | 59.4% | 0 | 0% | 10.69 | 4.9 | 45.84% | 0 | 0% | 10.69 | 6 | 56.13% | 0 | 0% | 10.69 | 6.09 | 56.97% | 0 | 0% | 10.69 | 6.21 | 58.09% | 0 | 0% | 10.69 | 6.35 | 59.4% | 0 | 0%
GNA_0126701_Capacity | Bay Area | East Bay | 8TH AVENUE BANK 1 | 126701 | Bank | None | None | None | 72.22% | 0 | 0% | 1.98 | 1.31 | 66.16% | 0 | 0% | 1.98 | 1.32 | 66.67% | 0 | 0% | 1.98 | 1.34 | 67.68% | 0 | 0% | 1.98 | 1.38 | 69.7% | 0 | 0% | 1.98 | 1.43 | 72.22% | 0 | 0%
GNA_012670401_Capacity | Bay Area | East Bay | 8TH AVENUE 0401 | 12670401 | Feeder | None | None | None | 69.7% | 0 | 0% | 1.98 | 1.26 | 63.64% | 0 | 0% | 1.98 | 1.28 | 64.65% | 0 | 0% | 1.98 | 1.3 | 65.66% | 0 | 0% | 1.98 | 1.33 | 67.17% | 0 | 0% | 1.98 | 1.38 | 69.7% | 0 | 0%
GNA_012541112_Capacity | Bay Area | East Bay | OAKLAND X 1112 | 12541112 | Feeder | None | None | None | 65.44% | 0 | 0% | 8.45 | 5.42 | 64.14% | 0 | 0% | 8.45 | 5.43 | 64.26% | 0 | 0% | 8.45 | 5.44 | 64.38% | 0 | 0% | 8.45 | 5.48 | 64.85% | 0 | 0% | 8.45 | 5.53 | 65.44% | 0 | 0%
GNA_012541114_Capacity | Bay Area | East Bay | OAKLAND X 1114 | 12541114 | Feeder | None | None | None | 58.78% | 0 | 0% | 8.49 | 2.35 | 27.68% | 0 | 0% | 8.49 | 3.19 | 37.57% | 0 | 0% | 8.49 | 3.16 | 37.22% | 0 | 0% | 8.49 | 4.95 | 58.3% | 0 | 0% | 8.49 | 4.99 | 58.78% | 0 | 0%
GNA_0125442_Capacity | Bay Area | East Bay | OAKLAND X UNIT SUB#2 | 125442 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012540402_Capacity | Bay Area | East Bay | OAKLAND X 0402 | 12540402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0125404_Capacity | Bay Area | East Bay | OAKLAND X BANK 4 | 125404 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012541101_Capacity | Bay Area | East Bay | OAKLAND X 1101 | 12541101 | Feeder | None | None | None | 43.73% | 0 | 0% | 12.83 | 5 | 38.97% | 0 | 0% | 12.83 | 5.12 | 39.91% | 0 | 0% | 12.83 | 5.28 | 41.15% | 0 | 0% | 12.83 | 5.41 | 42.17% | 0 | 0% | 12.83 | 5.61 | 43.73% | 0 | 0%
GNA_0133801_Capacity | Bay Area | East Bay | WOOD BANK 1 | 133801 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013380401_Capacity | Bay Area | East Bay | WOOD 0401 | 13380401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012541106_Capacity | Bay Area | East Bay | OAKLAND X 1106 | 12541106 | Feeder | None | None | None | 76.33% | 0 | 0% | 11.87 | 8.07 | 67.99% | 0 | 0% | 11.87 | 8.28 | 69.76% | 0 | 0% | 11.87 | 8.56 | 72.11% | 0 | 0% | 11.87 | 8.82 | 74.3% | 0 | 0% | 11.87 | 9.06 | 76.33% | 0 | 0%
GNA_012541109_Capacity | Bay Area | East Bay | OAKLAND X 1109 | 12541109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012541115_Capacity | Bay Area | East Bay | OAKLAND X 1115 | 12541115 | Feeder | None | None | None | 55.18% | 0 | 0% | 11.87 | 6.11 | 51.47% | 0 | 0% | 11.87 | 6.16 | 51.9% | 0 | 0% | 11.87 | 6.24 | 52.57% | 0 | 0% | 11.87 | 6.4 | 53.92% | 0 | 0% | 11.87 | 6.55 | 55.18% | 0 | 0%
GNA_0125441_Capacity | Bay Area | East Bay | OAKLAND X UNIT SUB#1 | 125441 | Bank | None | None | None | 66.67% | 0 | 0% | 1.98 | 1.17 | 59.09% | 0 | 0% | 1.98 | 1.2 | 60.61% | 0 | 0% | 1.98 | 1.24 | 62.63% | 0 | 0% | 1.98 | 1.27 | 64.14% | 0 | 0% | 1.98 | 1.32 | 66.67% | 0 | 0%
GNA_012540401_Capacity | Bay Area | East Bay | OAKLAND X 0401 | 12540401 | Feeder | None | None | None | 44.91% | 0 | 0% | 2.85 | 1.13 | 39.65% | 0 | 0% | 2.85 | 1.17 | 41.05% | 0 | 0% | 2.85 | 1.21 | 42.46% | 0 | 0% | 2.85 | 1.24 | 43.51% | 0 | 0% | 2.85 | 1.28 | 44.91% | 0 | 0%
GNA_0125405_Capacity | Bay Area | East Bay | OAKLAND X BANK 5 | 125405 | Bank | None | None | None | 87.5% | 0 | 0% | 29.68 | 24.83 | 83.66% | 0 | 0% | 29.68 | 25.17 | 84.8% | 0 | 0% | 29.68 | 25.8 | 86.93% | 0 | 0% | 29.68 | 25.1 | 84.57% | 0 | 0% | 29.68 | 25.97 | 87.5% | 0 | 0%
GNA_012541103_Capacity | Bay Area | East Bay | OAKLAND X 1103 | 12541103 | Feeder | None | None | None | 44.34% | 0 | 0% | 10.69 | 4.67 | 43.69% | 0 | 0% | 10.69 | 4.72 | 44.15% | 0 | 0% | 10.69 | 4.74 | 44.34% | 0 | 0% | 10.69 | 3.09 | 28.91% | 0 | 0% | 10.69 | 3.17 | 29.65% | 0 | 0%
GNA_012541104_Capacity | Bay Area | East Bay | OAKLAND X 1104 | 12541104 | Feeder | None | None | None | 48.25% | 0 | 0% | 12.83 | 5.75 | 44.82% | 0 | 0% | 12.83 | 5.68 | 44.27% | 0 | 0% | 12.83 | 5.82 | 45.36% | 0 | 0% | 12.83 | 6.03 | 47% | 0 | 0% | 12.83 | 6.19 | 48.25% | 0 | 0%
GNA_0131701_Capacity | Bay Area | East Bay | HOLLYWOOD BANK 1 | 131701 | Bank | None | None | None | 93.94% | 0 | 0% | 1.98 | 1.83 | 92.42% | 0 | 0% | 1.98 | 1.84 | 92.93% | 0 | 0% | 1.98 | 1.84 | 92.93% | 0 | 0% | 1.98 | 1.86 | 93.94% | 0 | 0% | 1.98 | 1.84 | 92.93% | 0 | 0%
GNA_013170401_Capacity | Bay Area | East Bay | HOLLYWOOD 0401 | 13170401 | Feeder | None | None | None | 82.11% | 0 | 0% | 2.18 | 1.77 | 81.19% | 0 | 0% | 2.18 | 1.78 | 81.65% | 0 | 0% | 2.18 | 1.78 | 81.65% | 0 | 0% | 2.18 | 1.79 | 82.11% | 0 | 0% | 2.18 | 1.78 | 81.65% | 0 | 0%
GNA_0131805_Capacity | Bay Area | East Bay | PALO SECO BANK 5 | 131805 | Bank | None | None | None | 64.78% | 0 | 0% | 2.47 | 1.43 | 57.89% | 0 | 0% | 2.47 | 1.47 | 59.51% | 0 | 0% | 2.47 | 1.52 | 61.54% | 0 | 0% | 2.47 | 1.57 | 63.56% | 0 | 0% | 2.47 | 1.6 | 64.78% | 0 | 0%
GNA_013180401_Capacity | Bay Area | East Bay | PALO SECO 0401 | 13180401 | Feeder | None | None | None | 60% | 0 | 0% | 2.6 | 1.38 | 53.08% | 0 | 0% | 2.6 | 1.42 | 54.62% | 0 | 0% | 2.6 | 1.47 | 56.54% | 0 | 0% | 2.6 | 1.53 | 58.85% | 0 | 0% | 2.6 | 1.56 | 60% | 0 | 0%
GNA_012541105_Capacity | Bay Area | East Bay | OAKLAND X 1105 | 12541105 | Feeder | None | None | None | 99.78% | 0 | 0% | 9.11 | 7.83 | 85.95% | 0 | 0% | 9.11 | 8.16 | 89.57% | 0 | 0% | 9.11 | 8.42 | 92.43% | 0 | 0% | 9.11 | 8.76 | 96.16% | 0 | 0% | 9.11 | 9.09 | 99.78% | 0 | 0%
GNA_0135201_Capacity | Bay Area | East Bay | MAPLE BANK 1 | 135201 | Bank | None | None | None | 46.15% | 0 | 0% | 2.47 | 1.02 | 41.3% | 0 | 0% | 2.47 | 1.04 | 42.11% | 0 | 0% | 2.47 | 1.05 | 42.51% | 0 | 0% | 2.47 | 1.09 | 44.13% | 0 | 0% | 2.47 | 1.14 | 46.15% | 0 | 0%
GNA_013520401_Capacity | Bay Area | East Bay | MAPLE 0401 | 13520401 | Feeder | None | None | None | 41.98% | 0 | 0% | 2.62 | 0.99 | 37.79% | 0 | 0% | 2.62 | 1 | 38.17% | 0 | 0% | 2.62 | 1.02 | 38.93% | 0 | 0% | 2.62 | 1.05 | 40.08% | 0 | 0% | 2.62 | 1.1 | 41.98% | 0 | 0%
GNA_012541107_Capacity | Bay Area | East Bay | OAKLAND X 1107 | 12541107 | Feeder | None | None | None | 46% | 0 | 0% | 11.87 | 4.78 | 40.27% | 0 | 0% | 11.87 | 4.85 | 40.86% | 0 | 0% | 11.87 | 4.96 | 41.79% | 0 | 0% | 11.87 | 5.23 | 44.06% | 0 | 0% | 11.87 | 5.46 | 46% | 0 | 0%
GNA_012011108_Capacity | Bay Area | East Bay | OAKLAND C 1108 | 12011108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011109_Capacity | Bay Area | East Bay | OAKLAND C 1109 | 12011109 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011110_Capacity | Bay Area | East Bay | OAKLAND C 1110 | 12011110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011112_Capacity | Bay Area | East Bay | OAKLAND C 1112 | 12011112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011113_Capacity | Bay Area | East Bay | OAKLAND C 1113 | 12011113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011114_Capacity | Bay Area | East Bay | OAKLAND C 1114 | 12011114 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011115_Capacity | Bay Area | East Bay | OAKLAND C 1115 | 12011115 | Feeder | None | None | None | 71.33% | 0 | 0% | 7.29 | 5.2 | 71.33% | 0 | 0% | 7.29 | 5.17 | 70.92% | 0 | 0% | 7.29 | 5.13 | 70.37% | 0 | 0% | 7.29 | 5.1 | 69.96% | 0 | 0% | 7.29 | 5.12 | 70.23% | 0 | 0%
GNA_012011116_Capacity | Bay Area | East Bay | OAKLAND C 1116 | 12011116 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011117_Capacity | Bay Area | East Bay | OAKLAND C 1117 | 12011117 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011118_Capacity | Bay Area | East Bay | OAKLAND C 1118 | 12011118 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011119_Capacity | Bay Area | East Bay | OAKLAND C 1119 | 12011119 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011120_Capacity | Bay Area | East Bay | OAKLAND C 1120 | 12011120 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011121_Capacity | Bay Area | East Bay | OAKLAND C 1121 | 12011121 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011132_Capacity | Bay Area | East Bay | OAKLAND C 1132 | 12011132 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012011133_Capacity | Bay Area | East Bay | OAKLAND C 1133 | 12011133 | Feeder | None | None | None | 69.75% | 0 | 0% | 9.52 | 6.29 | 66.07% | 0 | 0% | 9.52 | 6.37 | 66.91% | 0 | 0% | 9.52 | 6.46 | 67.86% | 0 | 0% | 9.52 | 6.55 | 68.8% | 0 | 0% | 9.52 | 6.64 | 69.75% | 0 | 0%
GNA_012011134_Capacity | Bay Area | East Bay | OAKLAND C 1134 | 12011134 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012111101_Capacity | Bay Area | East Bay | OAKLAND L 1101 | 12111101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012111102_Capacity | Bay Area | East Bay | OAKLAND L 1102 | 12111102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012111103_Capacity | Bay Area | East Bay | OAKLAND L 1103 | 12111103 | Feeder | None | None | None | 82.39% | 0 | 0% | 12.83 | 10.55 | 82.23% | 0 | 0% | 12.83 | 10.54 | 82.15% | 0 | 0% | 12.83 | 10.52 | 82% | 0 | 0% | 12.83 | 10.53 | 82.07% | 0 | 0% | 12.83 | 10.57 | 82.39% | 0 | 0%
GNA_012111104_Capacity | Bay Area | East Bay | OAKLAND L 1104 | 12111104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012111105_Capacity | Bay Area | East Bay | OAKLAND L 1105 | 12111105 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012111106_Capacity | Bay Area | East Bay | OAKLAND L 1106 | 12111106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012111107_Capacity | Bay Area | East Bay | OAKLAND L 1107 | 12111107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012111108_Capacity | Bay Area | East Bay | OAKLAND L 1108 | 12111108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0120403_Capacity | Bay Area | East Bay | OAKLAND D BANK 3 | 120403 | Bank | None | None | None | 47.91% | 0 | 0% | 29.68 | 13 | 43.8% | 0 | 0% | 29.68 | 13.55 | 45.65% | 0 | 0% | 29.68 | 13.7 | 46.16% | 0 | 0% | 29.68 | 13.92 | 46.9% | 0 | 0% | 29.68 | 14.22 | 47.91% | 0 | 0%
GNA_0120402_Capacity | Bay Area | East Bay | OAKLAND D BANK 2 | 120402 | Bank | None | None | None | 0% | 0 | 0% | 4.95 | 0 | 0% | 0 | 0% | 4.95 | 0 | 0% | 0 | 0% | 4.95 | 0 | 0% | 0 | 0% | 4.95 | 0 | 0% | 0 | 0% | 4.95 | 0 | 0% | 0 | 0%
GNA_012041103_Capacity | Bay Area | East Bay | OAKLAND D 1103 | 12041103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012041117_Capacity | Bay Area | East Bay | OAKLAND D 1117 | 12041117 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0138402_Capacity | Bay Area | East Bay | STUART BANK 2 | 138402 | Bank | None | None | None | 43.3% | 0 | 0% | 6.19 | 2.03 | 32.79% | 0 | 0% | 6.19 | 2.48 | 40.06% | 0 | 0% | 6.19 | 2.52 | 40.71% | 0 | 0% | 6.19 | 2.59 | 41.84% | 0 | 0% | 6.19 | 2.68 | 43.3% | 0 | 0%
GNA_013840404_Capacity | Bay Area | East Bay | STUART 0404 | 13840404 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013840405_Capacity | Bay Area | East Bay | STUART 0405 | 13840405 | Feeder | None | None | None | 28.03% | 0 | 0% | 3.14 | 0.78 | 24.84% | 0 | 0% | 3.14 | 0.8 | 25.48% | 0 | 0% | 3.14 | 0.81 | 25.8% | 0 | 0% | 3.14 | 0.85 | 27.07% | 0 | 0% | 3.14 | 0.88 | 28.03% | 0 | 0%
GNA_013840406_Capacity | Bay Area | East Bay | STUART 0406 | 13840406 | Feeder | None | None | None | 35.03% | 0 | 0% | 3.14 | 1 | 31.85% | 0 | 0% | 3.14 | 1.01 | 32.17% | 0 | 0% | 3.14 | 1.03 | 32.8% | 0 | 0% | 3.14 | 1.06 | 33.76% | 0 | 0% | 3.14 | 1.1 | 35.03% | 0 | 0%
GNA_0133101_Capacity | Bay Area | East Bay | RUSSELL BANK 1 | 133101 | Bank | None | None | None | 64.39% | 0 | 0% | 3.96 | 2.32 | 58.59% | 0 | 0% | 3.96 | 2.35 | 59.34% | 0 | 0% | 3.96 | 2.4 | 60.61% | 0 | 0% | 3.96 | 2.46 | 62.12% | 0 | 0% | 3.96 | 2.55 | 64.39% | 0 | 0%
GNA_013310401_Capacity | Bay Area | East Bay | RUSSELL 0401 | 13310401 | Feeder | None | None | None | 50.64% | 0 | 0% | 3.14 | 1.49 | 47.45% | 0 | 0% | 3.14 | 1.5 | 47.77% | 0 | 0% | 3.14 | 1.52 | 48.41% | 0 | 0% | 3.14 | 1.55 | 49.36% | 0 | 0% | 3.14 | 1.59 | 50.64% | 0 | 0%
GNA_013310402_Capacity | Bay Area | East Bay | RUSSELL 0402 | 13310402 | Feeder | None | None | None | 28.66% | 0 | 0% | 3.07 | 0.76 | 24.76% | 0 | 0% | 3.07 | 0.78 | 25.41% | 0 | 0% | 3.07 | 0.81 | 26.38% | 0 | 0% | 3.07 | 0.84 | 27.36% | 0 | 0% | 3.07 | 0.88 | 28.66% | 0 | 0%
GNA_0138401_Capacity | Bay Area | East Bay | STUART BANK 1 | 138401 | Bank | None | None | None | 45.56% | 0 | 0% | 6.19 | 2.48 | 40.06% | 0 | 0% | 6.19 | 2.55 | 41.2% | 0 | 0% | 6.19 | 2.62 | 42.33% | 0 | 0% | 6.19 | 2.7 | 43.62% | 0 | 0% | 6.19 | 2.82 | 45.56% | 0 | 0%
GNA_013840401_Capacity | Bay Area | East Bay | STUART 0401 | 13840401 | Feeder | None | None | None | 22.19% | 0 | 0% | 3.92 | 0.78 | 19.9% | 0 | 0% | 3.92 | 0.8 | 20.41% | 0 | 0% | 3.92 | 0.81 | 20.66% | 0 | 0% | 3.92 | 0.84 | 21.43% | 0 | 0% | 3.92 | 0.87 | 22.19% | 0 | 0%
GNA_013840402_Capacity | Bay Area | East Bay | STUART 0402 | 13840402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013840403_Capacity | Bay Area | East Bay | STUART 0403 | 13840403 | Feeder | None | None | None | 23.42% | 0 | 0% | 3.8 | 0.81 | 21.32% | 0 | 0% | 3.8 | 0.82 | 21.58% | 0 | 0% | 3.8 | 0.84 | 22.11% | 0 | 0% | 3.8 | 0.86 | 22.63% | 0 | 0% | 3.8 | 0.89 | 23.42% | 0 | 0%
GNA_0120404_Capacity | Bay Area | East Bay | OAKLAND D BANK 4 | 120404 | Bank | None | None | None | 96.07% | 0 | 0% | 44.54 | 36.29 | 81.48% | 0 | 0% | 44.54 | 42.29 | 94.95% | 0 | 0% | 44.54 | 42.46 | 95.33% | 0 | 0% | 44.54 | 42.79 | 96.07% | 0 | 0% | 44.54 | 42.5 | 95.42% | 0 | 0%
GNA_012041104_Capacity | Bay Area | East Bay | OAKLAND D 1104 | 12041104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012041105_Capacity | Bay Area | East Bay | OAKLAND D 1105 | 12041105 | Feeder | None | None | None | 93.11% | 0 | 0% | 8.42 | 7.84 | 93.11% | 0 | 0% | 8.42 | 7.63 | 90.62% | 0 | 0% | 8.42 | 7.69 | 91.33% | 0 | 0% | 8.42 | 7.78 | 92.4% | 0 | 0% | 8.42 | 7.21 | 85.63% | 0 | 0%
GNA_012041106_Capacity | Bay Area | East Bay | OAKLAND D 1106 | 12041106 | Feeder | Demand Growth | Capacity | 2024 | 163.7% | 4.73 | 63.75% | 7.42 | 5.88 | 79.25% | 0 | 0% | 7.42 | 12.12 | 163.3% | 4.7 | 63.34% | 7.42 | 12.12 | 163.3% | 4.7 | 63.34% | 7.42 | 12.14 | 163.6% | 4.72 | 63.61% | 7.42 | 12.15 | 163.7% | 4.73 | 63.75%
GNA_012041107_Capacity | Bay Area | East Bay | OAKLAND D 1107 | 12041107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012041110_Capacity | Bay Area | East Bay | OAKLAND D 1110 | 12041110 | Feeder | None | None | None | 68.65% | 0 | 0% | 9.92 | 6.15 | 62% | 0 | 0% | 9.92 | 6.31 | 63.61% | 0 | 0% | 9.92 | 6.46 | 65.12% | 0 | 0% | 9.92 | 6.64 | 66.94% | 0 | 0% | 9.92 | 6.81 | 68.65% | 0 | 0%
GNA_012041115_Capacity | Bay Area | East Bay | OAKLAND D 1115 | 12041115 | Feeder | None | None | None | 96.37% | 0 | 0% | 10.18 | 9.52 | 93.52% | 0 | 0% | 10.18 | 9.57 | 94.01% | 0 | 0% | 10.18 | 9.62 | 94.5% | 0 | 0% | 10.18 | 9.7 | 95.28% | 0 | 0% | 10.18 | 9.81 | 96.37% | 0 | 0%
GNA_0120444_Capacity | Bay Area | East Bay | OAKLAND D BANK 44 | 120444 | Bank | None | None | None | 30% | 0 | 0% | 9.9 | 2.61 | 26.36% | 0 | 0% | 9.9 | 2.69 | 27.17% | 0 | 0% | 9.9 | 2.77 | 27.98% | 0 | 0% | 9.9 | 2.87 | 28.99% | 0 | 0% | 9.9 | 2.97 | 30% | 0 | 0%
GNA_012040406_Capacity | Bay Area | East Bay | OAKLAND D 0406 | 12040406 | Feeder | None | None | None | 30.43% | 0 | 0% | 2.07 | 0.53 | 25.6% | 0 | 0% | 2.07 | 0.55 | 26.57% | 0 | 0% | 2.07 | 0.57 | 27.54% | 0 | 0% | 2.07 | 0.6 | 28.99% | 0 | 0% | 2.07 | 0.63 | 30.43% | 0 | 0%
GNA_012040407_Capacity | Bay Area | East Bay | OAKLAND D 0407 | 12040407 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012040408_Capacity | Bay Area | East Bay | OAKLAND D 0408 | 12040408 | Feeder | None | None | None | 33% | 0 | 0% | 2.03 | 0.5 | 24.63% | 0 | 0% | 2.03 | 0.54 | 26.6% | 0 | 0% | 2.03 | 0.57 | 28.08% | 0 | 0% | 2.03 | 0.62 | 30.54% | 0 | 0% | 2.03 | 0.67 | 33% | 0 | 0%
GNA_012040410_Capacity | Bay Area | East Bay | OAKLAND D 0410 | 12040410 | Feeder | None | None | None | 37.93% | 0 | 0% | 2.03 | 0.71 | 34.98% | 0 | 0% | 2.03 | 0.73 | 35.96% | 0 | 0% | 2.03 | 0.73 | 35.96% | 0 | 0% | 2.03 | 0.75 | 36.95% | 0 | 0% | 2.03 | 0.77 | 37.93% | 0 | 0%
GNA_0120405_Capacity | Bay Area | East Bay | OAKLAND D BANK 5 | 120405 | Bank | None | None | None | 91.06% | 0 | 0% | 44.54 | 40.5 | 90.93% | 0 | 0% | 44.54 | 40.56 | 91.06% | 0 | 0% | 44.54 | 40.45 | 90.82% | 0 | 0% | 44.54 | 40.51 | 90.95% | 0 | 0% | 44.54 | 39.72 | 89.18% | 0 | 0%
GNA_012041101_Capacity | Bay Area | East Bay | OAKLAND D 1101 | 12041101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012041102_Capacity | Bay Area | East Bay | OAKLAND D 1102 | 12041102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012041111_Capacity | Bay Area | East Bay | OAKLAND D 1111 | 12041111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012041112_Capacity | Bay Area | East Bay | OAKLAND D 1112 | 12041112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012041116_Capacity | Bay Area | East Bay | OAKLAND D 1116 | 12041116 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0120406_Capacity | Bay Area | East Bay | OAKLAND D BANK 6 | 120406 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012041130_Capacity | Bay Area | East Bay | OAKLAND D 1130 (previously 1109) | 12041130 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012041131_Capacity | Bay Area | East Bay | OAKLAND D 1131 (previously 1113) | 12041131 | Feeder | None | None | None | 56.78% | 0 | 0% | 11.57 | 6.22 | 53.76% | 0 | 0% | 11.57 | 6.29 | 54.36% | 0 | 0% | 11.57 | 6.34 | 54.8% | 0 | 0% | 11.57 | 6.44 | 55.66% | 0 | 0% | 11.57 | 6.57 | 56.78% | 0 | 0%
GNA_012041132_Capacity | Bay Area | East Bay | OAKLAND D 1132 (previously 1114) | 12041132 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012041133_Capacity | Bay Area | East Bay | OAKLAND D 1133 | 12041133 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012041134_Capacity | Bay Area | East Bay | OAKLAND D 1134 | 12041134 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0136802_Capacity | Bay Area | East Bay | EDES BANK 2 | 136802 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013681101_Capacity | Bay Area | East Bay | EDES 1101 | 13681101 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013681103_Capacity | Bay Area | East Bay | EDES 1103 | 13681103 | Feeder | None | None | None | 88.45% | 0 | 0% | 10.22 | 8.74 | 85.52% | 0 | 0% | 10.22 | 8.74 | 85.52% | 0 | 0% | 10.22 | 8.77 | 85.81% | 0 | 0% | 10.22 | 8.89 | 86.99% | 0 | 0% | 10.22 | 9.04 | 88.45% | 0 | 0%
GNA_0130302_Capacity | Bay Area | East Bay | BANCROFT BANK 2 | 130302 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013030402_Capacity | Bay Area | East Bay | BANCROFT 0402 | 13030402 | Feeder | None | None | None | 57.3% | 0 | 0% | 2.81 | 1.46 | 51.96% | 0 | 0% | 2.81 | 1.47 | 52.31% | 0 | 0% | 2.81 | 1.49 | 53.02% | 0 | 0% | 2.81 | 1.54 | 54.8% | 0 | 0% | 2.81 | 1.61 | 57.3% | 0 | 0%
GNA_013681105_Capacity | Bay Area | East Bay | EDES 1105 | 13681105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0136803_Capacity | Bay Area | East Bay | EDES BANK 3 | 136803 | Bank | Demand Growth | Capacity | 2023 | 120% | 8 | 20.02% | 39.97 | 44.91 | 112.4% | 4.94 | 12.36% | 39.97 | 47.97 | 120% | 8 | 20.02% | 39.97 | 47.62 | 119.1% | 7.65 | 19.14% | 39.97 | 47.48 | 118.8% | 7.51 | 18.79% | 39.97 | 47.46 | 118.7% | 7.49 | 18.74%
GNA_013681110_Capacity | Bay Area | East Bay | EDES 1110 | 13681110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013681111_Capacity | Bay Area | East Bay | EDES 1111 | 13681111 | Feeder | Demand Growth | Capacity | 2023 | 124.6% | 2.53 | 24.61% | 10.28 | 11.18 | 108.8% | 0.9 | 8.755% | 10.28 | 12.78 | 124.3% | 2.5 | 24.32% | 10.28 | 12.76 | 124.1% | 2.48 | 24.12% | 10.28 | 12.8 | 124.5% | 2.52 | 24.51% | 10.28 | 12.81 | 124.6% | 2.53 | 24.61%
GNA_013681112_Capacity | Bay Area | East Bay | EDES 1112 | 13681112 | Feeder | Demand Growth | Capacity | 2027 | 102% | 0.21 | 2.043% | 10.28 | 8.91 | 86.67% | 0 | 0% | 10.28 | 9.88 | 96.11% | 0 | 0% | 10.28 | 10.01 | 97.37% | 0 | 0% | 10.28 | 10.26 | 99.81% | 0 | 0% | 10.28 | 10.49 | 102% | 0.21 | 2.043%
GNA_013681113_Capacity | Bay Area | East Bay | EDES 1113 | 13681113 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013681114_Capacity | Bay Area | East Bay | EDES 1114 | 13681114 | Feeder | None | None | None | 81.76% | 0 | 0% | 12.83 | 9.81 | 76.46% | 0 | 0% | 12.83 | 10.49 | 81.76% | 0 | 0% | 12.83 | 10.44 | 81.37% | 0 | 0% | 12.83 | 10.41 | 81.14% | 0 | 0% | 12.83 | 10.41 | 81.14% | 0 | 0%
GNA_0120901_Capacity | Bay Area | East Bay | OAKLAND J BANK 1 | 120901 | Bank | Demand Growth | Capacity | 2024 | 119.8% | 7.93 | 19.78% | 40.1 | 39.35 | 98.13% | 0 | 0% | 40.1 | 47.29 | 117.9% | 7.19 | 17.93% | 40.1 | 47.1 | 117.5% | 7 | 17.46% | 40.1 | 47.29 | 117.9% | 7.19 | 17.93% | 40.1 | 48.03 | 119.8% | 7.93 | 19.78%
GNA_012091101_Capacity | Bay Area | East Bay | OAKLAND J 1101 | 12091101 | Feeder | None | None | None | 79.08% | 0 | 0% | 9.13 | 6.6 | 72.29% | 0 | 0% | 9.13 | 6.73 | 73.71% | 0 | 0% | 9.13 | 6.86 | 75.14% | 0 | 0% | 9.13 | 7.03 | 77% | 0 | 0% | 9.13 | 7.22 | 79.08% | 0 | 0%
GNA_012091103_Capacity | Bay Area | East Bay | OAKLAND J 1103 | 12091103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012091104_Capacity | Bay Area | East Bay | OAKLAND J 1104 | 12091104 | Feeder | Demand Growth | Capacity | 2023 | 136% | 3.6 | 36.04% | 9.99 | 13.59 | 136% | 3.6 | 36.04% | 9.99 | 13.54 | 135.5% | 3.55 | 35.54% | 9.99 | 13.53 | 135.4% | 3.54 | 35.44% | 9.99 | 13.48 | 134.9% | 3.49 | 34.93% | 9.99 | 13.49 | 135% | 3.5 | 35.04%
GNA_012091105_Capacity | Bay Area | East Bay | OAKLAND J 1105 | 12091105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012091109_Capacity | Bay Area | East Bay | OAKLAND J 1109 | 12091109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012091112_Capacity | Bay Area | East Bay | OAKLAND J 1112 | 12091112 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0120902_Capacity | Bay Area | East Bay | OAKLAND J BANK 2 | 120902 | Bank | None | None | None | 96.74% | 0 | 0% | 44.54 | 39.01 | 87.58% | 0 | 0% | 44.54 | 41.31 | 92.75% | 0 | 0% | 44.54 | 41.66 | 93.53% | 0 | 0% | 44.54 | 42.3 | 94.97% | 0 | 0% | 44.54 | 43.09 | 96.74% | 0 | 0%
GNA_0120801_Capacity | Bay Area | East Bay | OAKLAND I BANK 1 | 120801 | Bank | None | None | None | 50.51% | 0 | 0% | 1.98 | 0.97 | 48.99% | 0 | 0% | 1.98 | 0.97 | 48.99% | 0 | 0% | 1.98 | 0.97 | 48.99% | 0 | 0% | 1.98 | 0.99 | 50% | 0 | 0% | 1.98 | 1 | 50.51% | 0 | 0%
GNA_012080401_Capacity | Bay Area | East Bay | OAKLAND I 0401 | 12080401 | Feeder | None | None | None | 43.58% | 0 | 0% | 2.18 | 0.92 | 42.2% | 0 | 0% | 2.18 | 0.92 | 42.2% | 0 | 0% | 2.18 | 0.93 | 42.66% | 0 | 0% | 2.18 | 0.94 | 43.12% | 0 | 0% | 2.18 | 0.95 | 43.58% | 0 | 0%
GNA_0120802_Capacity | Bay Area | East Bay | OAKLAND I BANK 2 | 120802 | Bank | Demand Growth | Capacity | 2023 | 109.6% | 0.19 | 9.596% | 1.98 | 2.12 | 107.1% | 0.14 | 7.071% | 1.98 | 2.12 | 107.1% | 0.14 | 7.071% | 1.98 | 2.12 | 107.1% | 0.14 | 7.071% | 1.98 | 2.14 | 108.1% | 0.16 | 8.081% | 1.98 | 2.17 | 109.6% | 0.19 | 9.596%
GNA_012080402_Capacity | Bay Area | East Bay | OAKLAND I 0402 | 12080402 | Feeder | None | None | None | 94.95% | 0 | 0% | 2.18 | 2.02 | 92.66% | 0 | 0% | 2.18 | 2.02 | 92.66% | 0 | 0% | 2.18 | 2.02 | 92.66% | 0 | 0% | 2.18 | 2.05 | 94.04% | 0 | 0% | 2.18 | 2.07 | 94.95% | 0 | 0%
GNA_012091102_Capacity | Bay Area | East Bay | OAKLAND J 1102 | 12091102 | Feeder | Demand Growth | Capacity | 2027 | 101.5% | 0.15 | 1.512% | 9.92 | 9.14 | 92.14% | 0 | 0% | 9.92 | 9.31 | 93.85% | 0 | 0% | 9.92 | 9.5 | 95.77% | 0 | 0% | 9.92 | 9.76 | 98.39% | 0 | 0% | 9.92 | 10.07 | 101.5% | 0.15 | 1.512%
GNA_012091116_Capacity | Bay Area | East Bay | OAKLAND J 1116 | 12091116 | Feeder | Demand Growth | Capacity | 2023 | 113.8% | 1.4 | 13.78% | 10.16 | 11.08 | 109.1% | 0.92 | 9.055% | 10.16 | 11.15 | 109.7% | 0.99 | 9.744% | 10.16 | 11.22 | 110.4% | 1.06 | 10.43% | 10.16 | 11.36 | 111.8% | 1.2 | 11.81% | 10.16 | 11.56 | 113.8% | 1.4 | 13.78%
GNA_012091117_Capacity | Bay Area | East Bay | OAKLAND J 1117 | 12091117 | Feeder | Demand Growth | Capacity | 2023 | 151.5% | 5.61 | 51.47% | 10.9 | 14.19 | 130.2% | 3.29 | 30.18% | 10.9 | 16.22 | 148.8% | 5.32 | 48.81% | 10.9 | 16.27 | 149.3% | 5.37 | 49.27% | 10.9 | 16.37 | 150.2% | 5.47 | 50.18% | 10.9 | 16.51 | 151.5% | 5.61 | 51.47%
GNA_0126401_Capacity | Bay Area | East Bay | BECK STREET BANK 1 | 126401 | Bank | None | None | None | 20.56% | 0 | 0% | 2.48 | 0.49 | 19.76% | 0 | 0% | 2.48 | 0.49 | 19.76% | 0 | 0% | 2.48 | 0.49 | 19.76% | 0 | 0% | 2.48 | 0.5 | 20.16% | 0 | 0% | 2.48 | 0.51 | 20.56% | 0 | 0%
GNA_012640401_Capacity | Bay Area | East Bay | BECK STREET 0401 | 12640401 | Feeder | None | None | None | 18.01% | 0 | 0% | 2.72 | 0.46 | 16.91% | 0 | 0% | 2.72 | 0.46 | 16.91% | 0 | 0% | 2.72 | 0.46 | 16.91% | 0 | 0% | 2.72 | 0.48 | 17.65% | 0 | 0% | 2.72 | 0.49 | 18.01% | 0 | 0%
GNA_0120903_Capacity | Bay Area | East Bay | OAKLAND J BANK 3 | 120903 | Bank | None | None | None | 46.39% | 0 | 0% | 6.92 | 3.05 | 44.08% | 0 | 0% | 6.92 | 3.07 | 44.36% | 0 | 0% | 6.92 | 3.09 | 44.65% | 0 | 0% | 6.92 | 3.14 | 45.38% | 0 | 0% | 6.92 | 3.21 | 46.39% | 0 | 0%
GNA_012090403_Capacity | Bay Area | East Bay | OAKLAND J 0403 | 12090403 | Feeder | None | None | None | 62.98% | 0 | 0% | 2.35 | 1.38 | 58.72% | 0 | 0% | 2.35 | 1.39 | 59.15% | 0 | 0% | 2.35 | 1.4 | 59.57% | 0 | 0% | 2.35 | 1.43 | 60.85% | 0 | 0% | 2.35 | 1.48 | 62.98% | 0 | 0%
GNA_012090409_Capacity | Bay Area | East Bay | OAKLAND J 0409 | 12090409 | Feeder | None | None | None | 49.18% | 0 | 0% | 1.83 | 0.83 | 45.36% | 0 | 0% | 1.83 | 0.84 | 45.9% | 0 | 0% | 1.83 | 0.85 | 46.45% | 0 | 0% | 1.83 | 0.87 | 47.54% | 0 | 0% | 1.83 | 0.9 | 49.18% | 0 | 0%
GNA_0120904_Capacity | Bay Area | East Bay | OAKLAND J BANK 4 | 120904 | Bank | None | None | None | 36.42% | 0 | 0% | 6.92 | 2.37 | 34.25% | 0 | 0% | 6.92 | 2.38 | 34.39% | 0 | 0% | 6.92 | 2.4 | 34.68% | 0 | 0% | 6.92 | 2.45 | 35.4% | 0 | 0% | 6.92 | 2.52 | 36.42% | 0 | 0%
GNA_012090401_Capacity | Bay Area | East Bay | OAKLAND J 0401 | 12090401 | Feeder | None | None | None | 57.45% | 0 | 0% | 2.35 | 1.27 | 54.04% | 0 | 0% | 2.35 | 1.28 | 54.47% | 0 | 0% | 2.35 | 1.29 | 54.89% | 0 | 0% | 2.35 | 1.32 | 56.17% | 0 | 0% | 2.35 | 1.35 | 57.45% | 0 | 0%
GNA_012090408_Capacity | Bay Area | East Bay | OAKLAND J 0408 | 12090408 | Feeder | None | None | None | 47.66% | 0 | 0% | 2.35 | 1.05 | 44.68% | 0 | 0% | 2.35 | 1.05 | 44.68% | 0 | 0% | 2.35 | 1.06 | 45.11% | 0 | 0% | 2.35 | 1.08 | 45.96% | 0 | 0% | 2.35 | 1.12 | 47.66% | 0 | 0%
GNA_0120905_Capacity | Bay Area | East Bay | OAKLAND J BANK 5 | 120905 | Bank | None | None | None | 99.8% | 0 | 0% | 44.54 | 41.04 | 92.14% | 0 | 0% | 44.54 | 43.36 | 97.35% | 0 | 0% | 44.54 | 43.6 | 97.89% | 0 | 0% | 44.54 | 44.01 | 98.81% | 0 | 0% | 44.54 | 44.45 | 99.8% | 0 | 0%
GNA_012091106_Capacity | Bay Area | East Bay | OAKLAND J 1106 | 12091106 | Feeder | None | None | None | 99.87% | 0 | 0% | 7.7 | 7.69 | 99.87% | 0 | 0% | 7.7 | 6.89 | 89.48% | 0 | 0% | 7.7 | 6.97 | 90.52% | 0 | 0% | 7.7 | 7.15 | 92.86% | 0 | 0% | 7.7 | 7.32 | 95.06% | 0 | 0%
GNA_012091108_Capacity | Bay Area | East Bay | OAKLAND J 1108 | 12091108 | Feeder | None | None | None | 63% | 0 | 0% | 8.19 | 5.06 | 61.78% | 0 | 0% | 8.19 | 5.06 | 61.78% | 0 | 0% | 8.19 | 5.08 | 62.03% | 0 | 0% | 8.19 | 5.12 | 62.52% | 0 | 0% | 8.19 | 5.16 | 63% | 0 | 0%
GNA_012091110_Capacity | Bay Area | East Bay | OAKLAND J 1110 | 12091110 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012091111_Capacity | Bay Area | East Bay | OAKLAND J 1111 | 12091111 | Feeder | None | None | None | 68.74% | 0 | 0% | 8.19 | 5.63 | 68.74% | 0 | 0% | 8.19 | 5.59 | 68.25% | 0 | 0% | 8.19 | 5.59 | 68.25% | 0 | 0% | 8.19 | 5.58 | 68.13% | 0 | 0% | 8.19 | 5.59 | 68.25% | 0 | 0%
GNA_012091115_Capacity | Bay Area | East Bay | OAKLAND J 1115 | 12091115 | Feeder | None | None | None | 36.94% | 0 | 0% | 10.8 | 3.99 | 36.94% | 0 | 0% | 10.8 | 3.96 | 36.67% | 0 | 0% | 10.8 | 3.93 | 36.39% | 0 | 0% | 10.8 | 3.92 | 36.3% | 0 | 0% | 10.8 | 3.9 | 36.11% | 0 | 0%
GNA_012091118_Capacity | Bay Area | East Bay | OAKLAND J 1118 | 12091118 | Feeder | None | None | None | 65.08% | 0 | 0% | 8.19 | 5.04 | 61.54% | 0 | 0% | 8.19 | 5.08 | 62.03% | 0 | 0% | 8.19 | 5.12 | 62.52% | 0 | 0% | 8.19 | 5.22 | 63.74% | 0 | 0% | 8.19 | 5.33 | 65.08% | 0 | 0%
GNA_0139201_Capacity | Bay Area | East Bay | FRANKLIN BANK 1 | 139201 | Bank | None | None | None | 64.18% | 0 | 0% | 29.68 | 18.86 | 63.54% | 0 | 0% | 29.68 | 18.85 | 63.51% | 0 | 0% | 29.68 | 18.84 | 63.48% | 0 | 0% | 29.68 | 18.9 | 63.68% | 0 | 0% | 29.68 | 19.05 | 64.18% | 0 | 0%
GNA_013921101_Capacity | Bay Area | East Bay | FRANKLIN 1101 | 13921101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013921102_Capacity | Bay Area | East Bay | FRANKLIN 1102 | 13921102 | Feeder | None | None | None | 96.96% | 0 | 0% | 12.19 | 11.82 | 96.96% | 0 | 0% | 12.19 | 11.75 | 96.39% | 0 | 0% | 12.19 | 11.68 | 95.82% | 0 | 0% | 12.19 | 11.64 | 95.49% | 0 | 0% | 12.19 | 11.67 | 95.73% | 0 | 0%
GNA_0139202_Capacity | Bay Area | East Bay | FRANKLIN BANK 2 | 139202 | Bank | None | None | None | 79.21% | 0 | 0% | 29.68 | 22.5 | 75.81% | 0 | 0% | 29.68 | 22.65 | 76.31% | 0 | 0% | 29.68 | 22.81 | 76.85% | 0 | 0% | 29.68 | 23.12 | 77.9% | 0 | 0% | 29.68 | 23.51 | 79.21% | 0 | 0%
GNA_013921103_Capacity | Bay Area | East Bay | FRANKLIN 1103 | 13921103 | Feeder | None | None | None | 87.02% | 0 | 0% | 13.17 | 11.19 | 84.97% | 0 | 0% | 13.17 | 11.22 | 85.19% | 0 | 0% | 13.17 | 11.23 | 85.27% | 0 | 0% | 13.17 | 11.32 | 85.95% | 0 | 0% | 13.17 | 11.46 | 87.02% | 0 | 0%
GNA_013921104_Capacity | Bay Area | East Bay | FRANKLIN 1104 | 13921104 | Feeder | None | None | None | 97.19% | 0 | 0% | 12.83 | 11.84 | 92.28% | 0 | 0% | 12.83 | 11.93 | 92.99% | 0 | 0% | 12.83 | 12.06 | 94% | 0 | 0% | 12.83 | 12.25 | 95.48% | 0 | 0% | 12.83 | 12.47 | 97.19% | 0 | 0%
GNA_0142601_Capacity | Bay Area | East Bay | POINT PINOLE BANK 1 | 142601 | Bank | Demand Growth | Capacity | 2024 | 117.7% | 2.79 | 17.66% | 15.8 | 15.72 | 99.49% | 0 | 0% | 15.8 | 17.59 | 111.3% | 1.79 | 11.33% | 15.8 | 17.75 | 112.3% | 1.95 | 12.34% | 15.8 | 18.1 | 114.6% | 2.3 | 14.56% | 15.8 | 18.59 | 117.7% | 2.79 | 17.66%
GNA_014261101_Capacity | Bay Area | East Bay | POINT PINOLE 1101 | 14261101 | Feeder | None | None | None | 80.31% | 0 | 0% | 12.19 | 8.63 | 70.8% | 0 | 0% | 12.19 | 8.96 | 73.5% | 0 | 0% | 12.19 | 9.14 | 74.98% | 0 | 0% | 12.19 | 9.45 | 77.52% | 0 | 0% | 12.19 | 9.79 | 80.31% | 0 | 0%
GNA_014261102_Capacity | Bay Area | East Bay | POINT PINOLE 1102 | 14261102 | Feeder | None | None | None | 81.13% | 0 | 0% | 12.19 | 8.17 | 67.02% | 0 | 0% | 12.19 | 9.73 | 79.82% | 0 | 0% | 12.19 | 9.73 | 79.82% | 0 | 0% | 12.19 | 9.78 | 80.23% | 0 | 0% | 12.19 | 9.89 | 81.13% | 0 | 0%
GNA_0143701_Capacity | Bay Area | East Bay | SAN PABLO BANK 1 | 143701 | Bank | None | None | None | 42.93% | 0 | 0% | 44.54 | 19.09 | 42.86% | 0 | 0% | 44.54 | 18.94 | 42.52% | 0 | 0% | 44.54 | 18.83 | 42.28% | 0 | 0% | 44.54 | 18.9 | 42.43% | 0 | 0% | 44.54 | 19.12 | 42.93% | 0 | 0%
GNA_014371105_Capacity | Bay Area | East Bay | SAN PABLO 1105 | 14371105 | Feeder | None | None | None | 65.96% | 0 | 0% | 12.72 | 7.48 | 58.81% | 0 | 0% | 12.72 | 7.6 | 59.75% | 0 | 0% | 12.72 | 7.73 | 60.77% | 0 | 0% | 12.72 | 8.03 | 63.13% | 0 | 0% | 12.72 | 8.39 | 65.96% | 0 | 0%
GNA_014371106_Capacity | Bay Area | East Bay | SAN PABLO 1106 | 14371106 | Feeder | None | None | None | 99.92% | 0 | 0% | 12.72 | 12.71 | 99.92% | 0 | 0% | 12.72 | 12.65 | 99.45% | 0 | 0% | 12.72 | 12.61 | 99.14% | 0 | 0% | 12.72 | 12.6 | 99.06% | 0 | 0% | 12.72 | 12.64 | 99.37% | 0 | 0%
GNA_0143401_Capacity | Bay Area | East Bay | VALLEY VIEW BANK 1 | 143401 | Bank | None | None | None | 84.47% | 0 | 0% | 11.59 | 8.74 | 75.41% | 0 | 0% | 11.59 | 8.93 | 77.05% | 0 | 0% | 11.59 | 9.14 | 78.86% | 0 | 0% | 11.59 | 9.43 | 81.36% | 0 | 0% | 11.59 | 9.79 | 84.47% | 0 | 0%
GNA_014341103_Capacity | Bay Area | East Bay | VALLEY VIEW 1103 | 14341103 | Feeder | None | None | None | 90.37% | 0 | 0% | 10.8 | 8.71 | 80.65% | 0 | 0% | 10.8 | 8.9 | 82.41% | 0 | 0% | 10.8 | 9.11 | 84.35% | 0 | 0% | 10.8 | 9.4 | 87.04% | 0 | 0% | 10.8 | 9.76 | 90.37% | 0 | 0%
GNA_0143402_Capacity | Bay Area | East Bay | VALLEY VIEW BANK 2 | 143402 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014341105_Capacity | Bay Area | East Bay | VALLEY VIEW 1105 | 14341105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014341106_Capacity | Bay Area | East Bay | VALLEY VIEW 1106 | 14341106 | Feeder | Demand Growth | Capacity | 2027 | 100.9% | 0.1 | 0.9372% | 10.67 | 9.99 | 93.63% | 0 | 0% | 10.67 | 9.94 | 93.16% | 0 | 0% | 10.67 | 10.14 | 95.03% | 0 | 0% | 10.67 | 10.46 | 98.03% | 0 | 0% | 10.67 | 10.77 | 100.9% | 0.1 | 0.9372%
GNA_0125001_Capacity | Bay Area | East Bay | EL CERRITO G BANK 1 | 125001 | Bank | None | None | None | 49.92% | 0 | 0% | 59.38 | 26.72 | 45% | 0 | 0% | 59.38 | 27.26 | 45.91% | 0 | 0% | 59.38 | 27.8 | 46.82% | 0 | 0% | 59.38 | 28.65 | 48.25% | 0 | 0% | 59.38 | 29.64 | 49.92% | 0 | 0%
GNA_012501101_Capacity | Bay Area | East Bay | EL CERRITO G 1101 | 12501101 | Feeder | None | None | None | 81.18% | 0 | 0% | 8.13 | 6.02 | 74.05% | 0 | 0% | 8.13 | 6.14 | 75.52% | 0 | 0% | 8.13 | 6.27 | 77.12% | 0 | 0% | 8.13 | 6.42 | 78.97% | 0 | 0% | 8.13 | 6.6 | 81.18% | 0 | 0%
GNA_012501102_Capacity | Bay Area | East Bay | EL CERRITO G 1102 | 12501102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012501107_Capacity | Bay Area | East Bay | EL CERRITO G 1107 | 12501107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012501109_Capacity | Bay Area | East Bay | EL CERRITO G 1109 | 12501109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012501111_Capacity | Bay Area | East Bay | EL CERRITO G 1111 | 12501111 | Feeder | None | None | None | 82.42% | 0 | 0% | 8.19 | 6.29 | 76.8% | 0 | 0% | 8.19 | 6.33 | 77.29% | 0 | 0% | 8.19 | 6.39 | 78.02% | 0 | 0% | 8.19 | 6.54 | 79.85% | 0 | 0% | 8.19 | 6.75 | 82.42% | 0 | 0%
GNA_0125202_Capacity | Bay Area | East Bay | RICHMOND Q BANK 2 | 125202 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012520402_Capacity | Bay Area | East Bay | RICHMOND Q 0402 | 12520402 | Feeder | None | None | None | 29.36% | 0 | 0% | 2.18 | 0.6 | 27.52% | 0 | 0% | 2.18 | 0.61 | 27.98% | 0 | 0% | 2.18 | 0.61 | 27.98% | 0 | 0% | 2.18 | 0.62 | 28.44% | 0 | 0% | 2.18 | 0.64 | 29.36% | 0 | 0%
GNA_0123301_Capacity | Bay Area | East Bay | MIRA VISTA BANK 1 | 123301 | Bank | None | None | None | 45.45% | 0 | 0% | 3.96 | 1.56 | 39.39% | 0 | 0% | 3.96 | 1.57 | 39.65% | 0 | 0% | 3.96 | 1.6 | 40.4% | 0 | 0% | 3.96 | 1.67 | 42.17% | 0 | 0% | 3.96 | 1.8 | 45.45% | 0 | 0%
GNA_012330401_Capacity | Bay Area | East Bay | MIRA VISTA 0401 | 12330401 | Feeder | None | None | None | 64.96% | 0 | 0% | 2.74 | 1.54 | 56.2% | 0 | 0% | 2.74 | 1.56 | 56.93% | 0 | 0% | 2.74 | 1.58 | 57.66% | 0 | 0% | 2.74 | 1.66 | 60.58% | 0 | 0% | 2.74 | 1.78 | 64.96% | 0 | 0%
GNA_012501112_Capacity | Bay Area | East Bay | EL CERRITO G 1112 | 12501112 | Feeder | None | None | None | 96.6% | 0 | 0% | 9.13 | 7.15 | 78.31% | 0 | 0% | 9.13 | 7.48 | 81.93% | 0 | 0% | 9.13 | 7.81 | 85.54% | 0 | 0% | 9.13 | 8.29 | 90.8% | 0 | 0% | 9.13 | 8.82 | 96.6% | 0 | 0%
GNA_0123302_Capacity | Bay Area | East Bay | MIRA VISTA BANK 2 | 123302 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012330403_Capacity | Bay Area | East Bay | MIRA VISTA 0403 | 12330403 | Feeder | None | None | None | 58.4% | 0 | 0% | 2.5 | 1.2 | 48% | 0 | 0% | 2.5 | 1.24 | 49.6% | 0 | 0% | 2.5 | 1.29 | 51.6% | 0 | 0% | 2.5 | 1.36 | 54.4% | 0 | 0% | 2.5 | 1.46 | 58.4% | 0 | 0%
GNA_0125002_Capacity | Bay Area | East Bay | EL CERRITO G BANK 2 | 125002 | Bank | None | None | None | 67.63% | 0 | 0% | 59.38 | 36.19 | 60.95% | 0 | 0% | 59.38 | 36.41 | 61.32% | 0 | 0% | 59.38 | 37.12 | 62.51% | 0 | 0% | 59.38 | 38.19 | 64.31% | 0 | 0% | 59.38 | 40.16 | 67.63% | 0 | 0%
GNA_012501106_Capacity | Bay Area | East Bay | EL CERRITO G 1106 | 12501106 | Feeder | None | None | None | 61.13% | 0 | 0% | 8.13 | 4.53 | 55.72% | 0 | 0% | 8.13 | 4.64 | 57.07% | 0 | 0% | 8.13 | 4.73 | 58.18% | 0 | 0% | 8.13 | 4.85 | 59.66% | 0 | 0% | 8.13 | 4.97 | 61.13% | 0 | 0%
GNA_012501108_Capacity | Bay Area | East Bay | EL CERRITO G 1108 | 12501108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0137001_Capacity | Bay Area | East Bay | ARLINGTON BANK 1 | 137001 | Bank | None | None | None | 36.58% | 0 | 0% | 2.57 | 0.81 | 31.52% | 0 | 0% | 2.57 | 0.83 | 32.3% | 0 | 0% | 2.57 | 0.86 | 33.46% | 0 | 0% | 2.57 | 0.9 | 35.02% | 0 | 0% | 2.57 | 0.94 | 36.58% | 0 | 0%
GNA_013700401_Capacity | Bay Area | East Bay | ARLINGTON 0401 | 13700401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0126502_Capacity | Bay Area | East Bay | FAIRMOUNT BANK 2 | 126502 | Bank | None | None | None | 46.15% | 0 | 0% | 2.47 | 1.03 | 41.7% | 0 | 0% | 2.47 | 1.04 | 42.11% | 0 | 0% | 2.47 | 1.06 | 42.91% | 0 | 0% | 2.47 | 1.1 | 44.53% | 0 | 0% | 2.47 | 1.14 | 46.15% | 0 | 0%
GNA_012650402_Capacity | Bay Area | East Bay | FAIRMOUNT 0402 | 12650402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0120601_Capacity | Bay Area | East Bay | BERKELEY F BANK 1 | 120601 | Bank | None | None | None | 24.15% | 0 | 0% | 12.38 | 2.72 | 21.97% | 0 | 0% | 12.38 | 2.74 | 22.13% | 0 | 0% | 12.38 | 2.78 | 22.46% | 0 | 0% | 12.38 | 2.86 | 23.1% | 0 | 0% | 12.38 | 2.99 | 24.15% | 0 | 0%
GNA_012060401_Capacity | Bay Area | East Bay | BERKELEY F 0401 | 12060401 | Feeder | None | None | None | 3.07% | 0 | 0% | 2.28 | 0.07 | 3.07% | 0 | 0% | 2.28 | 0.07 | 3.07% | 0 | 0% | 2.28 | 0.07 | 3.07% | 0 | 0% | 2.28 | 0.07 | 3.07% | 0 | 0% | 2.28 | 0.07 | 3.07% | 0 | 0%
GNA_012060404_Capacity | Bay Area | East Bay | BERKELEY F 0404 | 12060404 | Feeder | None | None | None | 46.93% | 0 | 0% | 2.28 | 0.9 | 39.47% | 0 | 0% | 2.28 | 0.92 | 40.35% | 0 | 0% | 2.28 | 0.93 | 40.79% | 0 | 0% | 2.28 | 0.98 | 42.98% | 0 | 0% | 2.28 | 1.07 | 46.93% | 0 | 0%
GNA_012060405_Capacity | Bay Area | East Bay | BERKELEY F 0405 | 12060405 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012060406_Capacity | Bay Area | East Bay | BERKELEY F 0406 | 12060406 | Feeder | None | None | None | 58.75% | 0 | 0% | 1.6 | 0.84 | 52.5% | 0 | 0% | 1.6 | 0.85 | 53.12% | 0 | 0% | 1.6 | 0.87 | 54.37% | 0 | 0% | 1.6 | 0.9 | 56.25% | 0 | 0% | 1.6 | 0.94 | 58.75% | 0 | 0%
GNA_012060407_Capacity | Bay Area | East Bay | BERKELEY F 0407 | 12060407 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0120602_Capacity | Bay Area | East Bay | BERKELEY F BANK 2 | 120602 | Bank | None | None | None | 39.74% | 0 | 0% | 12.38 | 4.46 | 36.03% | 0 | 0% | 12.38 | 4.5 | 36.35% | 0 | 0% | 12.38 | 4.6 | 37.16% | 0 | 0% | 12.38 | 4.79 | 38.69% | 0 | 0% | 12.38 | 4.92 | 39.74% | 0 | 0%
GNA_012060402_Capacity | Bay Area | East Bay | BERKELEY F 0402 | 12060402 | Feeder | None | None | None | 50% | 0 | 0% | 2.28 | 1.1 | 48.25% | 0 | 0% | 2.28 | 1.11 | 48.68% | 0 | 0% | 2.28 | 1.12 | 49.12% | 0 | 0% | 2.28 | 1.13 | 49.56% | 0 | 0% | 2.28 | 1.14 | 50% | 0 | 0%
GNA_012060403_Capacity | Bay Area | East Bay | BERKELEY F 0403 | 12060403 | Feeder | None | None | None | 36.4% | 0 | 0% | 2.28 | 0.75 | 32.89% | 0 | 0% | 2.28 | 0.75 | 32.89% | 0 | 0% | 2.28 | 0.76 | 33.33% | 0 | 0% | 2.28 | 0.8 | 35.09% | 0 | 0% | 2.28 | 0.83 | 36.4% | 0 | 0%
GNA_012060408_Capacity | Bay Area | East Bay | BERKELEY F 0408 | 12060408 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012060409_Capacity | Bay Area | East Bay | BERKELEY F 0409 | 12060409 | Feeder | None | None | None | 55.19% | 0 | 0% | 1.83 | 0.91 | 49.73% | 0 | 0% | 1.83 | 0.92 | 50.27% | 0 | 0% | 1.83 | 0.95 | 51.91% | 0 | 0% | 1.83 | 1 | 54.64% | 0 | 0% | 1.83 | 1.01 | 55.19% | 0 | 0%
GNA_012060410_Capacity | Bay Area | East Bay | BERKELEY F 0410 | 12060410 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012060411_Capacity | Bay Area | East Bay | BERKELEY F 0411 | 12060411 | Feeder | None | None | None | 40.17% | 0 | 0% | 2.39 | 0.84 | 35.15% | 0 | 0% | 2.39 | 0.85 | 35.56% | 0 | 0% | 2.39 | 0.87 | 36.4% | 0 | 0% | 2.39 | 0.91 | 38.08% | 0 | 0% | 2.39 | 0.96 | 40.17% | 0 | 0%
GNA_0126601_Capacity | Bay Area | East Bay | BERKELEY T BANK 1 | 126601 | Bank | None | None | None | 4.848% | 0 | 0% | 4.95 | -0.24 | -4.848% | 0 | 0% | 4.95 | -0.24 | -4.848% | 0 | 0% | 4.95 | -0.24 | -4.848% | 0 | 0% | 4.95 | -0.23 | -4.646% | 0 | 0% | 4.95 | -0.22 | -4.444% | 0 | 0%
GNA_012660401_Capacity | Bay Area | East Bay | BERKELEY T 0401 | 12660401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012660404_Capacity | Bay Area | East Bay | BERKELEY T 0404 | 12660404 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012061102_Capacity | Bay Area | East Bay | BERKELEY F 1102 | 12061102 | Feeder | None | None | None | 67.16% | 0 | 0% | 8.19 | 5.49 | 67.03% | 0 | 0% | 8.19 | 5.5 | 67.16% | 0 | 0% | 8.19 | 5.5 | 67.16% | 0 | 0% | 8.19 | 5.49 | 67.03% | 0 | 0% | 8.19 | 5.5 | 67.16% | 0 | 0%
GNA_012061103_Capacity | Bay Area | East Bay | BERKELEY F 1103 | 12061103 | Feeder | None | None | None | 69.01% | 0 | 0% | 9.26 | 6.32 | 68.25% | 0 | 0% | 9.26 | 6.28 | 67.82% | 0 | 0% | 9.26 | 6.28 | 67.82% | 0 | 0% | 9.26 | 6.32 | 68.25% | 0 | 0% | 9.26 | 6.39 | 69.01% | 0 | 0%
GNA_012061104_Capacity | Bay Area | East Bay | BERKELEY F 1104 (FT2/F1152) | 12061104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0126602_Capacity | Bay Area | East Bay | BERKELEY T BANK 2 | 126602 | Bank | None | None | None | 18.38% | 0 | 0% | 4.95 | -0.34 | -6.869% | 0 | 0% | 4.95 | -0.91 | -18.38% | 0 | 0% | 4.95 | -0.9 | -18.18% | 0 | 0% | 4.95 | -0.86 | -17.37% | 0 | 0% | 4.95 | -0.81 | -16.36% | 0 | 0%
GNA_012660402_Capacity | Bay Area | East Bay | BERKELEY T 0402 | 12660402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012660403_Capacity | Bay Area | East Bay | BERKELEY T 0403 | 12660403 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012061105_Capacity | Bay Area | East Bay | BERKELEY F 1105 | 12061105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0128402_Capacity | Bay Area | East Bay | RIDGE BANK 2 | 128402 | Bank | None | None | None | 32.83% | 0 | 0% | 1.98 | 0.56 | 28.28% | 0 | 0% | 1.98 | 0.58 | 29.29% | 0 | 0% | 1.98 | 0.6 | 30.3% | 0 | 0% | 1.98 | 0.63 | 31.82% | 0 | 0% | 1.98 | 0.65 | 32.83% | 0 | 0%
GNA_012840402_Capacity | Bay Area | East Bay | RIDGE 0402 | 12840402 | Feeder | None | None | None | 34.97% | 0 | 0% | 1.83 | 0.55 | 30.05% | 0 | 0% | 1.83 | 0.57 | 31.15% | 0 | 0% | 1.83 | 0.59 | 32.24% | 0 | 0% | 1.83 | 0.62 | 33.88% | 0 | 0% | 1.83 | 0.64 | 34.97% | 0 | 0%
GNA_0125003_Capacity | Bay Area | East Bay | EL CERRITO G BANK 3 | 125003 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012501103_Capacity | Bay Area | East Bay | EL CERRITO G 1103 | 12501103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012501104_Capacity | Bay Area | East Bay | EL CERRITO G 1104 | 12501104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0126501_Capacity | Bay Area | East Bay | FAIRMOUNT BANK 1 | 126501 | Bank | None | None | None | 51.75% | 0 | 0% | 2.28 | 0.98 | 42.98% | 0 | 0% | 2.28 | 1.01 | 44.3% | 0 | 0% | 2.28 | 1.03 | 45.18% | 0 | 0% | 2.28 | 1.09 | 47.81% | 0 | 0% | 2.28 | 1.18 | 51.75% | 0 | 0%
GNA_012650401_Capacity | Bay Area | East Bay | FAIRMOUNT 0401 | 12650401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012501105_Capacity | Bay Area | East Bay | EL CERRITO G 1105 | 12501105 | Feeder | None | None | None | 88.42% | 0 | 0% | 10.97 | 8.55 | 77.94% | 0 | 0% | 10.97 | 8.76 | 79.85% | 0 | 0% | 10.97 | 8.99 | 81.95% | 0 | 0% | 10.97 | 9.32 | 84.96% | 0 | 0% | 10.97 | 9.7 | 88.42% | 0 | 0%
GNA_0128401_Capacity | Bay Area | East Bay | RIDGE BANK 1 | 128401 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012840401_Capacity | Bay Area | East Bay | RIDGE 0401 | 12840401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012501110_Capacity | Bay Area | East Bay | EL CERRITO G 1110 | 12501110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0126001_Capacity | Bay Area | East Bay | OAK BANK 1 | 126001 | Bank | None | None | None | 45.37% | 0 | 0% | 2.27 | 0.92 | 40.53% | 0 | 0% | 2.27 | 0.94 | 41.41% | 0 | 0% | 2.27 | 0.96 | 42.29% | 0 | 0% | 2.27 | 1 | 44.05% | 0 | 0% | 2.27 | 1.03 | 45.37% | 0 | 0%
GNA_012600401_Capacity | Bay Area | East Bay | OAK 0401 | 12600401 | Feeder | None | None | None | 40.8% | 0 | 0% | 2.5 | 0.91 | 36.4% | 0 | 0% | 2.5 | 0.93 | 37.2% | 0 | 0% | 2.5 | 0.95 | 38% | 0 | 0% | 2.5 | 0.99 | 39.6% | 0 | 0% | 2.5 | 1.02 | 40.8% | 0 | 0%
GNA_0131402_Capacity | Bay Area | East Bay | SOLANO BANK 2 | 131402 | Bank | None | None | None | 27.27% | 0 | 0% | 1.98 | 0.07 | 3.535% | 0 | 0% | 1.98 | 0.13 | 6.566% | 0 | 0% | 1.98 | 0.22 | 11.11% | 0 | 0% | 1.98 | 0.36 | 18.18% | 0 | 0% | 1.98 | 0.54 | 27.27% | 0 | 0%
GNA_013140402_Capacity | Bay Area | East Bay | SOLANO 0402 | 13140402 | Feeder | None | None | None | 24.77% | 0 | 0% | 2.18 | 0.07 | 3.211% | 0 | 0% | 2.18 | 0.13 | 5.963% | 0 | 0% | 2.18 | 0.22 | 10.09% | 0 | 0% | 2.18 | 0.36 | 16.51% | 0 | 0% | 2.18 | 0.54 | 24.77% | 0 | 0%
GNA_012501113_Capacity | Bay Area | East Bay | EL CERRITO G 1113 | 12501113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012501114_Capacity | Bay Area | East Bay | EL CERRITO G 1114 | 12501114 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0133501_Capacity | Bay Area | East Bay | WALDO BANK 1 | 133501 | Bank | None | None | None | 55.95% | 0 | 0% | 2.27 | 1.13 | 49.78% | 0 | 0% | 2.27 | 1.15 | 50.66% | 0 | 0% | 2.27 | 1.16 | 51.1% | 0 | 0% | 2.27 | 1.21 | 53.3% | 0 | 0% | 2.27 | 1.27 | 55.95% | 0 | 0%
GNA_013350401_Capacity | Bay Area | East Bay | WALDO 0401 | 13350401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0133502_Capacity | Bay Area | East Bay | WALDO BANK 2 | 133502 | Bank | None | None | None | 53.03% | 0 | 0% | 1.98 | 0.92 | 46.46% | 0 | 0% | 1.98 | 0.94 | 47.47% | 0 | 0% | 1.98 | 0.96 | 48.48% | 0 | 0% | 1.98 | 1 | 50.51% | 0 | 0% | 1.98 | 1.05 | 53.03% | 0 | 0%
GNA_013350402_Capacity | Bay Area | East Bay | WALDO 0402 | 13350402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0134702_Capacity | Bay Area | East Bay | RICHMOND R BANK 2 | 134702 | Bank | None | None | None | 99.42% | 0 | 0% | 44.6 | 38.55 | 86.43% | 0 | 0% | 44.6 | 42.93 | 96.26% | 0 | 0% | 44.6 | 43.27 | 97.02% | 0 | 0% | 44.6 | 43.77 | 98.14% | 0 | 0% | 44.6 | 44.34 | 99.42% | 0 | 0%
GNA_013471118_Capacity | Bay Area | East Bay | RICHMOND R 1118 | 13471118 | Feeder | None | None | None | 45.67% | 0 | 0% | 12.83 | 5.46 | 42.56% | 0 | 0% | 12.83 | 5.57 | 43.41% | 0 | 0% | 12.83 | 5.63 | 43.88% | 0 | 0% | 12.83 | 5.77 | 44.97% | 0 | 0% | 12.83 | 5.86 | 45.67% | 0 | 0%
GNA_013471120_Capacity | Bay Area | East Bay | RICHMOND R 1120 | 13471120 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013471121_Capacity | Bay Area | East Bay | RICHMOND R 1121 | 13471121 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013471123_Capacity | Bay Area | East Bay | RICHMOND R 1123 | 13471123 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013471124_Capacity | Bay Area | East Bay | RICHMOND R 1124 | 13471124 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013471125_Capacity | Bay Area | East Bay | RICHMOND R 1125 | 13471125 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0125201_Capacity | Bay Area | East Bay | RICHMOND Q BANK 1 | 125201 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012520401_Capacity | Bay Area | East Bay | RICHMOND Q 0401 | 12520401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0137801_Capacity | Bay Area | East Bay | VIRGINIA BANK 1 | 137801 | Bank | None | None | None | 43.94% | 0 | 0% | 1.98 | 0.85 | 42.93% | 0 | 0% | 1.98 | 0.86 | 43.43% | 0 | 0% | 1.98 | 0.86 | 43.43% | 0 | 0% | 1.98 | 0.87 | 43.94% | 0 | 0% | 1.98 | 0.87 | 43.94% | 0 | 0%
GNA_013780401_Capacity | Bay Area | East Bay | VIRGINIA 0401 | 13780401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013471126_Capacity | Bay Area | East Bay | RICHMOND R 1126 | 13471126 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0132101_Capacity | Bay Area | East Bay | BROOKSIDE BANK 1 | 132101 | Bank | None | None | None | 42.93% | 0 | 0% | 1.98 | 0.82 | 41.41% | 0 | 0% | 1.98 | 0.82 | 41.41% | 0 | 0% | 1.98 | 0.83 | 41.92% | 0 | 0% | 1.98 | 0.83 | 41.92% | 0 | 0% | 1.98 | 0.85 | 42.93% | 0 | 0%
GNA_013210401_Capacity | Bay Area | East Bay | BROOKSIDE 0401 | 13210401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0134703_Capacity | Bay Area | East Bay | RICHMOND R BANK 3 | 134703 | Bank | None | None | None | 98.7% | 0 | 0% | 44.6 | 39.36 | 88.25% | 0 | 0% | 44.6 | 39.62 | 88.83% | 0 | 0% | 44.6 | 43.11 | 96.66% | 0 | 0% | 44.6 | 43.5 | 97.53% | 0 | 0% | 44.6 | 44.02 | 98.7% | 0 | 0%
GNA_013471119_Capacity | Bay Area | East Bay | RICHMOND R 1119 | 13471119 | Feeder | None | None | None | 85.95% | 0 | 0% | 9.54 | 7.85 | 82.29% | 0 | 0% | 9.54 | 7.94 | 83.23% | 0 | 0% | 9.54 | 8 | 83.86% | 0 | 0% | 9.54 | 8.09 | 84.8% | 0 | 0% | 9.54 | 8.2 | 85.95% | 0 | 0%
GNA_0130201_Capacity | Bay Area | East Bay | BARRETT BANK 1 | 130201 | Bank | None | None | None | 69.72% | 0 | 0% | 2.18 | 1.48 | 67.89% | 0 | 0% | 2.18 | 1.49 | 68.35% | 0 | 0% | 2.18 | 1.49 | 68.35% | 0 | 0% | 2.18 | 1.51 | 69.27% | 0 | 0% | 2.18 | 1.52 | 69.72% | 0 | 0%
GNA_013020401_Capacity | Bay Area | East Bay | BARRETT 0401 | 13020401 | Feeder | None | None | None | 68.35% | 0 | 0% | 2.18 | 1.45 | 66.51% | 0 | 0% | 2.18 | 1.46 | 66.97% | 0 | 0% | 2.18 | 1.46 | 66.97% | 0 | 0% | 2.18 | 1.48 | 67.89% | 0 | 0% | 2.18 | 1.49 | 68.35% | 0 | 0%
GNA_0130202_Capacity | Bay Area | East Bay | BARRETT BANK 2 | 130202 | Bank | None | None | None | 56.88% | 0 | 0% | 2.18 | 1.16 | 53.21% | 0 | 0% | 2.18 | 1.17 | 53.67% | 0 | 0% | 2.18 | 1.17 | 53.67% | 0 | 0% | 2.18 | 1.19 | 54.59% | 0 | 0% | 2.18 | 1.24 | 56.88% | 0 | 0%
GNA_013020402_Capacity | Bay Area | East Bay | BARRETT 0402 | 13020402 | Feeder | None | None | None | 58.1% | 0 | 0% | 2.1 | 1.14 | 54.29% | 0 | 0% | 2.1 | 1.15 | 54.76% | 0 | 0% | 2.1 | 1.16 | 55.24% | 0 | 0% | 2.1 | 1.18 | 56.19% | 0 | 0% | 2.1 | 1.22 | 58.1% | 0 | 0%
GNA_013471122_Capacity | Bay Area | East Bay | RICHMOND R 1122 | 13471122 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013471127_Capacity | Bay Area | East Bay | RICHMOND R 1127 | 13471127 | Feeder | None | None | None | 90.41% | 0 | 0% | 11.57 | 10.34 | 89.37% | 0 | 0% | 11.57 | 10.35 | 89.46% | 0 | 0% | 11.57 | 10.36 | 89.54% | 0 | 0% | 11.57 | 10.38 | 89.71% | 0 | 0% | 11.57 | 10.46 | 90.41% | 0 | 0%
GNA_013471128_Capacity | Bay Area | East Bay | RICHMOND R 1128 | 13471128 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0137401_Capacity | Bay Area | East Bay | WALL BANK 1 | 137401 | Bank | None | None | None | 46.93% | 0 | 0% | 2.28 | 0.95 | 41.67% | 0 | 0% | 2.28 | 0.97 | 42.54% | 0 | 0% | 2.28 | 0.99 | 43.42% | 0 | 0% | 2.28 | 1.03 | 45.18% | 0 | 0% | 2.28 | 1.07 | 46.93% | 0 | 0%
GNA_013740401_Capacity | Bay Area | East Bay | WALL 0401 | 13740401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013471129_Capacity | Bay Area | East Bay | RICHMOND R 1129 | 13471129 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013471130_Capacity | Bay Area | East Bay | RICHMOND R 1130 | 13471130 | Feeder | None | None | None | 61.45% | 0 | 0% | 9.52 | 5.69 | 59.77% | 0 | 0% | 9.52 | 5.7 | 59.87% | 0 | 0% | 9.52 | 5.7 | 59.87% | 0 | 0% | 9.52 | 5.76 | 60.5% | 0 | 0% | 9.52 | 5.85 | 61.45% | 0 | 0%
GNA_2515102_Capacity | Central Valley | Fresno | AG WISHON POWERHOUSE BANK 2 | 2515102 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_251511101_Capacity | Central Valley | Fresno | AG WISHON 1101 | 251511101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2541501_Capacity | Central Valley | Fresno | AUBERRY BANK 1 | 2541501 | Bank | None | None | None | 53.07% | 0 | 0% | 12.36 | 6.54 | 52.91% | 0 | 0% | 12.36 | 6.51 | 52.67% | 0 | 0% | 12.36 | 6.49 | 52.51% | 0 | 0% | 12.36 | 6.51 | 52.67% | 0 | 0% | 12.36 | 6.56 | 53.07% | 0 | 0%
GNA_254151102_Capacity | Central Valley | Fresno | AUBERRY 1102 | 254151102 | Feeder | None | None | None | 61.93% | 0 | 0% | 10.69 | 6.6 | 61.74% | 0 | 0% | 10.69 | 6.57 | 61.46% | 0 | 0% | 10.69 | 6.54 | 61.18% | 0 | 0% | 10.69 | 6.57 | 61.46% | 0 | 0% | 10.69 | 6.62 | 61.93% | 0 | 0%
GNA_2541502_Capacity | Central Valley | Fresno | AUBERRY BANK 2 | 2541502 | Bank | None | None | None | 68.04% | 0 | 0% | 12.36 | 8.09 | 65.45% | 0 | 0% | 12.36 | 8.11 | 65.61% | 0 | 0% | 12.36 | 8.17 | 66.1% | 0 | 0% | 12.36 | 8.24 | 66.67% | 0 | 0% | 12.36 | 8.41 | 68.04% | 0 | 0%
GNA_254151101_Capacity | Central Valley | Fresno | AUBERRY 1101 | 254151101 | Feeder | None | None | None | 67.19% | 0 | 0% | 12.83 | 8.3 | 64.69% | 0 | 0% | 12.83 | 8.32 | 64.85% | 0 | 0% | 12.83 | 8.38 | 65.32% | 0 | 0% | 12.83 | 8.44 | 65.78% | 0 | 0% | 12.83 | 8.62 | 67.19% | 0 | 0%
GNA_2525001_Capacity | Central Valley | Fresno | BALCH NO 1 BANK 1 | 2525001 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252501101_Capacity | Central Valley | Fresno | BALCH NO 1 1101 | 252501101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_259932101_Capacity | Central Valley | Fresno | HAAS 2101 | 259932101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2525604_Capacity | Central Valley | Fresno | KERCKHOFF BANK 4 | 2525604 | Bank | None | None | None | 4.735% | 0 | 0% | 15.84 | 0.75 | 4.735% | 0 | 0% | 15.84 | 0.73 | 4.609% | 0 | 0% | 15.84 | 0.73 | 4.609% | 0 | 0% | 15.84 | 0.72 | 4.545% | 0 | 0% | 15.84 | 0.73 | 4.609% | 0 | 0%
GNA_252561101_Capacity | Central Valley | Fresno | KERCKHOFF 1101 | 252561101 | Feeder | None | None | None | 24.63% | 0 | 0% | 4.06 | 1 | 24.63% | 0 | 0% | 4.06 | 0.98 | 24.14% | 0 | 0% | 4.06 | 0.98 | 24.14% | 0 | 0% | 4.06 | 0.96 | 23.65% | 0 | 0% | 4.06 | 0.96 | 23.65% | 0 | 0%
GNA_2520501_Capacity | Central Valley | Fresno | ASHLAN AVENUE BANK 1 | 2520501 | Bank | None | None | None | 88.19% | 0 | 0% | 59.2 | 49.78 | 84.09% | 0 | 0% | 59.2 | 50.95 | 86.06% | 0 | 0% | 59.2 | 51.14 | 86.39% | 0 | 0% | 59.2 | 51.65 | 87.25% | 0 | 0% | 59.2 | 52.21 | 88.19% | 0 | 0%
GNA_252051102_Capacity | Central Valley | Fresno | ASHLAN AVENUE 1102 | 252051102 | Feeder | None | None | None | 83.58% | 0 | 0% | 9.56 | 7.95 | 83.16% | 0 | 0% | 9.56 | 7.85 | 82.11% | 0 | 0% | 9.56 | 7.84 | 82.01% | 0 | 0% | 9.56 | 7.9 | 82.64% | 0 | 0% | 9.56 | 7.99 | 83.58% | 0 | 0%
GNA_252051103_Capacity | Central Valley | Fresno | ASHLAN AVENUE 1103 | 252051103 | Feeder | None | None | None | 40% | 0 | 0% | 10.05 | 3.92 | 39% | 0 | 0% | 10.05 | 3.92 | 39% | 0 | 0% | 10.05 | 3.96 | 39.4% | 0 | 0% | 10.05 | 4.02 | 40% | 0 | 0% | 10.05 | 4.02 | 40% | 0 | 0%
GNA_252051107_Capacity | Central Valley | Fresno | ASHLAN AVENUE 1107 | 252051107 | Feeder | None | None | None | 84.52% | 0 | 0% | 8.98 | 7.59 | 84.52% | 0 | 0% | 8.98 | 7.53 | 83.85% | 0 | 0% | 8.98 | 7.46 | 83.07% | 0 | 0% | 8.98 | 7.5 | 83.52% | 0 | 0% | 8.98 | 7.59 | 84.52% | 0 | 0%
GNA_252051112_Capacity | Central Valley | Fresno | ASHLAN AVENUE 1112 | 252051112 | Feeder | Demand Growth | Capacity | 2023 | 113.6% | 1.37 | 13.63% | 10.05 | 11.15 | 110.9% | 1.1 | 10.95% | 10.05 | 11.17 | 111.1% | 1.12 | 11.14% | 10.05 | 11.18 | 111.2% | 1.13 | 11.24% | 10.05 | 11.28 | 112.2% | 1.23 | 12.24% | 10.05 | 11.42 | 113.6% | 1.37 | 13.63%
GNA_252051113_Capacity | Central Valley | Fresno | ASHLAN AVENUE 1113 | 252051113 | Feeder | None | None | None | 94% | 0 | 0% | 12.83 | 10.1 | 78.72% | 0 | 0% | 12.83 | 11.45 | 89.24% | 0 | 0% | 12.83 | 11.77 | 91.74% | 0 | 0% | 12.83 | 11.9 | 92.75% | 0 | 0% | 12.83 | 12.06 | 94% | 0 | 0%
GNA_252051114_Capacity | Central Valley | Fresno | ASHLAN AVENUE 1114 | 252051114 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2520502_Capacity | Central Valley | Fresno | ASHLAN AVENUE BANK 2 | 2520502 | Bank | None | None | None | 92.6% | 0 | 0% | 59.2 | 54.82 | 92.6% | 0 | 0% | 59.2 | 54.36 | 91.82% | 0 | 0% | 59.2 | 54.1 | 91.39% | 0 | 0% | 59.2 | 54.15 | 91.47% | 0 | 0% | 59.2 | 54.26 | 91.66% | 0 | 0%
GNA_252052101_Capacity | Central Valley | Fresno | ASHLAN AVENUE 2101 | 252052101 | Feeder | None | None | None | 30.7% | 0 | 0% | 18.63 | 5.72 | 30.7% | 0 | 0% | 18.63 | 5.66 | 30.38% | 0 | 0% | 18.63 | 5.63 | 30.22% | 0 | 0% | 18.63 | 5.62 | 30.17% | 0 | 0% | 18.63 | 5.61 | 30.11% | 0 | 0%
GNA_252052105_Capacity | Central Valley | Fresno | ASHLAN AVENUE 2105 | 252052105 | Feeder | None | None | None | 21.15% | 0 | 0% | 13 | 2.33 | 17.92% | 0 | 0% | 13 | 2.38 | 18.31% | 0 | 0% | 13 | 2.45 | 18.85% | 0 | 0% | 13 | 2.61 | 20.08% | 0 | 0% | 13 | 2.75 | 21.15% | 0 | 0%
GNA_252052110_Capacity | Central Valley | Fresno | ASHLAN AVENUE 2110 | 252052110 | Feeder | None | None | None | 38.85% | 0 | 0% | 17.63 | 6.85 | 38.85% | 0 | 0% | 17.63 | 6.8 | 38.57% | 0 | 0% | 17.63 | 6.75 | 38.29% | 0 | 0% | 17.63 | 6.75 | 38.29% | 0 | 0% | 17.63 | 6.8 | 38.57% | 0 | 0%
GNA_252052115_Capacity | Central Valley | Fresno | ASHLAN AVENUE 2115 | 252052115 | Feeder | None | None | None | 19.25% | 0 | 0% | 20 | 3.85 | 19.25% | 0 | 0% | 20 | 3.81 | 19.05% | 0 | 0% | 20 | 3.81 | 19.05% | 0 | 0% | 20 | 3.84 | 19.2% | 0 | 0% | 20 | 3.83 | 19.15% | 0 | 0%
GNA_252052117_Capacity | Central Valley | Fresno | ASHLAN AVENUE 2117 | 252052117 | Feeder | None | None | None | 39.7% | 0 | 0% | 21.41 | 8.5 | 39.7% | 0 | 0% | 21.41 | 8.44 | 39.42% | 0 | 0% | 21.41 | 8.37 | 39.09% | 0 | 0% | 21.41 | 8.31 | 38.81% | 0 | 0% | 21.41 | 8.28 | 38.67% | 0 | 0%
GNA_252052118_Capacity | Central Valley | Fresno | ASHLAN AVENUE 2118 | 252052118 | Feeder | None | None | None | 70.85% | 0 | 0% | 21.41 | 15.09 | 70.48% | 0 | 0% | 21.41 | 15.08 | 70.43% | 0 | 0% | 21.41 | 15.07 | 70.39% | 0 | 0% | 21.41 | 15.1 | 70.53% | 0 | 0% | 21.41 | 15.17 | 70.85% | 0 | 0%
GNA_252052119_Capacity | Central Valley | Fresno | ASHLAN AVENUE 2119 | 252052119 | Feeder | None | None | None | 79.53% | 0 | 0% | 16.56 | 13.14 | 79.35% | 0 | 0% | 16.56 | 13.03 | 78.68% | 0 | 0% | 16.56 | 13.03 | 78.68% | 0 | 0% | 16.56 | 13.12 | 79.23% | 0 | 0% | 16.56 | 13.17 | 79.53% | 0 | 0%
GNA_2520503_Capacity | Central Valley | Fresno | ASHLAN AVENUE BANK 3 | 2520503 | Bank | Demand Growth | Capacity | 2025 | 105.7% | 3.37 | 5.693% | 59.2 | 58.73 | 99.21% | 0 | 0% | 59.2 | 59.11 | 99.85% | 0 | 0% | 59.2 | 59.94 | 101.2% | 0.74 | 1.25% | 59.2 | 60.91 | 102.9% | 1.71 | 2.889% | 59.2 | 62.57 | 105.7% | 3.37 | 5.693%
GNA_252051104_Capacity | Central Valley | Fresno | ASHLAN AVENUE 1104 | 252051104 | Feeder | None | None | None | 94.12% | 0 | 0% | 9.02 | 8.24 | 91.35% | 0 | 0% | 9.02 | 8.49 | 94.12% | 0 | 0% | 9.02 | 6.84 | 75.83% | 0 | 0% | 9.02 | 7.16 | 79.38% | 0 | 0% | 9.02 | 8.19 | 90.8% | 0 | 0%
GNA_252051106_Capacity | Central Valley | Fresno | ASHLAN AVENUE 1106 | 252051106 | Feeder | None | None | None | 97.81% | 0 | 0% | 10.05 | 9.83 | 97.81% | 0 | 0% | 10.05 | 9.79 | 97.41% | 0 | 0% | 10.05 | 9.75 | 97.01% | 0 | 0% | 10.05 | 9.71 | 96.62% | 0 | 0% | 10.05 | 9.66 | 96.12% | 0 | 0%
GNA_252051108_Capacity | Central Valley | Fresno | ASHLAN AVENUE 1108 | 252051108 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252051109_Capacity | Central Valley | Fresno | ASHLAN AVENUE 1109 | 252051109 | Feeder | Demand Growth | Capacity | 2025 | 113.2% | 1.61 | 13.21% | 12.19 | 11.95 | 98.03% | 0 | 0% | 12.19 | 12.06 | 98.93% | 0 | 0% | 12.19 | 12.27 | 100.7% | 0.08 | 0.6563% | 12.19 | 12.9 | 105.8% | 0.71 | 5.824% | 12.19 | 13.8 | 113.2% | 1.61 | 13.21%
GNA_252051111_Capacity | Central Valley | Fresno | ASHLAN AVENUE 1111 | 252051111 | Feeder | None | None | None | 66.69% | 0 | 0% | 12.19 | 8.13 | 66.69% | 0 | 0% | 12.19 | 8.04 | 65.96% | 0 | 0% | 12.19 | 7.96 | 65.3% | 0 | 0% | 12.19 | 7.88 | 64.64% | 0 | 0% | 12.19 | 7.82 | 64.15% | 0 | 0%
GNA_252051116_Capacity | Central Valley | Fresno | ASHLAN AVENUE 1116 | 252051116 | Feeder | None | None | None | 89.83% | 0 | 0% | 12.19 | 10.95 | 89.83% | 0 | 0% | 12.19 | 10.82 | 88.76% | 0 | 0% | 12.19 | 10.7 | 87.78% | 0 | 0% | 12.19 | 10.63 | 87.2% | 0 | 0% | 12.19 | 10.67 | 87.53% | 0 | 0%
GNA_2535701_Capacity | Central Valley | Fresno | BARTON BANK 1 | 2535701 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253571101_Capacity | Central Valley | Fresno | BARTON 1101 | 253571101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253571102_Capacity | Central Valley | Fresno | BARTON 1102 | 253571102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253571104_Capacity | Central Valley | Fresno | BARTON 1104 | 253571104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253571105_Capacity | Central Valley | Fresno | BARTON 1105 | 253571105 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253571106_Capacity | Central Valley | Fresno | BARTON 1106 | 253571106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253571108_Capacity | Central Valley | Fresno | BARTON 1108 | 253571108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2535702_Capacity | Central Valley | Fresno | BARTON BANK 2 | 2535702 | Bank | None | None | None | 91.24% | 0 | 0% | 44.53 | 37.04 | 83.18% | 0 | 0% | 44.53 | 38.88 | 87.31% | 0 | 0% | 44.53 | 39.64 | 89.02% | 0 | 0% | 44.53 | 40.37 | 90.66% | 0 | 0% | 44.53 | 40.63 | 91.24% | 0 | 0%
GNA_253571109_Capacity | Central Valley | Fresno | BARTON 1109 | 253571109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253571110_Capacity | Central Valley | Fresno | BARTON 1110 | 253571110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253571111_Capacity | Central Valley | Fresno | BARTON 1111 | 253571111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253571112_Capacity | Central Valley | Fresno | BARTON 1112 | 253571112 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2535703_Capacity | Central Valley | Fresno | BARTON BANK 3 | 2535703 | Bank | None | None | None | 98.01% | 0 | 0% | 29.7 | 27.65 | 93.1% | 0 | 0% | 29.7 | 28.1 | 94.61% | 0 | 0% | 29.7 | 28.51 | 95.99% | 0 | 0% | 29.7 | 28.96 | 97.51% | 0 | 0% | 29.7 | 29.11 | 98.01% | 0 | 0%
GNA_253571114_Capacity | Central Valley | Fresno | BARTON 1114 | 253571114 | Feeder | None | None | None | 92.83% | 0 | 0% | 10.46 | 9.47 | 90.54% | 0 | 0% | 10.46 | 9.52 | 91.01% | 0 | 0% | 10.46 | 9.58 | 91.59% | 0 | 0% | 10.46 | 9.66 | 92.35% | 0 | 0% | 10.46 | 9.71 | 92.83% | 0 | 0%
GNA_253571115_Capacity | Central Valley | Fresno | BARTON 1115 | 253571115 | Feeder | None | None | None | 97.43% | 0 | 0% | 12.83 | 11.52 | 89.79% | 0 | 0% | 12.83 | 11.85 | 92.36% | 0 | 0% | 12.83 | 12.14 | 94.62% | 0 | 0% | 12.83 | 12.46 | 97.12% | 0 | 0% | 12.83 | 12.5 | 97.43% | 0 | 0%
GNA_253571116_Capacity | Central Valley | Fresno | BARTON 1116 | 253571116 | Feeder | None | None | None | 79.64% | 0 | 0% | 10.46 | 8.23 | 78.68% | 0 | 0% | 10.46 | 8.29 | 79.25% | 0 | 0% | 10.46 | 8.31 | 79.45% | 0 | 0% | 10.46 | 8.32 | 79.54% | 0 | 0% | 10.46 | 8.33 | 79.64% | 0 | 0%
GNA_2539602_Capacity | Central Valley | Fresno | BULLARD BANK 2 | 2539602 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253961105_Capacity | Central Valley | Fresno | BULLARD 1105 | 253961105 | Feeder | None | None | None | 69.77% | 0 | 0% | 9.56 | 6.67 | 69.77% | 0 | 0% | 9.56 | 6.65 | 69.56% | 0 | 0% | 9.56 | 6.65 | 69.56% | 0 | 0% | 9.56 | 6.64 | 69.46% | 0 | 0% | 9.56 | 6.62 | 69.25% | 0 | 0%
GNA_253961106_Capacity | Central Valley | Fresno | BULLARD 1106 | 253961106 | Feeder | None | None | None | 32.34% | 0 | 0% | 10.76 | 3.48 | 32.34% | 0 | 0% | 10.76 | 3.45 | 32.06% | 0 | 0% | 10.76 | 3.44 | 31.97% | 0 | 0% | 10.76 | 3.42 | 31.78% | 0 | 0% | 10.76 | 3.41 | 31.69% | 0 | 0%
GNA_253961107_Capacity | Central Valley | Fresno | BULLARD 1107 | 253961107 | Feeder | None | None | None | 54.18% | 0 | 0% | 9.56 | 5.18 | 54.18% | 0 | 0% | 9.56 | 5.14 | 53.77% | 0 | 0% | 9.56 | 5.1 | 53.35% | 0 | 0% | 9.56 | 5.07 | 53.03% | 0 | 0% | 9.56 | 5.07 | 53.03% | 0 | 0%
GNA_253961108_Capacity | Central Valley | Fresno | BULLARD 1108 | 253961108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253961109_Capacity | Central Valley | Fresno | BULLARD 1109 | 253961109 | Feeder | None | None | None | 53.35% | 0 | 0% | 10.76 | 5.74 | 53.35% | 0 | 0% | 10.76 | 5.7 | 52.97% | 0 | 0% | 10.76 | 5.68 | 52.79% | 0 | 0% | 10.76 | 5.68 | 52.79% | 0 | 0% | 10.76 | 5.68 | 52.79% | 0 | 0%
GNA_253961110_Capacity | Central Valley | Fresno | BULLARD 1110 | 253961110 | Feeder | None | None | None | 76.49% | 0 | 0% | 10.76 | 8.09 | 75.19% | 0 | 0% | 10.76 | 8.11 | 75.37% | 0 | 0% | 10.76 | 8.14 | 75.65% | 0 | 0% | 10.76 | 8.18 | 76.02% | 0 | 0% | 10.76 | 8.23 | 76.49% | 0 | 0%
GNA_2539603_Capacity | Central Valley | Fresno | BULLARD BANK 3 | 2539603 | Bank | None | None | None | 94.48% | 0 | 0% | 44.55 | 42.09 | 94.48% | 0 | 0% | 44.55 | 42.01 | 94.3% | 0 | 0% | 44.55 | 41.87 | 93.98% | 0 | 0% | 44.55 | 41.87 | 93.98% | 0 | 0% | 44.55 | 42.04 | 94.37% | 0 | 0%
GNA_253961101_Capacity | Central Valley | Fresno | BULLARD 1101 | 253961101 | Feeder | None | None | None | 90.75% | 0 | 0% | 11.67 | 10.59 | 90.75% | 0 | 0% | 11.67 | 10.51 | 90.06% | 0 | 0% | 11.67 | 10.39 | 89.03% | 0 | 0% | 11.67 | 10.35 | 88.69% | 0 | 0% | 11.67 | 10.33 | 88.52% | 0 | 0%
GNA_253961102_Capacity | Central Valley | Fresno | BULLARD 1102 | 253961102 | Feeder | None | None | None | 79.4% | 0 | 0% | 10.58 | 8.21 | 77.6% | 0 | 0% | 10.58 | 8.29 | 78.36% | 0 | 0% | 10.58 | 8.36 | 79.02% | 0 | 0% | 10.58 | 8.38 | 79.21% | 0 | 0% | 10.58 | 8.4 | 79.4% | 0 | 0%
GNA_253961103_Capacity | Central Valley | Fresno | BULLARD 1103 | 253961103 | Feeder | None | None | None | 69.19% | 0 | 0% | 10.58 | 7.32 | 69.19% | 0 | 0% | 10.58 | 7.25 | 68.53% | 0 | 0% | 10.58 | 7.19 | 67.96% | 0 | 0% | 10.58 | 7.16 | 67.67% | 0 | 0% | 10.58 | 7.18 | 67.86% | 0 | 0%
GNA_253961104_Capacity | Central Valley | Fresno | BULLARD 1104 | 253961104 | Feeder | None | None | None | 60.59% | 0 | 0% | 10.76 | 6.52 | 60.59% | 0 | 0% | 10.76 | 6.52 | 60.59% | 0 | 0% | 10.76 | 6.49 | 60.32% | 0 | 0% | 10.76 | 6.47 | 60.13% | 0 | 0% | 10.76 | 6.45 | 59.94% | 0 | 0%
GNA_253961113_Capacity | Central Valley | Fresno | BULLARD 1113 | 253961113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2539201_Capacity | Central Valley | Fresno | MANCHESTER BANK 1 | 2539201 | Bank | None | None | None | 66% | 0 | 0% | 44.53 | 29.39 | 66% | 0 | 0% | 44.53 | 29.37 | 65.96% | 0 | 0% | 44.53 | 29.34 | 65.89% | 0 | 0% | 44.53 | 29.31 | 65.82% | 0 | 0% | 44.53 | 29.29 | 65.78% | 0 | 0%
GNA_253921101_Capacity | Central Valley | Fresno | MANCHESTER 1101 | 253921101 | Feeder | None | None | None | 72.09% | 0 | 0% | 12.36 | 8.91 | 72.09% | 0 | 0% | 12.36 | 8.88 | 71.84% | 0 | 0% | 12.36 | 8.82 | 71.36% | 0 | 0% | 12.36 | 8.77 | 70.95% | 0 | 0% | 12.36 | 8.73 | 70.63% | 0 | 0%
GNA_253921103_Capacity | Central Valley | Fresno | MANCHESTER 1103 | 253921103 | Feeder | None | None | None | 91.02% | 0 | 0% | 12.36 | 10.99 | 88.92% | 0 | 0% | 12.36 | 11.04 | 89.32% | 0 | 0% | 12.36 | 11.09 | 89.72% | 0 | 0% | 12.36 | 11.18 | 90.45% | 0 | 0% | 12.36 | 11.25 | 91.02% | 0 | 0%
GNA_253921104_Capacity | Central Valley | Fresno | MANCHESTER 1104 | 253921104 | Feeder | None | None | None | 42.72% | 0 | 0% | 11.33 | 4.84 | 42.72% | 0 | 0% | 11.33 | 4.81 | 42.45% | 0 | 0% | 11.33 | 4.8 | 42.37% | 0 | 0% | 11.33 | 4.76 | 42.01% | 0 | 0% | 11.33 | 4.73 | 41.75% | 0 | 0%
GNA_253921107_Capacity | Central Valley | Fresno | MANCHESTER 1107 | 253921107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2539202_Capacity | Central Valley | Fresno | MANCHESTER BANK 2 | 2539202 | Bank | None | None | None | 93.36% | 0 | 0% | 44.55 | 41.59 | 93.36% | 0 | 0% | 44.55 | 41.45 | 93.04% | 0 | 0% | 44.55 | 41.39 | 92.91% | 0 | 0% | 44.55 | 41.42 | 92.97% | 0 | 0% | 44.55 | 41.5 | 93.15% | 0 | 0%
GNA_253921102_Capacity | Central Valley | Fresno | MANCHESTER 1102 | 253921102 | Feeder | None | None | None | 86.87% | 0 | 0% | 12.19 | 10.59 | 86.87% | 0 | 0% | 12.19 | 10.54 | 86.46% | 0 | 0% | 12.19 | 10.49 | 86.05% | 0 | 0% | 12.19 | 10.45 | 85.73% | 0 | 0% | 12.19 | 10.44 | 85.64% | 0 | 0%
GNA_253921105_Capacity | Central Valley | Fresno | MANCHESTER 1105 | 253921105 | Feeder | None | None | None | 100.2% | 0.02 | 0.1618% | 12.36 | 12.15 | 98.3% | 0 | 0% | 12.36 | 12.17 | 98.46% | 0 | 0% | 12.36 | 12.2 | 98.71% | 0 | 0% | 12.36 | 12.27 | 99.27% | 0 | 0% | 12.36 | 12.38 | 100.2% | 0.02 | 0.1618%
GNA_253921106_Capacity | Central Valley | Fresno | MANCHESTER 1106 | 253921106 | Feeder | None | None | None | 90.15% | 0 | 0% | 10.46 | 9.43 | 90.15% | 0 | 0% | 10.46 | 9.36 | 89.48% | 0 | 0% | 10.46 | 9.33 | 89.2% | 0 | 0% | 10.46 | 9.31 | 89.01% | 0 | 0% | 10.46 | 9.3 | 88.91% | 0 | 0%
GNA_253921108_Capacity | Central Valley | Fresno | MANCHESTER 1108 | 253921108 | Feeder | None | None | None | 88.57% | 0 | 0% | 11.55 | 10.23 | 88.57% | 0 | 0% | 11.55 | 10.14 | 87.79% | 0 | 0% | 11.55 | 10.1 | 87.45% | 0 | 0% | 11.55 | 10.16 | 87.97% | 0 | 0% | 11.55 | 10.22 | 88.48% | 0 | 0%
GNA_2539203_Capacity | Central Valley | Fresno | MANCHESTER BANK 3 | 2539203 | Bank | None | None | None | 96.92% | 0 | 0% | 44.55 | 43.1 | 96.75% | 0 | 0% | 44.55 | 43.14 | 96.84% | 0 | 0% | 44.55 | 43.18 | 96.92% | 0 | 0% | 44.55 | 43.13 | 96.81% | 0 | 0% | 44.55 | 43.12 | 96.79% | 0 | 0%
GNA_253921109_Capacity | Central Valley | Fresno | MANCHESTER 1109 | 253921109 | Feeder | Demand Growth | Capacity | 2025 | 100.5% | 0.06 | 0.5296% | 11.33 | 11.3 | 99.74% | 0 | 0% | 11.33 | 11.34 | 100.1% | 0.01 | 0.08826% | 11.33 | 11.39 | 100.5% | 0.06 | 0.5296% | 11.33 | 11.31 | 99.82% | 0 | 0% | 11.33 | 11.25 | 99.29% | 0 | 0%
GNA_253921110_Capacity | Central Valley | Fresno | MANCHESTER 1110 | 253921110 | Feeder | None | None | None | 99.56% | 0 | 0% | 11.33 | 11.06 | 97.62% | 0 | 0% | 11.33 | 11.12 | 98.15% | 0 | 0% | 11.33 | 11.17 | 98.59% | 0 | 0% | 11.33 | 11.24 | 99.21% | 0 | 0% | 11.33 | 11.28 | 99.56% | 0 | 0%
GNA_253921111_Capacity | Central Valley | Fresno | MANCHESTER 1111 | 253921111 | Feeder | Demand Growth | Capacity | 2023 | 108.6% | 0.93 | 8.643% | 10.76 | 11.69 | 108.6% | 0.93 | 8.643% | 10.76 | 11.63 | 108.1% | 0.87 | 8.086% | 10.76 | 11.57 | 107.5% | 0.81 | 7.528% | 10.76 | 11.5 | 106.9% | 0.74 | 6.877% | 10.76 | 11.49 | 106.8% | 0.73 | 6.784%
GNA_253921112_Capacity | Central Valley | Fresno | MANCHESTER 1112 | 253921112 | Feeder | None | None | None | 89.13% | 0 | 0% | 10.76 | 9.59 | 89.13% | 0 | 0% | 10.76 | 9.52 | 88.48% | 0 | 0% | 10.76 | 9.47 | 88.01% | 0 | 0% | 10.76 | 9.44 | 87.73% | 0 | 0% | 10.76 | 9.47 | 88.01% | 0 | 0%
GNA_2520401_Capacity | Central Valley | Fresno | AIRWAYS BANK 1 | 2520401 | Bank | Demand Growth | Capacity | 2025 | 110.3% | 4.57 | 10.26% | 44.55 | 42.55 | 95.51% | 0 | 0% | 44.55 | 44.67 | 100.3% | 0.12 | 0.2694% | 44.55 | 47.28 | 106.1% | 2.73 | 6.128% | 44.55 | 48.46 | 108.8% | 3.91 | 8.777% | 44.55 | 49.12 | 110.3% | 4.57 | 10.26%
GNA_252041101_Capacity | Central Valley | Fresno | AIRWAYS 1101 | 252041101 | Feeder | None | None | None | 92.72% | 0 | 0% | 11.82 | 9.45 | 79.95% | 0 | 0% | 11.82 | 10.2 | 86.29% | 0 | 0% | 11.82 | 10.73 | 90.78% | 0 | 0% | 11.82 | 10.83 | 91.62% | 0 | 0% | 11.82 | 10.96 | 92.72% | 0 | 0%
GNA_252041102_Capacity | Central Valley | Fresno | AIRWAYS 1102 | 252041102 | Feeder | Demand Growth | Capacity | 2023 | 131.3% | 3.81 | 31.26% | 12.19 | 13.3 | 109.1% | 1.11 | 9.106% | 12.19 | 14.29 | 117.2% | 2.1 | 17.23% | 12.19 | 15.3 | 125.5% | 3.11 | 25.51% | 12.19 | 15.87 | 130.2% | 3.68 | 30.19% | 12.19 | 16 | 131.3% | 3.81 | 31.26%
GNA_252041103_Capacity | Central Valley | Fresno | AIRWAYS 1103 | 252041103 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252041104_Capacity | Central Valley | Fresno | AIRWAYS 1104 | 252041104 | Feeder | None | None | None | 94.23% | 0 | 0% | 12.83 | 11.24 | 87.61% | 0 | 0% | 12.83 | 11.57 | 90.18% | 0 | 0% | 12.83 | 11.68 | 91.04% | 0 | 0% | 12.83 | 11.86 | 92.44% | 0 | 0% | 12.83 | 12.09 | 94.23% | 0 | 0%
GNA_2520402_Capacity | Central Valley | Fresno | AIRWAYS BANK 2 | 2520402 | Bank | Demand Growth | Capacity | 2025 | 104.2% | 1.86 | 4.175% | 44.55 | 40.97 | 91.96% | 0 | 0% | 44.55 | 43.62 | 97.91% | 0 | 0% | 44.55 | 45.44 | 102% | 0.89 | 1.998% | 44.55 | 45.98 | 103.2% | 1.43 | 3.21% | 44.55 | 46.41 | 104.2% | 1.86 | 4.175%
GNA_252041105_Capacity | Central Valley | Fresno | AIRWAYS 1105 | 252041105 | Feeder | None | None | None | 88.16% | 0 | 0% | 11.82 | 9.43 | 79.78% | 0 | 0% | 11.82 | 9.49 | 80.29% | 0 | 0% | 11.82 | 9.92 | 83.93% | 0 | 0% | 11.82 | 10.24 | 86.63% | 0 | 0% | 11.82 | 10.42 | 88.16% | 0 | 0%
GNA_252041106_Capacity | Central Valley | Fresno | AIRWAYS 1106 | 252041106 | Feeder | None | None | None | 91.82% | 0 | 0% | 12.83 | 10.13 | 78.96% | 0 | 0% | 12.83 | 11.43 | 89.09% | 0 | 0% | 12.83 | 11.69 | 91.11% | 0 | 0% | 12.83 | 11.73 | 91.43% | 0 | 0% | 12.83 | 11.78 | 91.82% | 0 | 0%
GNA_252041107_Capacity | Central Valley | Fresno | AIRWAYS 1107 | 252041107 | Feeder | Demand Growth | Capacity | 2024 | 112.9% | 1.65 | 12.86% | 12.83 | 12.09 | 94.23% | 0 | 0% | 12.83 | 13.22 | 103% | 0.39 | 3.04% | 12.83 | 14.27 | 111.2% | 1.44 | 11.22% | 12.83 | 14.36 | 111.9% | 1.53 | 11.93% | 12.83 | 14.48 | 112.9% | 1.65 | 12.86%
GNA_252041108_Capacity | Central Valley | Fresno | AIRWAYS 1108 | 252041108 | Feeder | None | None | None | 82.62% | 0 | 0% | 12.83 | 10.6 | 82.62% | 0 | 0% | 12.83 | 10.56 | 82.31% | 0 | 0% | 12.83 | 10.52 | 82% | 0 | 0% | 12.83 | 10.48 | 81.68% | 0 | 0% | 12.83 | 10.44 | 81.37% | 0 | 0%
GNA_2540801_Capacity | Central Valley | Fresno | CLOVIS BANK 1 | 2540801 | Bank | None | None | None | 89.78% | 0 | 0% | 44.53 | 38.43 | 86.3% | 0 | 0% | 44.53 | 38.64 | 86.77% | 0 | 0% | 44.53 | 39.06 | 87.72% | 0 | 0% | 44.53 | 39.51 | 88.73% | 0 | 0% | 44.53 | 39.98 | 89.78% | 0 | 0%
GNA_254081101_Capacity | Central Valley | Fresno | CLOVIS 1101 | 254081101 | Feeder | None | None | None | 73.42% | 0 | 0% | 12.19 | 8.3 | 68.09% | 0 | 0% | 12.19 | 8.39 | 68.83% | 0 | 0% | 12.19 | 8.64 | 70.88% | 0 | 0% | 12.19 | 8.83 | 72.44% | 0 | 0% | 12.19 | 8.95 | 73.42% | 0 | 0%
GNA_254081102_Capacity | Central Valley | Fresno | CLOVIS 1102 | 254081102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254081103_Capacity | Central Valley | Fresno | CLOVIS 1103 | 254081103 | Feeder | None | None | None | 93.57% | 0 | 0% | 11.97 | 10.93 | 91.31% | 0 | 0% | 11.97 | 10.96 | 91.56% | 0 | 0% | 11.97 | 11.01 | 91.98% | 0 | 0% | 11.97 | 11.09 | 92.65% | 0 | 0% | 11.97 | 11.2 | 93.57% | 0 | 0%
GNA_254081104_Capacity | Central Valley | Fresno | CLOVIS 1104 | 254081104 | Feeder | None | None | None | 90.83% | 0 | 0% | 11.67 | 10.47 | 89.72% | 0 | 0% | 11.67 | 10.46 | 89.63% | 0 | 0% | 11.67 | 10.48 | 89.8% | 0 | 0% | 11.67 | 10.52 | 90.15% | 0 | 0% | 11.67 | 10.6 | 90.83% | 0 | 0%
GNA_2540802_Capacity | Central Valley | Fresno | CLOVIS BANK 2 | 2540802 | Bank | None | None | None | 99.93% | 0 | 0% | 44.55 | 41.96 | 94.19% | 0 | 0% | 44.55 | 42.18 | 94.68% | 0 | 0% | 44.55 | 42.91 | 96.32% | 0 | 0% | 44.55 | 43.44 | 97.51% | 0 | 0% | 44.55 | 44.52 | 99.93% | 0 | 0%
GNA_254081105_Capacity | Central Valley | Fresno | CLOVIS 1105 | 254081105 | Feeder | None | None | None | 79.59% | 0 | 0% | 14.11 | 11.06 | 78.38% | 0 | 0% | 14.11 | 11.11 | 78.74% | 0 | 0% | 14.11 | 11.14 | 78.95% | 0 | 0% | 14.11 | 11.2 | 79.38% | 0 | 0% | 14.11 | 11.23 | 79.59% | 0 | 0%
GNA_254081106_Capacity | Central Valley | Fresno | CLOVIS 1106 | 254081106 | Feeder | None | None | None | 78.82% | 0 | 0% | 11.33 | 8.51 | 75.11% | 0 | 0% | 11.33 | 8.6 | 75.9% | 0 | 0% | 11.33 | 8.71 | 76.88% | 0 | 0% | 11.33 | 8.82 | 77.85% | 0 | 0% | 11.33 | 8.93 | 78.82% | 0 | 0%
GNA_254081107_Capacity | Central Valley | Fresno | CLOVIS 1107 | 254081107 | Feeder | None | None | None | 99.86% | 0 | 0% | 14.11 | 12.65 | 89.65% | 0 | 0% | 14.11 | 12.74 | 90.29% | 0 | 0% | 14.11 | 13.2 | 93.55% | 0 | 0% | 14.11 | 13.4 | 94.97% | 0 | 0% | 14.11 | 14.09 | 99.86% | 0 | 0%
GNA_254081108_Capacity | Central Valley | Fresno | CLOVIS 1108 | 254081108 | Feeder | None | None | None | 98.93% | 0 | 0% | 12.19 | 11.57 | 94.91% | 0 | 0% | 12.19 | 11.66 | 95.65% | 0 | 0% | 12.19 | 11.76 | 96.47% | 0 | 0% | 12.19 | 11.89 | 97.54% | 0 | 0% | 12.19 | 12.06 | 98.93% | 0 | 0%
GNA_2524101_Capacity | Central Valley | Fresno | COPPERMINE BANK 1 | 2524101 | Bank | None | None | None | 92.29% | 0 | 0% | 18.81 | 16.19 | 86.07% | 0 | 0% | 18.81 | 16.39 | 87.13% | 0 | 0% | 18.81 | 16.61 | 88.3% | 0 | 0% | 18.81 | 16.97 | 90.22% | 0 | 0% | 18.81 | 17.36 | 92.29% | 0 | 0%
GNA_252411104_Capacity | Central Valley | Fresno | COPPERMINE 1104 | 252411104 | Feeder | None | None | None | 99.02% | 0 | 0% | 12.19 | 11.42 | 93.68% | 0 | 0% | 12.19 | 11.52 | 94.5% | 0 | 0% | 12.19 | 11.65 | 95.57% | 0 | 0% | 12.19 | 11.85 | 97.21% | 0 | 0% | 12.19 | 12.07 | 99.02% | 0 | 0%
GNA_252411106_Capacity | Central Valley | Fresno | COPPERMINE 1106 | 252411106 | Feeder | None | None | None | 61.96% | 0 | 0% | 11.33 | 6.52 | 57.55% | 0 | 0% | 11.33 | 6.62 | 58.43% | 0 | 0% | 11.33 | 6.71 | 59.22% | 0 | 0% | 11.33 | 6.86 | 60.55% | 0 | 0% | 11.33 | 7.02 | 61.96% | 0 | 0%
GNA_252411112_Capacity | Central Valley | Fresno | COPPERMINE 1112 | 252411112 | Feeder | None | None | None | 29.35% | 0 | 0% | 4.94 | 1.43 | 28.95% | 0 | 0% | 4.94 | 1.44 | 29.15% | 0 | 0% | 4.94 | 1.44 | 29.15% | 0 | 0% | 4.94 | 1.44 | 29.15% | 0 | 0% | 4.94 | 1.45 | 29.35% | 0 | 0%
GNA_2521601_Capacity | Central Valley | Fresno | COALINGA NO 1 BANK 1 | 2521601 | Bank | None | None | None | 99.31% | 0 | 0% | 15.84 | 15.73 | 99.31% | 0 | 0% | 15.84 | 15.7 | 99.12% | 0 | 0% | 15.84 | 15.67 | 98.93% | 0 | 0% | 15.84 | 15.66 | 98.86% | 0 | 0% | 15.84 | 15.63 | 98.67% | 0 | 0%
GNA_252161108_Capacity | Central Valley | Fresno | COALINGA NO 1 1108 | 252161108 | Feeder | None | None | None | 93.09% | 0 | 0% | 8.83 | 8.22 | 93.09% | 0 | 0% | 8.83 | 8.2 | 92.87% | 0 | 0% | 8.83 | 8.18 | 92.64% | 0 | 0% | 8.83 | 8.18 | 92.64% | 0 | 0% | 8.83 | 8.16 | 92.41% | 0 | 0%
GNA_252161109_Capacity | Central Valley | Fresno | COALINGA NO 1 1109 | 252161109 | Feeder | None | None | None | 94.96% | 0 | 0% | 8.13 | 7.72 | 94.96% | 0 | 0% | 8.13 | 7.72 | 94.96% | 0 | 0% | 8.13 | 7.71 | 94.83% | 0 | 0% | 8.13 | 7.71 | 94.83% | 0 | 0% | 8.13 | 7.7 | 94.71% | 0 | 0%
GNA_2521602_Capacity | Central Valley | Fresno | COALINGA NO 1 BANK 2 | 2521602 | Bank | Demand Growth | Capacity | 2025 | 153.6% | 5.57 | 53.56% | 10.4 | 9.58 | 92.12% | 0 | 0% | 10.4 | 9.57 | 92.02% | 0 | 0% | 10.4 | 15.96 | 153.5% | 5.56 | 53.46% | 10.4 | 15.97 | 153.6% | 5.57 | 53.56% | 10.4 | 15.96 | 153.5% | 5.56 | 53.46%
GNA_252161106_Capacity | Central Valley | Fresno | COALINGA NO 1 1106 | 252161106 | Feeder | None | None | None | 63.53% | 0 | 0% | 8.83 | 5.61 | 63.53% | 0 | 0% | 8.83 | 5.6 | 63.42% | 0 | 0% | 8.83 | 5.59 | 63.31% | 0 | 0% | 8.83 | 5.6 | 63.42% | 0 | 0% | 8.83 | 5.58 | 63.19% | 0 | 0%
GNA_252161107_Capacity | Central Valley | Fresno | COALINGA NO 1 1107 | 252161107 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2523801_Capacity | Central Valley | Fresno | COALINGA NO 2 BANK 1 | 2523801 | Bank | Demand Growth | Capacity | 2024 | 127.7% | 5.43 | 27.75% | 19.57 | 15.56 | 79.51% | 0 | 0% | 19.57 | 21.63 | 110.5% | 2.06 | 10.53% | 19.57 | 22.85 | 116.8% | 3.28 | 16.76% | 19.57 | 22.84 | 116.7% | 3.27 | 16.71% | 19.57 | 25 | 127.7% | 5.43 | 27.75%
GNA_252381105_Capacity | Central Valley | Fresno | COALINGA NO 2 1105 | 252381105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252381106_Capacity | Central Valley | Fresno | COALINGA NO 2 1106 | 252381106 | Feeder | Demand Growth | Capacity | 2027 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252381107_Capacity | Central Valley | Fresno | COALINGA NO 2 1107 | 252381107 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2540001_Capacity | Central Valley | Fresno | ALPAUGH BANK 1 | 2540001 | Bank | None | None | None | 40.34% | 0 | 0% | 29.7 | 11.98 | 40.34% | 0 | 0% | 29.7 | 11.97 | 40.3% | 0 | 0% | 29.7 | 11.97 | 40.3% | 0 | 0% | 29.7 | 11.96 | 40.27% | 0 | 0% | 29.7 | 11.95 | 40.24% | 0 | 0%
GNA_254001103_Capacity | Central Valley | Fresno | ALPAUGH 1103 | 254001103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254001104_Capacity | Central Valley | Fresno | ALPAUGH 1104 | 254001104 | Feeder | None | None | None | 67.02% | 0 | 0% | 10.46 | 7.01 | 67.02% | 0 | 0% | 10.46 | 7 | 66.92% | 0 | 0% | 10.46 | 7 | 66.92% | 0 | 0% | 10.46 | 6.99 | 66.83% | 0 | 0% | 10.46 | 6.98 | 66.73% | 0 | 0%
GNA_2540002_Capacity | Central Valley | Fresno | ALPAUGH BANK 2 | 2540002 | Bank | None | None | None | 49.33% | 0 | 0% | 10.4 | 5.13 | 49.33% | 0 | 0% | 10.4 | 5.07 | 48.75% | 0 | 0% | 10.4 | 4.98 | 47.88% | 0 | 0% | 10.4 | 4.92 | 47.31% | 0 | 0% | 10.4 | 4.88 | 46.92% | 0 | 0%
GNA_254001106_Capacity | Central Valley | Fresno | ALPAUGH 1106 | 254001106 | Feeder | None | None | None | 50% | 0 | 0% | 10.28 | 5.14 | 50% | 0 | 0% | 10.28 | 5.09 | 49.51% | 0 | 0% | 10.28 | 4.99 | 48.54% | 0 | 0% | 10.28 | 4.94 | 48.05% | 0 | 0% | 10.28 | 4.9 | 47.67% | 0 | 0%
GNA_2521501_Capacity | Central Valley | Fresno | ANGIOLA BANK 1 | 2521501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252151102_Capacity | Central Valley | Fresno | ANGIOLA 1102 | 252151102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252151103_Capacity | Central Valley | Fresno | ANGIOLA 1103 | 252151103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252151104_Capacity | Central Valley | Fresno | ANGIOLA 1104 | 252151104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2521703_Capacity | Central Valley | Fresno | CORCORAN BANK 3 | 2521703 | Bank | Demand Growth | Capacity | 2023 | 117.6% | 5.23 | 17.61% | 29.7 | 34.52 | 116.2% | 4.82 | 16.23% | 29.7 | 34.59 | 116.5% | 4.89 | 16.46% | 29.7 | 34.68 | 116.8% | 4.98 | 16.77% | 29.7 | 34.79 | 117.1% | 5.09 | 17.14% | 29.7 | 34.93 | 117.6% | 5.23 | 17.61%
GNA_252171112_Capacity | Central Valley | Fresno | CORCORAN 1112 | 252171112 | Feeder | Demand Growth | Capacity | 2023 | 118.9% | 2.21 | 18.94% | 11.67 | 13.45 | 115.3% | 1.78 | 15.25% | 11.67 | 13.53 | 115.9% | 1.86 | 15.94% | 11.67 | 13.64 | 116.9% | 1.97 | 16.88% | 11.67 | 13.76 | 117.9% | 2.09 | 17.91% | 11.67 | 13.88 | 118.9% | 2.21 | 18.94%
GNA_252171116_Capacity | Central Valley | Fresno | CORCORAN 1116 | 252171116 | Feeder | Demand Growth | Capacity | 2023 | 107.1% | 0.87 | 7.137% | 12.19 | 13.04 | 107% | 0.85 | 6.973% | 12.19 | 13.04 | 107% | 0.85 | 6.973% | 12.19 | 13.04 | 107% | 0.85 | 6.973% | 12.19 | 13.04 | 107% | 0.85 | 6.973% | 12.19 | 13.06 | 107.1% | 0.87 | 7.137%
GNA_252171118_Capacity | Central Valley | Fresno | CORCORAN 1118 | 252171118 | Feeder | None | None | None | 86.13% | 0 | 0% | 12.83 | 11.05 | 86.13% | 0 | 0% | 12.83 | 11.03 | 85.97% | 0 | 0% | 12.83 | 11.03 | 85.97% | 0 | 0% | 12.83 | 11.02 | 85.89% | 0 | 0% | 12.83 | 11.02 | 85.89% | 0 | 0%
GNA_2521704_Capacity | Central Valley | Fresno | CORCORAN BANK 4 | 2521704 | Bank | None | None | None | 92.12% | 0 | 0% | 29.7 | 26.8 | 90.24% | 0 | 0% | 29.7 | 26.86 | 90.44% | 0 | 0% | 29.7 | 26.96 | 90.77% | 0 | 0% | 29.7 | 27.13 | 91.35% | 0 | 0% | 29.7 | 27.36 | 92.12% | 0 | 0%
GNA_252171104_Capacity | Central Valley | Fresno | CORCORAN 1104 | 252171104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252171106_Capacity | Central Valley | Fresno | CORCORAN 1106 | 252171106 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252171108_Capacity | Central Valley | Fresno | CORCORAN 1108 | 252171108 | Feeder | Demand Growth | Capacity | 2023 | 104.7% | 0.55 | 4.713% | 11.67 | 11.92 | 102.1% | 0.25 | 2.142% | 11.67 | 11.96 | 102.5% | 0.29 | 2.485% | 11.67 | 12.04 | 103.2% | 0.37 | 3.171% | 11.67 | 12.1 | 103.7% | 0.43 | 3.685% | 11.67 | 12.22 | 104.7% | 0.55 | 4.713%
GNA_2540601_Capacity | Central Valley | Fresno | DUNLAP BANK 1 | 2540601 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254061102_Capacity | Central Valley | Fresno | DUNLAP 1102 | 254061102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254061103_Capacity | Central Valley | Fresno | DUNLAP 1103 | 254061103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2546001_Capacity | Central Valley | Fresno | SAND CREEK BANK 1 | 2546001 | Bank | None | None | None | 65.53% | 0 | 0% | 7.02 | 4.6 | 65.53% | 0 | 0% | 7.02 | 4.59 | 65.38% | 0 | 0% | 7.02 | 4.59 | 65.38% | 0 | 0% | 7.02 | 4.59 | 65.38% | 0 | 0% | 7.02 | 4.58 | 65.24% | 0 | 0%
GNA_254601103_Capacity | Central Valley | Fresno | SAND CREEK 1103 | 254601103 | Feeder | None | None | None | 82.47% | 0 | 0% | 5.99 | 4.94 | 82.47% | 0 | 0% | 5.99 | 4.93 | 82.3% | 0 | 0% | 5.99 | 4.93 | 82.3% | 0 | 0% | 5.99 | 4.93 | 82.3% | 0 | 0% | 5.99 | 4.92 | 82.14% | 0 | 0%
GNA_2545501_Capacity | Central Valley | Fresno | FIGARDEN BANK 1 | 2545501 | Bank | Demand Growth | Capacity | 2025 | 104.6% | 2.99 | 4.646% | 64.35 | 63.39 | 98.51% | 0 | 0% | 64.35 | 64.42 | 100.1% | 0.07 | 0.1088% | 64.35 | 64.72 | 100.6% | 0.37 | 0.575% | 64.35 | 65.74 | 102.2% | 1.39 | 2.16% | 64.35 | 67.34 | 104.6% | 2.99 | 4.646%
GNA_254552102_Capacity | Central Valley | Fresno | FIGARDEN 2102 | 254552102 | Feeder | Demand Growth | Capacity | 2023 | 119.4% | 4.11 | 19.37% | 21.22 | 22.66 | 106.8% | 1.44 | 6.786% | 21.22 | 23.63 | 111.4% | 2.41 | 11.36% | 21.22 | 23.86 | 112.4% | 2.64 | 12.44% | 21.22 | 24.45 | 115.2% | 3.23 | 15.22% | 21.22 | 25.33 | 119.4% | 4.11 | 19.37%
GNA_254552103_Capacity | Central Valley | Fresno | FIGARDEN 2103 | 254552103 | Feeder | None | None | None | 67.31% | 0 | 0% | 18.63 | 11.75 | 63.07% | 0 | 0% | 18.63 | 11.87 | 63.71% | 0 | 0% | 18.63 | 12.08 | 64.84% | 0 | 0% | 18.63 | 12.34 | 66.24% | 0 | 0% | 18.63 | 12.54 | 67.31% | 0 | 0%
GNA_254552104_Capacity | Central Valley | Fresno | FIGARDEN 2104 | 254552104 | Feeder | None | None | None | 58.43% | 0 | 0% | 19.63 | 10.79 | 54.97% | 0 | 0% | 19.63 | 11.01 | 56.09% | 0 | 0% | 19.63 | 11.11 | 56.6% | 0 | 0% | 19.63 | 11.27 | 57.41% | 0 | 0% | 19.63 | 11.47 | 58.43% | 0 | 0%
GNA_254552105_Capacity | Central Valley | Fresno | FIGARDEN 2105 | 254552105 | Feeder | None | None | None | 77.24% | 0 | 0% | 18.63 | 14.39 | 77.24% | 0 | 0% | 18.63 | 14.3 | 76.76% | 0 | 0% | 18.63 | 14.26 | 76.54% | 0 | 0% | 18.63 | 14.3 | 76.76% | 0 | 0% | 18.63 | 14.36 | 77.08% | 0 | 0%
GNA_2545502_Capacity | Central Valley | Fresno | FIGARDEN BANK 2 | 2545502 | Bank | Demand Growth | Capacity | 2027 | 100.8% | 0.49 | 0.7615% | 64.35 | 59.44 | 92.37% | 0 | 0% | 64.35 | 64.23 | 99.81% | 0 | 0% | 64.35 | 64.13 | 99.66% | 0 | 0% | 64.35 | 64.37 | 100% | 0.02 | 0.03108% | 64.35 | 64.84 | 100.8% | 0.49 | 0.7615%
GNA_254552107_Capacity | Central Valley | Fresno | FIGARDEN 2107 | 254552107 | Feeder | None | None | None | 90.39% | 0 | 0% | 18.63 | 16.58 | 89% | 0 | 0% | 18.63 | 16.56 | 88.89% | 0 | 0% | 18.63 | 16.54 | 88.78% | 0 | 0% | 18.63 | 16.65 | 89.37% | 0 | 0% | 18.63 | 16.84 | 90.39% | 0 | 0%
GNA_254552108_Capacity | Central Valley | Fresno | FIGARDEN 2108 | 254552108 | Feeder | None | None | None | 86.42% | 0 | 0% | 18.63 | 14.59 | 78.31% | 0 | 0% | 18.63 | 16.1 | 86.42% | 0 | 0% | 18.63 | 16.03 | 86.04% | 0 | 0% | 18.63 | 16.02 | 85.99% | 0 | 0% | 18.63 | 16.05 | 86.15% | 0 | 0%
GNA_254552109_Capacity | Central Valley | Fresno | FIGARDEN 2109 | 254552109 | Feeder | None | None | None | 51.76% | 0 | 0% | 19.63 | 7.95 | 40.5% | 0 | 0% | 19.63 | 9.92 | 50.53% | 0 | 0% | 19.63 | 9.98 | 50.84% | 0 | 0% | 19.63 | 10.05 | 51.2% | 0 | 0% | 19.63 | 10.16 | 51.76% | 0 | 0%
GNA_254552110_Capacity | Central Valley | Fresno | FIGARDEN 2110 | 254552110 | Feeder | None | None | None | 96.12% | 0 | 0% | 21.11 | 18.76 | 88.87% | 0 | 0% | 21.11 | 20.12 | 95.31% | 0 | 0% | 21.11 | 20.02 | 94.84% | 0 | 0% | 21.11 | 20.1 | 95.22% | 0 | 0% | 21.11 | 20.29 | 96.12% | 0 | 0%
GNA_2545503_Capacity | Central Valley | Fresno | FIGARDEN BANK 3 | 2545503 | Bank | None | None | None | 80% | 0 | 0% | 64.35 | 51.48 | 80% | 0 | 0% | 64.35 | 49.7 | 77.23% | 0 | 0% | 64.35 | 49.86 | 77.48% | 0 | 0% | 64.35 | 50.2 | 78.01% | 0 | 0% | 64.35 | 50.56 | 78.57% | 0 | 0%
GNA_254552111_Capacity | Central Valley | Fresno | FIGARDEN 2111 | 254552111 | Feeder | None | None | None | 82.42% | 0 | 0% | 21.22 | 17.49 | 82.42% | 0 | 0% | 21.22 | 17.47 | 82.33% | 0 | 0% | 21.22 | 17.43 | 82.14% | 0 | 0% | 21.22 | 17.41 | 82.05% | 0 | 0% | 21.22 | 17.29 | 81.48% | 0 | 0%
GNA_254552112_Capacity | Central Valley | Fresno | FIGARDEN 2112 | 254552112 | Feeder | None | None | None | 78.8% | 0 | 0% | 22.22 | 17.51 | 78.8% | 0 | 0% | 22.22 | 15.75 | 70.88% | 0 | 0% | 22.22 | 16 | 72.01% | 0 | 0% | 22.22 | 16.25 | 73.13% | 0 | 0% | 22.22 | 16.46 | 74.08% | 0 | 0%
GNA_254552113_Capacity | Central Valley | Fresno | FIGARDEN 2113 | 254552113 | Feeder | None | None | None | 79.77% | 0 | 0% | 21.11 | 16.27 | 77.07% | 0 | 0% | 21.11 | 16.33 | 77.36% | 0 | 0% | 21.11 | 16.36 | 77.5% | 0 | 0% | 21.11 | 16.59 | 78.59% | 0 | 0% | 21.11 | 16.84 | 79.77% | 0 | 0%
GNA_2534401_Capacity | Central Valley | Fresno | CALFLAX BANK 1 | 2534401 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253441101_Capacity | Central Valley | Fresno | CALFLAX 1101 | 253441101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253441102_Capacity | Central Valley | Fresno | CALFLAX 1102 | 253441102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253441103_Capacity | Central Valley | Fresno | CALFLAX 1103 | 253441103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253441104_Capacity | Central Valley | Fresno | CALFLAX 1104 | 253441104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2535901_Capacity | Central Valley | Fresno | CANTUA BANK 1 | 2535901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253591101_Capacity | Central Valley | Fresno | CANTUA 1101 | 253591101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253591102_Capacity | Central Valley | Fresno | CANTUA 1102 | 253591102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253591103_Capacity | Central Valley | Fresno | CANTUA 1103 | 253591103 | Feeder | None | None | None | 80.16% | 0 | 0% | 8.92 | 7.15 | 80.16% | 0 | 0% | 8.92 | 7.14 | 80.04% | 0 | 0% | 8.92 | 7.14 | 80.04% | 0 | 0% | 8.92 | 7.14 | 80.04% | 0 | 0% | 8.92 | 7.13 | 79.93% | 0 | 0%
GNA_253591105_Capacity | Central Valley | Fresno | CANTUA 1105 | 253591105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2539303_Capacity | Central Valley | Fresno | GATES BANK 3 | 2539303 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253931101_Capacity | Central Valley | Fresno | GATES 1101 | 253931101 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253931102_Capacity | Central Valley | Fresno | GATES 1102 | 253931102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2539304_Capacity | Central Valley | Fresno | GATES BANK 4 | 2539304 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253931104_Capacity | Central Valley | Fresno | GATES 1104 | 253931104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253931105_Capacity | Central Valley | Fresno | GATES 1105 | 253931105 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253931106_Capacity | Central Valley | Fresno | GATES 1106 | 253931106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253931110_Capacity | Central Valley | Fresno | GATES 1110 | 253931110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2531501_Capacity | Central Valley | Fresno | GIFFEN BANK 1 | 2531501 | Bank | Demand Growth | Capacity | 2023 | 160% | 10.57 | 59.95% | 17.63 | 20.86 | 118.3% | 3.23 | 18.32% | 17.63 | 24.43 | 138.6% | 6.8 | 38.57% | 17.63 | 28.2 | 160% | 10.57 | 59.95% | 17.63 | 28.2 | 160% | 10.57 | 59.95% | 17.63 | 28.19 | 159.9% | 10.56 | 59.9%
GNA_253151102_Capacity | Central Valley | Fresno | GIFFEN 1102 | 253151102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253151103_Capacity | Central Valley | Fresno | GIFFEN 1103 | 253151103 | Feeder | Demand Growth | Capacity | 2023 | 101.7% | 0.21 | 1.723% | 12.19 | 12.4 | 101.7% | 0.21 | 1.723% | 12.19 | 12.4 | 101.7% | 0.21 | 1.723% | 12.19 | 12.39 | 101.6% | 0.2 | 1.641% | 12.19 | 12.39 | 101.6% | 0.2 | 1.641% | 12.19 | 12.38 | 101.6% | 0.19 | 1.559%
GNA_2531601_Capacity | Central Valley | Fresno | HURON BANK 1 | 2531601 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253161106_Capacity | Central Valley | Fresno | HURON 1106 | 253161106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253161108_Capacity | Central Valley | Fresno | HURON 1108 | 253161108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253161112_Capacity | Central Valley | Fresno | HURON 1112 | 253161112 | Feeder | None | None | None | 70.63% | 0 | 0% | 10.69 | 7.16 | 66.98% | 0 | 0% | 10.69 | 7.26 | 67.91% | 0 | 0% | 10.69 | 7.36 | 68.85% | 0 | 0% | 10.69 | 7.46 | 69.78% | 0 | 0% | 10.69 | 7.55 | 70.63% | 0 | 0%
GNA_253161116_Capacity | Central Valley | Fresno | HURON 1116 | 253161116 | Feeder | None | None | None | 38.26% | 0 | 0% | 10.69 | 4.09 | 38.26% | 0 | 0% | 10.69 | 4.09 | 38.26% | 0 | 0% | 10.69 | 4.09 | 38.26% | 0 | 0% | 10.69 | 4.09 | 38.26% | 0 | 0% | 10.69 | 4.08 | 38.17% | 0 | 0%
GNA_2528902_Capacity | Central Valley | Fresno | SCHINDLER BANK 2 | 2528902 | Bank | None | None | None | 82.18% | 0 | 0% | 29.69 | 24.4 | 82.18% | 0 | 0% | 29.69 | 24.37 | 82.08% | 0 | 0% | 29.69 | 24.36 | 82.05% | 0 | 0% | 29.69 | 24.35 | 82.01% | 0 | 0% | 29.69 | 24.33 | 81.95% | 0 | 0%
GNA_252891104_Capacity | Central Valley | Fresno | SCHINDLER 1104 | 252891104 | Feeder | None | None | None | 0% | 0 | 0% | 9.88 | 0 | 0% | 0 | 0% | 9.88 | 0 | 0% | 0 | 0% | 9.88 | 0 | 0% | 0 | 0% | 9.88 | 0 | 0% | 0 | 0% | 9.88 | 0 | 0% | 0 | 0%
GNA_252891105_Capacity | Central Valley | Fresno | SCHINDLER 1105 | 252891105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252891114_Capacity | Central Valley | Fresno | SCHINDLER 1114 | 252891114 | Feeder | Demand Growth | Capacity | 2023 | 107.4% | 0.9 | 7.383% | 12.19 | 13.09 | 107.4% | 0.9 | 7.383% | 12.19 | 13.07 | 107.2% | 0.88 | 7.219% | 12.19 | 13.06 | 107.1% | 0.87 | 7.137% | 12.19 | 13.05 | 107.1% | 0.86 | 7.055% | 12.19 | 13.04 | 107% | 0.85 | 6.973%
GNA_252891116_Capacity | Central Valley | Fresno | SCHINDLER 1116 | 252891116 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2528903_Capacity | Central Valley | Fresno | SCHINDLER BANK 3 | 2528903 | Bank | Demand Growth | Capacity | 2023 | 101.1% | 0.34 | 1.145% | 29.69 | 30.03 | 101.1% | 0.34 | 1.145% | 29.69 | 30 | 101% | 0.31 | 1.044% | 29.69 | 29.99 | 101% | 0.3 | 1.01% | 29.69 | 29.99 | 101% | 0.3 | 1.01% | 29.69 | 29.96 | 100.9% | 0.27 | 0.9094%
GNA_252891110_Capacity | Central Valley | Fresno | SCHINDLER 1110 | 252891110 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252891111_Capacity | Central Valley | Fresno | SCHINDLER 1111 | 252891111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252891112_Capacity | Central Valley | Fresno | SCHINDLER 1112 | 252891112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2526601_Capacity | Central Valley | Fresno | GUERNSEY BANK 1 | 2526601 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252661102_Capacity | Central Valley | Fresno | GUERNSEY 1102 | 252661102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252661104_Capacity | Central Valley | Fresno | GUERNSEY 1104 | 252661104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252661106_Capacity | Central Valley | Fresno | GUERNSEY 1106 | 252661106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2526602_Capacity | Central Valley | Fresno | GUERNSEY BANK 2 | 2526602 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252661101_Capacity | Central Valley | Fresno | GUERNSEY 1101 | 252661101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252661103_Capacity | Central Valley | Fresno | GUERNSEY 1103 | 252661103 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2526801_Capacity | Central Valley | Fresno | HENRIETTA BANK 1 | 2526801 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252681104_Capacity | Central Valley | Fresno | HENRIETTA 1104 | 252681104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252681108_Capacity | Central Valley | Fresno | HENRIETTA 1108 | 252681108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2526805_Capacity | Central Valley | Fresno | HENRIETTA BANK 5 | 2526805 | Bank | Demand Growth | Capacity | 2023 | 111.2% | 1.77 | 11.17% | 15.84 | 17.61 | 111.2% | 1.77 | 11.17% | 15.84 | 17.59 | 111% | 1.75 | 11.05% | 15.84 | 17.58 | 111% | 1.74 | 10.98% | 15.84 | 17.57 | 110.9% | 1.73 | 10.92% | 15.84 | 17.56 | 110.9% | 1.72 | 10.86%
GNA_252681106_Capacity | Central Valley | Fresno | HENRIETTA 1106 | 252681106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252681110_Capacity | Central Valley | Fresno | HENRIETTA 1110 | 252681110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2547701_Capacity | Central Valley | Fresno | JACOBS CORNER BANK 1 | 2547701 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254771101_Capacity | Central Valley | Fresno | JACOBS CORNER 1101 | 254771101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2547702_Capacity | Central Valley | Fresno | JACOBS CORNER BANK 2 | 2547702 | Bank | None | None | None | 79.73% | 0 | 0% | 15.84 | 8.97 | 56.63% | 0 | 0% | 15.84 | 12.63 | 79.73% | 0 | 0% | 15.84 | 12.63 | 79.73% | 0 | 0% | 15.84 | 12.62 | 79.67% | 0 | 0% | 15.84 | 12.62 | 79.67% | 0 | 0%
GNA_254771102_Capacity | Central Valley | Fresno | JACOBS CORNER 1102 | 254771102 | Feeder | None | None | None | 83.8% | 0 | 0% | 15.12 | 9.02 | 59.66% | 0 | 0% | 15.12 | 12.67 | 83.8% | 0 | 0% | 15.12 | 12.67 | 83.8% | 0 | 0% | 15.12 | 12.67 | 83.8% | 0 | 0% | 15.12 | 12.67 | 83.8% | 0 | 0%
GNA_2541802_Capacity | Central Valley | Fresno | RESERVE OIL BANK 2 | 2541802 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254181101_Capacity | Central Valley | Fresno | RESERVE OIL 1101 | 254181101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2522101_Capacity | Central Valley | Fresno | BIOLA BANK 1 | 2522101 | Bank | Demand Growth | Capacity | 2023 | 104.6% | 0.86 | 4.572% | 18.81 | 19.3 | 102.6% | 0.49 | 2.605% | 18.81 | 19.61 | 104.3% | 0.8 | 4.253% | 18.81 | 19.59 | 104.1% | 0.78 | 4.147% | 18.81 | 19.61 | 104.3% | 0.8 | 4.253% | 18.81 | 19.67 | 104.6% | 0.86 | 4.572%
GNA_252211101_Capacity | Central Valley | Fresno | BIOLA 1101 | 252211101 | Feeder | None | None | None | 73.55% | 0 | 0% | 8.13 | 5.96 | 73.31% | 0 | 0% | 8.13 | 5.95 | 73.19% | 0 | 0% | 8.13 | 5.95 | 73.19% | 0 | 0% | 8.13 | 5.96 | 73.31% | 0 | 0% | 8.13 | 5.98 | 73.55% | 0 | 0%
GNA_252211102_Capacity | Central Valley | Fresno | BIOLA 1102 | 252211102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252211103_Capacity | Central Valley | Fresno | BIOLA 1103 | 252211103 | Feeder | None | None | None | 84.85% | 0 | 0% | 10.69 | 8.69 | 81.29% | 0 | 0% | 10.69 | 9.02 | 84.38% | 0 | 0% | 10.69 | 9.02 | 84.38% | 0 | 0% | 10.69 | 9.03 | 84.47% | 0 | 0% | 10.69 | 9.07 | 84.85% | 0 | 0%
GNA_252211104_Capacity | Central Valley | Fresno | BIOLA 1104 | 252211104 | Feeder | None | None | None | 32.46% | 0 | 0% | 10.69 | 3.47 | 32.46% | 0 | 0% | 10.69 | 3.46 | 32.37% | 0 | 0% | 10.69 | 3.46 | 32.37% | 0 | 0% | 10.69 | 3.45 | 32.27% | 0 | 0% | 10.69 | 3.46 | 32.37% | 0 | 0%
GNA_2527001_Capacity | Central Valley | Fresno | KEARNEY BANK 1 | 2527001 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252701104_Capacity | Central Valley | Fresno | KEARNEY 1104 | 252701104 | Feeder | None | None | None | 58.93% | 0 | 0% | 10.69 | 6.3 | 58.93% | 0 | 0% | 10.69 | 6.28 | 58.75% | 0 | 0% | 10.69 | 6.27 | 58.65% | 0 | 0% | 10.69 | 6.27 | 58.65% | 0 | 0% | 10.69 | 6.3 | 58.93% | 0 | 0%
GNA_252701106_Capacity | Central Valley | Fresno | KEARNEY 1106 | 252701106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252701110_Capacity | Central Valley | Fresno | KEARNEY 1110 | 252701110 | Feeder | None | None | None | 76.7% | 0 | 0% | 12.83 | 9.43 | 73.5% | 0 | 0% | 12.83 | 9.5 | 74.05% | 0 | 0% | 12.83 | 9.6 | 74.82% | 0 | 0% | 12.83 | 9.69 | 75.53% | 0 | 0% | 12.83 | 9.84 | 76.7% | 0 | 0%
GNA_2527003_Capacity | Central Valley | Fresno | KEARNEY BANK 3 | 2527003 | Bank | Demand Growth | Capacity | 2023 | 108.7% | 0.64 | 8.672% | 7.38 | 7.51 | 101.8% | 0.13 | 1.762% | 7.38 | 7.6 | 103% | 0.22 | 2.981% | 7.38 | 7.72 | 104.6% | 0.34 | 4.607% | 7.38 | 7.87 | 106.6% | 0.49 | 6.64% | 7.38 | 8.02 | 108.7% | 0.64 | 8.672%
GNA_252701114_Capacity | Central Valley | Fresno | KEARNEY 1114 | 252701114 | Feeder | None | None | None | 76.39% | 0 | 0% | 10.46 | 7.5 | 71.7% | 0 | 0% | 10.46 | 7.59 | 72.56% | 0 | 0% | 10.46 | 7.7 | 73.61% | 0 | 0% | 10.46 | 7.84 | 74.95% | 0 | 0% | 10.46 | 7.99 | 76.39% | 0 | 0%
GNA_2527101_Capacity | Central Valley | Fresno | KERMAN BANK 1 | 2527101 | Bank | None | None | None | 88.82% | 0 | 0% | 29.7 | 24.75 | 83.33% | 0 | 0% | 29.7 | 26.09 | 87.85% | 0 | 0% | 29.7 | 26.16 | 88.08% | 0 | 0% | 29.7 | 26.27 | 88.45% | 0 | 0% | 29.7 | 26.38 | 88.82% | 0 | 0%
GNA_252711104_Capacity | Central Valley | Fresno | KERMAN 1104 | 252711104 | Feeder | None | None | None | 91.39% | 0 | 0% | 10.69 | 8.92 | 83.44% | 0 | 0% | 10.69 | 9.77 | 91.39% | 0 | 0% | 10.69 | 9.76 | 91.3% | 0 | 0% | 10.69 | 9.76 | 91.3% | 0 | 0% | 10.69 | 9.75 | 91.21% | 0 | 0%
GNA_252711106_Capacity | Central Valley | Fresno | KERMAN 1106 | 252711106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252711108_Capacity | Central Valley | Fresno | KERMAN 1108 | 252711108 | Feeder | None | None | None | 70.3% | 0 | 0% | 12.19 | 7.77 | 63.74% | 0 | 0% | 12.19 | 8.27 | 67.84% | 0 | 0% | 12.19 | 8.35 | 68.5% | 0 | 0% | 12.19 | 8.45 | 69.32% | 0 | 0% | 12.19 | 8.57 | 70.3% | 0 | 0%
GNA_2527102_Capacity | Central Valley | Fresno | KERMAN BANK 2 | 2527102 | Bank | Demand Growth | Capacity | 2023 | 118.8% | 5.59 | 18.82% | 29.7 | 33.04 | 111.2% | 3.34 | 11.25% | 29.7 | 33.14 | 111.6% | 3.44 | 11.58% | 29.7 | 34.67 | 116.7% | 4.97 | 16.73% | 29.7 | 34.95 | 117.7% | 5.25 | 17.68% | 29.7 | 35.29 | 118.8% | 5.59 | 18.82%
GNA_252711101_Capacity | Central Valley | Fresno | KERMAN 1101 | 252711101 | Feeder | Demand Growth | Capacity | 2025 | 107.6% | 0.8 | 7.648% | 10.46 | 9.9 | 94.65% | 0 | 0% | 10.46 | 9.85 | 94.17% | 0 | 0% | 10.46 | 11.24 | 107.5% | 0.78 | 7.457% | 10.46 | 11.24 | 107.5% | 0.78 | 7.457% | 10.46 | 11.26 | 107.6% | 0.8 | 7.648%
GNA_252711102_Capacity | Central Valley | Fresno | KERMAN 1102 | 252711102 | Feeder | None | None | None | 96.65% | 0 | 0% | 12.83 | 11.91 | 92.83% | 0 | 0% | 12.83 | 11.99 | 93.45% | 0 | 0% | 12.83 | 12.08 | 94.15% | 0 | 0% | 12.83 | 12.23 | 95.32% | 0 | 0% | 12.83 | 12.4 | 96.65% | 0 | 0%
GNA_252711103_Capacity | Central Valley | Fresno | KERMAN 1103 | 252711103 | Feeder | Demand Growth | Capacity | 2023 | 112.7% | 1.48 | 12.68% | 11.67 | 12.78 | 109.5% | 1.11 | 9.512% | 11.67 | 12.85 | 110.1% | 1.18 | 10.11% | 11.67 | 12.89 | 110.5% | 1.22 | 10.45% | 11.67 | 13.01 | 111.5% | 1.34 | 11.48% | 11.67 | 13.15 | 112.7% | 1.48 | 12.68%
GNA_2550001_Capacity | Central Valley | Fresno | AVENAL BANK 1 | 2550001 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_255002101_Capacity | Central Valley | Fresno | AVENAL 2101 | 255002101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2534501_Capacity | Central Valley | Fresno | DEVILS DEN BANK 1 | 2534501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253451101_Capacity | Central Valley | Fresno | DEVILS DEN 1101 | 253451101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253451102_Capacity | Central Valley | Fresno | DEVILS DEN 1102 | 253451102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2527301_Capacity | Central Valley | Fresno | KETTLEMAN HILLS BANK 1 | 2527301 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252731101_Capacity | Central Valley | Fresno | KETTLEMAN HILLS 1101 | 252731101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252732104_Capacity | Central Valley | Fresno | KETTLEMAN HILLS 2104 | 252732104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2529501_Capacity | Central Valley | Fresno | TULARE LAKE BANK 1 | 2529501 | Bank | None | None | None | 55.07% | 0 | 0% | 29.69 | 15.29 | 51.5% | 0 | 0% | 29.69 | 16.35 | 55.07% | 0 | 0% | 29.69 | 16.32 | 54.97% | 0 | 0% | 29.69 | 16.32 | 54.97% | 0 | 0% | 29.69 | 16.32 | 54.97% | 0 | 0%
GNA_252951104_Capacity | Central Valley | Fresno | TULARE LAKE 1104 | 252951104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252951106_Capacity | Central Valley | Fresno | TULARE LAKE 1106 | 252951106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2529502_Capacity | Central Valley | Fresno | TULARE LAKE BANK 2 | 2529502 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252951108_Capacity | Central Valley | Fresno | TULARE LAKE 1108 | 252951108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2522401_Capacity | Central Valley | Fresno | KINGSBURG BANK 1 | 2522401 | Bank | None | None | None | 87.7% | 0 | 0% | 44.55 | 37.41 | 83.97% | 0 | 0% | 44.55 | 37.69 | 84.6% | 0 | 0% | 44.55 | 38.08 | 85.48% | 0 | 0% | 44.55 | 38.53 | 86.49% | 0 | 0% | 44.55 | 39.07 | 87.7% | 0 | 0%
GNA_252241102_Capacity | Central Valley | Fresno | KINGSBURG 1102 | 252241102 | Feeder | None | None | None | 81.95% | 0 | 0% | 12.19 | 9.49 | 77.85% | 0 | 0% | 12.19 | 9.5 | 77.93% | 0 | 0% | 12.19 | 9.61 | 78.84% | 0 | 0% | 12.19 | 9.77 | 80.15% | 0 | 0% | 12.19 | 9.99 | 81.95% | 0 | 0%
GNA_252241108_Capacity | Central Valley | Fresno | KINGSBURG 1108 | 252241108 | Feeder | None | None | None | 83.12% | 0 | 0% | 11.2 | 8.77 | 78.3% | 0 | 0% | 11.2 | 8.82 | 78.75% | 0 | 0% | 11.2 | 8.92 | 79.64% | 0 | 0% | 11.2 | 9.1 | 81.25% | 0 | 0% | 11.2 | 9.31 | 83.12% | 0 | 0%
GNA_252241110_Capacity | Central Valley | Fresno | KINGSBURG 1110 | 252241110 | Feeder | None | None | None | 96.55% | 0 | 0% | 12.19 | 11.77 | 96.55% | 0 | 0% | 12.19 | 11.77 | 96.55% | 0 | 0% | 12.19 | 11.77 | 96.55% | 0 | 0% | 12.19 | 11.77 | 96.55% | 0 | 0% | 12.19 | 11.77 | 96.55% | 0 | 0%
GNA_252241116_Capacity | Central Valley | Fresno | KINGSBURG 1116 | 252241116 | Feeder | Demand Growth | Capacity | 2023 | 106.3% | 0.73 | 6.32% | 11.55 | 11.92 | 103.2% | 0.37 | 3.203% | 11.55 | 11.99 | 103.8% | 0.44 | 3.81% | 11.55 | 12.07 | 104.5% | 0.52 | 4.502% | 11.55 | 12.18 | 105.5% | 0.63 | 5.455% | 11.55 | 12.28 | 106.3% | 0.73 | 6.32%
GNA_2522403_Capacity | Central Valley | Fresno | KINGSBURG BANK 3 | 2522403 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252241111_Capacity | Central Valley | Fresno | KINGSBURG 1111 (old 1114) | 252241111 | Feeder | None | None | None | 100.3% | 0.04 | 0.3236% | 12.36 | 11.25 | 91.02% | 0 | 0% | 12.36 | 11.38 | 92.07% | 0 | 0% | 12.36 | 11.64 | 94.17% | 0 | 0% | 12.36 | 12 | 97.09% | 0 | 0% | 12.36 | 12.4 | 100.3% | 0.04 | 0.3236%
GNA_252241112_Capacity | Central Valley | Fresno | KINGSBURG 1112 | 252241112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252241113_Capacity | Central Valley | Fresno | KINGSBURG 1113 | 252241113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252241114_Capacity | Central Valley | Fresno | KINGSBURG 1114 | 252241114 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2541204_Capacity | Central Valley | Fresno | MC CALL BANK 4 | 2541204 | Bank | None | None | None | 90.82% | 0 | 0% | 44.55 | 39.01 | 87.56% | 0 | 0% | 44.55 | 39.35 | 88.33% | 0 | 0% | 44.55 | 39.71 | 89.14% | 0 | 0% | 44.55 | 40.46 | 90.82% | 0 | 0% | 44.55 | 40.42 | 90.73% | 0 | 0%
GNA_254121101_Capacity | Central Valley | Fresno | MC CALL 1101 | 254121101 | Feeder | None | None | None | 75.14% | 0 | 0% | 12.19 | 8.74 | 71.7% | 0 | 0% | 12.19 | 8.83 | 72.44% | 0 | 0% | 12.19 | 8.93 | 73.26% | 0 | 0% | 12.19 | 9.03 | 74.08% | 0 | 0% | 12.19 | 9.16 | 75.14% | 0 | 0%
GNA_254121103_Capacity | Central Valley | Fresno | MC CALL 1103 | 254121103 | Feeder | None | None | None | 95.16% | 0 | 0% | 12.19 | 9.34 | 76.62% | 0 | 0% | 12.19 | 10.5 | 86.14% | 0 | 0% | 12.19 | 10.6 | 86.96% | 0 | 0% | 12.19 | 11.03 | 90.48% | 0 | 0% | 12.19 | 11.6 | 95.16% | 0 | 0%
GNA_254121105_Capacity | Central Valley | Fresno | MC CALL 1105 | 254121105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254121107_Capacity | Central Valley | Fresno | MC CALL 1107 | 254121107 | Feeder | None | None | None | 91.11% | 0 | 0% | 12.83 | 11.69 | 91.11% | 0 | 0% | 12.83 | 10.76 | 83.87% | 0 | 0% | 12.83 | 10.84 | 84.49% | 0 | 0% | 12.83 | 10.97 | 85.5% | 0 | 0% | 12.83 | 10.15 | 79.11% | 0 | 0%
GNA_2541205_Capacity | Central Valley | Fresno | MC CALL BANK 5 | 2541205 | Bank | Demand Growth | Capacity | 2023 | 101.2% | 0.55 | 1.235% | 44.55 | 45.1 | 101.2% | 0.55 | 1.235% | 44.55 | 44.36 | 99.57% | 0 | 0% | 44.55 | 43.78 | 98.27% | 0 | 0% | 44.55 | 44.26 | 99.35% | 0 | 0% | 44.55 | 44.84 | 100.7% | 0.29 | 0.651%
GNA_254121102_Capacity | Central Valley | Fresno | MC CALL 1102 | 254121102 | Feeder | None | None | None | 99.59% | 0 | 0% | 12.19 | 11.75 | 96.39% | 0 | 0% | 12.19 | 11.76 | 96.47% | 0 | 0% | 12.19 | 11.81 | 96.88% | 0 | 0% | 12.19 | 11.95 | 98.03% | 0 | 0% | 12.19 | 12.14 | 99.59% | 0 | 0%
GNA_254121104_Capacity | Central Valley | Fresno | MC CALL 1104 | 254121104 | Feeder | Demand Growth | Capacity | 2023 | 107.1% | 0.87 | 7.137% | 12.19 | 13.05 | 107.1% | 0.86 | 7.055% | 12.19 | 12.94 | 106.2% | 0.75 | 6.153% | 12.19 | 12.95 | 106.2% | 0.76 | 6.235% | 12.19 | 13.02 | 106.8% | 0.83 | 6.809% | 12.19 | 13.06 | 107.1% | 0.87 | 7.137%
GNA_254121106_Capacity | Central Valley | Fresno | MC CALL 1106 | 254121106 | Feeder | Demand Growth | Capacity | 2026 | 102.2% | 0.27 | 2.215% | 12.19 | 12.06 | 98.93% | 0 | 0% | 12.19 | 12.15 | 99.67% | 0 | 0% | 12.19 | 12.23 | 100.3% | 0.04 | 0.3281% | 12.19 | 12.33 | 101.1% | 0.14 | 1.148% | 12.19 | 12.46 | 102.2% | 0.27 | 2.215%
GNA_254121108_Capacity | Central Valley | Fresno | MC CALL 1108 | 254121108 | Feeder | None | None | None | 78.72% | 0 | 0% | 12.83 | 10.1 | 78.72% | 0 | 0% | 12.83 | 10.01 | 78.02% | 0 | 0% | 12.83 | 10 | 77.94% | 0 | 0% | 12.83 | 9.98 | 77.79% | 0 | 0% | 12.83 | 9.95 | 77.55% | 0 | 0%
GNA_2522902_Capacity | Central Valley | Fresno | PARLIER BANK 2 | 2522902 | Bank | None | None | None | 64.79% | 0 | 0% | 44.53 | 25.67 | 57.65% | 0 | 0% | 44.53 | 27.69 | 62.18% | 0 | 0% | 44.53 | 27.72 | 62.25% | 0 | 0% | 44.53 | 27.75 | 62.32% | 0 | 0% | 44.53 | 28.85 | 64.79% | 0 | 0%
GNA_252291102_Capacity | Central Valley | Fresno | PARLIER 1102 | 252291102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252291103_Capacity | Central Valley | Fresno | PARLIER 1103 | 252291103 | Feeder | None | None | None | 51.28% | 0 | 0% | 9.75 | 4.24 | 43.49% | 0 | 0% | 9.75 | 5 | 51.28% | 0 | 0% | 9.75 | 4.98 | 51.08% | 0 | 0% | 9.75 | 4.97 | 50.97% | 0 | 0% | 9.75 | 4.98 | 51.08% | 0 | 0%
GNA_252291104_Capacity | Central Valley | Fresno | PARLIER 1104 | 252291104 | Feeder | None | None | None | 89.71% | 0 | 0% | 10.69 | 9.59 | 89.71% | 0 | 0% | 10.69 | 8.79 | 82.23% | 0 | 0% | 10.69 | 8.76 | 81.95% | 0 | 0% | 10.69 | 8.72 | 81.57% | 0 | 0% | 10.69 | 8.74 | 81.76% | 0 | 0%
GNA_252291105_Capacity | Central Valley | Fresno | PARLIER 1105 | 252291105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2523001_Capacity | Central Valley | Fresno | CAMDEN BANK 1 | 2523001 | Bank | None | None | None | 96.2% | 0 | 0% | 29.7 | 28.35 | 95.45% | 0 | 0% | 29.7 | 28.39 | 95.59% | 0 | 0% | 29.7 | 28.43 | 95.72% | 0 | 0% | 29.7 | 28.49 | 95.93% | 0 | 0% | 29.7 | 28.57 | 96.2% | 0 | 0%
GNA_252301103_Capacity | Central Valley | Fresno | CAMDEN 1103 | 252301103 | Feeder | None | None | None | 100% | 0 | 0% | 12.19 | 12.19 | 100% | 0 | 0% | 12.19 | 12.16 | 99.75% | 0 | 0% | 12.19 | 12.14 | 99.59% | 0 | 0% | 12.19 | 12.12 | 99.43% | 0 | 0% | 12.19 | 12.1 | 99.26% | 0 | 0%
GNA_252301104_Capacity | Central Valley | Fresno | CAMDEN 1104 | 252301104 | Feeder | None | None | None | 86.87% | 0 | 0% | 12.19 | 10.25 | 84.09% | 0 | 0% | 12.19 | 10.32 | 84.66% | 0 | 0% | 12.19 | 10.41 | 85.4% | 0 | 0% | 12.19 | 10.49 | 86.05% | 0 | 0% | 12.19 | 10.59 | 86.87% | 0 | 0%
GNA_252301105_Capacity | Central Valley | Fresno | CAMDEN 1105 | 252301105 | Feeder | None | None | None | 90.98% | 0 | 0% | 12.19 | 11.09 | 90.98% | 0 | 0% | 12.19 | 11.08 | 90.89% | 0 | 0% | 12.19 | 11.06 | 90.73% | 0 | 0% | 12.19 | 11.06 | 90.73% | 0 | 0% | 12.19 | 11.06 | 90.73% | 0 | 0%
GNA_2523002_Capacity | Central Valley | Fresno | CAMDEN BANK 2 | 2523002 | Bank | None | None | None | 39.49% | 0 | 0% | 29.7 | 11.4 | 38.38% | 0 | 0% | 29.7 | 11.49 | 38.69% | 0 | 0% | 29.7 | 11.57 | 38.96% | 0 | 0% | 29.7 | 11.65 | 39.23% | 0 | 0% | 29.7 | 11.73 | 39.49% | 0 | 0%
GNA_252301102_Capacity | Central Valley | Fresno | CAMDEN 1102 | 252301102 | Feeder | Demand Growth | Capacity | 2023 | 118.6% | 1.99 | 18.62% | 10.69 | 12.34 | 115.4% | 1.65 | 15.43% | 10.69 | 12.43 | 116.3% | 1.74 | 16.28% | 10.69 | 12.51 | 117% | 1.82 | 17.03% | 10.69 | 12.59 | 117.8% | 1.9 | 17.77% | 10.69 | 12.68 | 118.6% | 1.99 | 18.62%
GNA_2537101_Capacity | Central Valley | Fresno | HARDWICK BANK 1 | 2537101 | Bank | Demand Growth | Capacity | 2023 | 112.9% | 1.85 | 12.88% | 14.36 | 16.14 | 112.4% | 1.78 | 12.4% | 14.36 | 16.08 | 112% | 1.72 | 11.98% | 14.36 | 16.05 | 111.8% | 1.69 | 11.77% | 14.36 | 16.08 | 112% | 1.72 | 11.98% | 14.36 | 16.21 | 112.9% | 1.85 | 12.88%
GNA_253711101_Capacity | Central Valley | Fresno | HARDWICK 1101 | 253711101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253711102_Capacity | Central Valley | Fresno | HARDWICK 1102 | 253711102 | Feeder | Demand Growth | Capacity | 2027 | 101.9% | 0.2 | 1.912% | 10.46 | 10.38 | 99.24% | 0 | 0% | 10.46 | 10.34 | 98.85% | 0 | 0% | 10.46 | 10.33 | 98.76% | 0 | 0% | 10.46 | 10.37 | 99.14% | 0 | 0% | 10.46 | 10.66 | 101.9% | 0.2 | 1.912%
GNA_2536001_Capacity | Central Valley | Fresno | LEMOORE BANK 1 | 2536001 | Bank | None | None | None | 82.28% | 0 | 0% | 29.69 | 22.23 | 74.87% | 0 | 0% | 29.69 | 22.63 | 76.22% | 0 | 0% | 29.69 | 23.52 | 79.22% | 0 | 0% | 29.69 | 24.18 | 81.44% | 0 | 0% | 29.69 | 24.43 | 82.28% | 0 | 0%
GNA_253601101_Capacity | Central Valley | Fresno | LEMOORE 1101 | 253601101 | Feeder | Demand Growth | Capacity | 2025 | 100.8% | 0.1 | 0.8203% | 12.19 | 11.33 | 92.95% | 0 | 0% | 12.19 | 11.64 | 95.49% | 0 | 0% | 12.19 | 12.29 | 100.8% | 0.1 | 0.8203% | 12.19 | 12.29 | 100.8% | 0.1 | 0.8203% | 12.19 | 12.29 | 100.8% | 0.1 | 0.8203%
GNA_253601103_Capacity | Central Valley | Fresno | LEMOORE 1103 | 253601103 | Feeder | None | None | None | 95.82% | 0 | 0% | 12.19 | 11.3 | 92.7% | 0 | 0% | 12.19 | 11.33 | 92.95% | 0 | 0% | 12.19 | 11.43 | 93.77% | 0 | 0% | 12.19 | 11.54 | 94.67% | 0 | 0% | 12.19 | 11.68 | 95.82% | 0 | 0%
GNA_2536002_Capacity | Central Valley | Fresno | LEMOORE BANK 2 | 2536002 | Bank | Demand Growth | Capacity | 2023 | 101.1% | 0.33 | 1.111% | 29.7 | 30.03 | 101.1% | 0.33 | 1.111% | 29.7 | 26.47 | 89.12% | 0 | 0% | 29.7 | 26.75 | 90.07% | 0 | 0% | 29.7 | 27.14 | 91.38% | 0 | 0% | 29.7 | 27.58 | 92.86% | 0 | 0%
GNA_253601102_Capacity | Central Valley | Fresno | LEMOORE 1102 | 253601102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253601104_Capacity | Central Valley | Fresno | LEMOORE 1104 | 253601104 | Feeder | None | None | None | 80.38% | 0 | 0% | 9.43 | 7.21 | 76.46% | 0 | 0% | 9.43 | 7.29 | 77.31% | 0 | 0% | 9.43 | 7.37 | 78.15% | 0 | 0% | 9.43 | 7.45 | 79% | 0 | 0% | 9.43 | 7.58 | 80.38% | 0 | 0%
GNA_253601105_Capacity | Central Valley | Fresno | LEMOORE 1105 | 253601105 | Feeder | Demand Growth | Capacity | 2023 | 108% | 0.98 | 8.039% | 12.19 | 12.95 | 106.2% | 0.76 | 6.235% | 12.19 | 12.96 | 106.3% | 0.77 | 6.317% | 12.19 | 13.02 | 106.8% | 0.83 | 6.809% | 12.19 | 13.1 | 107.5% | 0.91 | 7.465% | 12.19 | 13.17 | 108% | 0.98 | 8.039%
GNA_2535301_Capacity | Central Valley | Fresno | BOWLES BANK 1 | 2535301 | Bank | None | None | None | 66.56% | 0 | 0% | 25.69 | 16.48 | 64.15% | 0 | 0% | 25.69 | 17.01 | 66.21% | 0 | 0% | 25.69 | 16.99 | 66.13% | 0 | 0% | 25.69 | 17.05 | 66.37% | 0 | 0% | 25.69 | 17.1 | 66.56% | 0 | 0%
GNA_253531101_Capacity | Central Valley | Fresno | BOWLES 1101 | 253531101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253531102_Capacity | Central Valley | Fresno | BOWLES 1102 | 253531102 | Feeder | None | None | None | 36.04% | 0 | 0% | 7.63 | 2.75 | 36.04% | 0 | 0% | 7.63 | 2.74 | 35.91% | 0 | 0% | 7.63 | 2.73 | 35.78% | 0 | 0% | 7.63 | 2.74 | 35.91% | 0 | 0% | 7.63 | 2.75 | 36.04% | 0 | 0%
GNA_253531103_Capacity | Central Valley | Fresno | BOWLES 1103 | 253531103 | Feeder | None | None | None | 51.93% | 0 | 0% | 8.55 | 4.38 | 51.23% | 0 | 0% | 8.55 | 4.36 | 50.99% | 0 | 0% | 8.55 | 4.37 | 51.11% | 0 | 0% | 8.55 | 4.41 | 51.58% | 0 | 0% | 8.55 | 4.44 | 51.93% | 0 | 0%
GNA_253531104_Capacity | Central Valley | Fresno | BOWLES 1104 | 253531104 | Feeder | None | None | None | 63.09% | 0 | 0% | 6.61 | 4.16 | 62.93% | 0 | 0% | 6.61 | 4.15 | 62.78% | 0 | 0% | 6.61 | 4.15 | 62.78% | 0 | 0% | 6.61 | 4.16 | 62.93% | 0 | 0% | 6.61 | 4.17 | 63.09% | 0 | 0%
GNA_2523701_Capacity | Central Valley | Fresno | CARUTHERS BANK 1 | 2523701 | Bank | None | None | None | 83.06% | 0 | 0% | 29.7 | 24.04 | 80.94% | 0 | 0% | 29.7 | 24.67 | 83.06% | 0 | 0% | 29.7 | 24.65 | 83% | 0 | 0% | 29.7 | 24.63 | 82.93% | 0 | 0% | 29.7 | 24.65 | 83% | 0 | 0%
GNA_252371101_Capacity | Central Valley | Fresno | CARUTHERS 1101 | 252371101 | Feeder | None | None | None | 100% | 0 | 0% | 11.67 | 11.67 | 100% | 0 | 0% | 11.67 | 11.65 | 99.83% | 0 | 0% | 11.67 | 11.63 | 99.66% | 0 | 0% | 11.67 | 11.61 | 99.49% | 0 | 0% | 11.67 | 11.61 | 99.49% | 0 | 0%
GNA_252371102_Capacity | Central Valley | Fresno | CARUTHERS 1102 | 252371102 | Feeder | Demand Growth | Capacity | 2024 | 112.9% | 1.65 | 12.86% | 14.97 | 13.8 | 92.18% | 0 | 0% | 12.83 | 14.46 | 112.7% | 1.63 | 12.7% | 12.83 | 14.46 | 112.7% | 1.63 | 12.7% | 12.83 | 14.46 | 112.7% | 1.63 | 12.7% | 12.83 | 14.48 | 112.9% | 1.65 | 12.86%
GNA_2523702_Capacity | Central Valley | Fresno | CARUTHERS BANK 2 | 2523702 | Bank | None | None | None | 69.09% | 0 | 0% | 29.7 | 20.52 | 69.09% | 0 | 0% | 29.7 | 19.92 | 67.07% | 0 | 0% | 29.7 | 19.89 | 66.97% | 0 | 0% | 29.7 | 19.87 | 66.9% | 0 | 0% | 29.7 | 19.87 | 66.9% | 0 | 0%
GNA_252371104_Capacity | Central Valley | Fresno | CARUTHERS 1104 | 252371104 | Feeder | None | None | None | 71.47% | 0 | 0% | 12.83 | 9.17 | 71.47% | 0 | 0% | 12.83 | 8.58 | 66.87% | 0 | 0% | 12.83 | 8.55 | 66.64% | 0 | 0% | 12.83 | 8.53 | 66.48% | 0 | 0% | 12.83 | 8.54 | 66.56% | 0 | 0%
GNA_252371105_Capacity | Central Valley | Fresno | CARUTHERS 1105 | 252371105 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2544101_Capacity | Central Valley | Fresno | MC MULLIN BANK 1 | 2544101 | Bank | None | None | None | 68.17% | 0 | 0% | 44.55 | 30.37 | 68.17% | 0 | 0% | 44.55 | 30.32 | 68.06% | 0 | 0% | 44.55 | 30.24 | 67.88% | 0 | 0% | 44.55 | 30.21 | 67.81% | 0 | 0% | 44.55 | 30.18 | 67.74% | 0 | 0%
GNA_254411104_Capacity | Central Valley | Fresno | MC MULLIN SUB 1104 | 254411104 | Feeder | None | None | None | 92.53% | 0 | 0% | 12.19 | 11.28 | 92.53% | 0 | 0% | 12.19 | 11.26 | 92.37% | 0 | 0% | 12.19 | 11.22 | 92.04% | 0 | 0% | 12.19 | 11.22 | 92.04% | 0 | 0% | 12.19 | 11.21 | 91.96% | 0 | 0%
GNA_254411105_Capacity | Central Valley | Fresno | MC MULLIN SUB 1105 | 254411105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254411106_Capacity | Central Valley | Fresno | MC MULLIN SUB 1106 | 254411106 | Feeder | None | None | None | 85.97% | 0 | 0% | 12.19 | 10.48 | 85.97% | 0 | 0% | 12.19 | 10.44 | 85.64% | 0 | 0% | 12.19 | 10.41 | 85.4% | 0 | 0% | 12.19 | 10.39 | 85.23% | 0 | 0% | 12.19 | 10.39 | 85.23% | 0 | 0%
GNA_2523601_Capacity | Central Valley | Fresno | SAN JOAQUIN BANK 1 | 2523601 | Bank | Demand Growth | Capacity | 2023 | 128.5% | 2.96 | 28.46% | 10.4 | 12.65 | 121.6% | 2.25 | 21.63% | 10.4 | 12.73 | 122.4% | 2.33 | 22.4% | 10.4 | 13.15 | 126.4% | 2.75 | 26.44% | 10.4 | 13.24 | 127.3% | 2.84 | 27.31% | 10.4 | 13.36 | 128.5% | 2.96 | 28.46%
GNA_252361106_Capacity | Central Valley | Fresno | SAN JOAQUIN 1106 | 252361106 | Feeder | Demand Growth | Capacity | 2023 | 116% | 1.3 | 15.99% | 8.13 | 8.81 | 108.4% | 0.68 | 8.364% | 8.13 | 8.9 | 109.5% | 0.77 | 9.471% | 8.13 | 9.23 | 113.5% | 1.1 | 13.53% | 8.13 | 9.32 | 114.6% | 1.19 | 14.64% | 8.13 | 9.43 | 116% | 1.3 | 15.99%
GNA_252361108_Capacity | Central Valley | Fresno | SAN JOAQUIN 1108 | 252361108 | Feeder | None | None | None | 71.47% | 0 | 0% | 7.01 | 4.95 | 70.61% | 0 | 0% | 7.01 | 4.93 | 70.33% | 0 | 0% | 7.01 | 5.01 | 71.47% | 0 | 0% | 7.01 | 5.01 | 71.47% | 0 | 0% | 7.01 | 5.01 | 71.47% | 0 | 0%
GNA_2523602_Capacity | Central Valley | Fresno | SAN JOAQUIN BANK 2 | 2523602 | Bank | None | None | None | 97.55% | 0 | 0% | 6.93 | 6.76 | 97.55% | 0 | 0% | 6.93 | 6.74 | 97.26% | 0 | 0% | 6.93 | 6.72 | 96.97% | 0 | 0% | 6.93 | 6.7 | 96.68% | 0 | 0% | 6.93 | 6.69 | 96.54% | 0 | 0%
GNA_252361112_Capacity | Central Valley | Fresno | SAN JOAQUIN 1112 | 252361112 | Feeder | None | None | None | 87.08% | 0 | 0% | 8.13 | 7.08 | 87.08% | 0 | 0% | 8.13 | 7.06 | 86.84% | 0 | 0% | 8.13 | 7.04 | 86.59% | 0 | 0% | 8.13 | 7.02 | 86.35% | 0 | 0% | 8.13 | 7.01 | 86.22% | 0 | 0%
GNA_2536601_Capacity | Central Valley | Fresno | STROUD BANK 1 | 2536601 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253661101_Capacity | Central Valley | Fresno | STROUD 1101 | 253661101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253661102_Capacity | Central Valley | Fresno | STROUD 1102 | 253661102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253661104_Capacity | Central Valley | Fresno | STROUD 1104 | 253661104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2540901_Capacity | Central Valley | Fresno | DINUBA BANK 1 | 2540901 | Bank | None | None | None | 89.49% | 0 | 0% | 29.7 | 25.39 | 85.49% | 0 | 0% | 29.7 | 25.89 | 87.17% | 0 | 0% | 29.7 | 26.07 | 87.78% | 0 | 0% | 29.7 | 26.28 | 88.48% | 0 | 0% | 29.7 | 26.58 | 89.49% | 0 | 0%
GNA_254091102_Capacity | Central Valley | Fresno | DINUBA 1102 | 254091102 | Feeder | Demand Growth | Capacity | 2023 | 105.7% | 0.81 | 5.68% | 14.26 | 14.59 | 102.3% | 0.33 | 2.314% | 14.26 | 14.96 | 104.9% | 0.7 | 4.909% | 14.26 | 14.99 | 105.1% | 0.73 | 5.119% | 14.26 | 15.01 | 105.3% | 0.75 | 5.259% | 14.26 | 15.07 | 105.7% | 0.81 | 5.68%
GNA_254091104_Capacity | Central Valley | Fresno | DINUBA 1104 | 254091104 | Feeder | Demand Growth | Capacity | 2023 | 115.6% | 2 | 15.59% | 12.83 | 14.42 | 112.4% | 1.59 | 12.39% | 12.83 | 14.49 | 112.9% | 1.66 | 12.94% | 12.83 | 14.58 | 113.6% | 1.75 | 13.64% | 12.83 | 14.7 | 114.6% | 1.87 | 14.58% | 12.83 | 14.83 | 115.6% | 2 | 15.59%
GNA_2540902_Capacity | Central Valley | Fresno | DINUBA BANK 2 | 2540902 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254091105_Capacity | Central Valley | Fresno | DINUBA 1105 | 254091105 | Feeder | Demand Growth | Capacity | 2023 | 120.9% | 2.68 | 20.89% | 12.83 | 15.51 | 120.9% | 2.68 | 20.89% | 12.83 | 15.49 | 120.7% | 2.66 | 20.73% | 12.83 | 15.47 | 120.6% | 2.64 | 20.58% | 12.83 | 15.47 | 120.6% | 2.64 | 20.58% | 12.83 | 15.5 | 120.8% | 2.67 | 20.81%
GNA_254091106_Capacity | Central Valley | Fresno | DINUBA 1106 | 254091106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2528401_Capacity | Central Valley | Fresno | OROSI BANK 1 | 2528401 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252841101_Capacity | Central Valley | Fresno | OROSI 1101 | 252841101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252841103_Capacity | Central Valley | Fresno | OROSI 1103 | 252841103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2528402_Capacity | Central Valley | Fresno | OROSI BANK 2 | 2528402 | Bank | None | None | None | 43.7% | 0 | 0% | 29.7 | 11.66 | 39.26% | 0 | 0% | 29.7 | 11.35 | 38.22% | 0 | 0% | 29.7 | 11.23 | 37.81% | 0 | 0% | 29.7 | 11.12 | 37.44% | 0 | 0% | 29.7 | 12.98 | 43.7% | 0 | 0%
GNA_252841102_Capacity | Central Valley | Fresno | OROSI 1102 | 252841102 | Feeder | None | None | None | 77.14% | 0 | 0% | 4.68 | 1.75 | 37.39% | 0 | 0% | 4.68 | 1.73 | 36.97% | 0 | 0% | 4.68 | 1.71 | 36.54% | 0 | 0% | 4.68 | 1.7 | 36.32% | 0 | 0% | 4.68 | 3.61 | 77.14% | 0 | 0%
GNA_252841104_Capacity | Central Valley | Fresno | OROSI 1104 | 252841104 | Feeder | None | None | None | 100.3% | 0.03 | 0.2868% | 10.46 | 10.49 | 100.3% | 0.03 | 0.2868% | 10.46 | 10.27 | 98.18% | 0 | 0% | 10.46 | 10.2 | 97.51% | 0 | 0% | 10.46 | 10.07 | 96.27% | 0 | 0% | 10.46 | 9.97 | 95.32% | 0 | 0%
GNA_2523401_Capacity | Central Valley | Fresno | REEDLEY BANK 1 | 2523401 | Bank | None | None | None | 80.54% | 0 | 0% | 29.7 | 22.58 | 76.03% | 0 | 0% | 29.7 | 23.92 | 80.54% | 0 | 0% | 29.7 | 23.79 | 80.1% | 0 | 0% | 29.7 | 23.78 | 80.07% | 0 | 0% | 29.7 | 21.91 | 73.77% | 0 | 0%
GNA_252341106_Capacity | Central Valley | Fresno | REEDLEY 1106 | 252341106 | Feeder | Demand Growth | Capacity | 2023 | 128.6% | 2.91 | 28.64% | 10.16 | 11.59 | 114.1% | 1.43 | 14.07% | 10.16 | 13.05 | 128.4% | 2.89 | 28.44% | 10.16 | 13.04 | 128.3% | 2.88 | 28.35% | 10.16 | 13.07 | 128.6% | 2.91 | 28.64% | 10.16 | 11.16 | 109.8% | 1 | 9.843%
GNA_252341112_Capacity | Central Valley | Fresno | REEDLEY 1112 | 252341112 | Feeder | None | None | None | 89.17% | 0 | 0% | 12.19 | 10.87 | 89.17% | 0 | 0% | 12.19 | 10.78 | 88.43% | 0 | 0% | 12.19 | 10.7 | 87.78% | 0 | 0% | 12.19 | 10.66 | 87.45% | 0 | 0% | 12.19 | 10.61 | 87.04% | 0 | 0%
GNA_2523403_Capacity | Central Valley | Fresno | REEDLEY BANK 3 | 2523403 | Bank | Demand Growth | Capacity | 2023 | 132.3% | 8.21 | 32.28% | 25.43 | 33.41 | 131.4% | 7.98 | 31.38% | 25.43 | 33.34 | 131.1% | 7.91 | 31.1% | 25.43 | 33.28 | 130.9% | 7.85 | 30.87% | 25.43 | 33.33 | 131.1% | 7.9 | 31.07% | 25.43 | 33.64 | 132.3% | 8.21 | 32.28%
GNA_252341101_Capacity | Central Valley | Fresno | REEDLEY 1101 | 252341101 | Feeder | None | None | None | 83.1% | 0 | 0% | 12.19 | 9.89 | 81.13% | 0 | 0% | 12.19 | 9.88 | 81.05% | 0 | 0% | 12.19 | 9.89 | 81.13% | 0 | 0% | 12.19 | 9.97 | 81.79% | 0 | 0% | 12.19 | 10.13 | 83.1% | 0 | 0%
GNA_252341104_Capacity | Central Valley | Fresno | REEDLEY 1104 | 252341104 | Feeder | None | None | None | 93.4% | 0 | 0% | 10.46 | 9.77 | 93.4% | 0 | 0% | 10.46 | 9.68 | 92.54% | 0 | 0% | 10.46 | 9.54 | 91.2% | 0 | 0% | 10.46 | 9.4 | 89.87% | 0 | 0% | 10.46 | 9.28 | 88.72% | 0 | 0%
GNA_252341110_Capacity | Central Valley | Fresno | REEDLEY 1110 | 252341110 | Feeder | None | None | None | 98.28% | 0 | 0% | 12.19 | 11.89 | 97.54% | 0 | 0% | 12.19 | 11.88 | 97.46% | 0 | 0% | 12.19 | 11.86 | 97.29% | 0 | 0% | 12.19 | 11.89 | 97.54% | 0 | 0% | 12.19 | 11.98 | 98.28% | 0 | 0%
GNA_2545302_Capacity | Central Valley | Fresno | WAHTOKE BANK 2 | 2545302 | Bank | Demand Growth | Capacity | 2023 | 118.2% | 5.41 | 18.22% | 29.69 | 34.56 | 116.4% | 4.87 | 16.4% | 29.69 | 34.74 | 117% | 5.05 | 17.01% | 29.69 | 34.79 | 117.2% | 5.1 | 17.18% | 29.69 | 34.93 | 117.6% | 5.24 | 17.65% | 29.69 | 35.1 | 118.2% | 5.41 | 18.22%
GNA_254531106_Capacity | Central Valley | Fresno | WAHTOKE 1106 | 254531106 | Feeder | Demand Growth | Capacity | 2023 | 101.8% | 0.22 | 1.805% | 12.19 | 12.31 | 101% | 0.12 | 0.9844% | 12.19 | 12.3 | 100.9% | 0.11 | 0.9024% | 12.19 | 12.31 | 101% | 0.12 | 0.9844% | 12.19 | 12.36 | 101.4% | 0.17 | 1.395% | 12.19 | 12.41 | 101.8% | 0.22 | 1.805%
GNA_254531107_Capacity | Central Valley | Fresno | WAHTOKE 1107 | 254531107 | Feeder | Demand Growth | Capacity | 2023 | 108% | 0.97 | 7.957% | 12.19 | 12.79 | 104.9% | 0.6 | 4.922% | 12.19 | 12.83 | 105.3% | 0.64 | 5.25% | 12.19 | 12.9 | 105.8% | 0.71 | 5.824% | 12.19 | 13.02 | 106.8% | 0.83 | 6.809% | 12.19 | 13.16 | 108% | 0.97 | 7.957%
GNA_254531108_Capacity | Central Valley | Fresno | WAHTOKE 1108 | 254531108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2545303_Capacity | Central Valley | Fresno | WAHTOKE BANK 3 | 2545303 | Bank | None | None | None | 94.61% | 0 | 0% | 29.7 | 28.1 | 94.61% | 0 | 0% | 29.7 | 27.24 | 91.72% | 0 | 0% | 29.7 | 27.43 | 92.36% | 0 | 0% | 29.7 | 27.63 | 93.03% | 0 | 0% | 29.7 | 27.87 | 93.84% | 0 | 0%
GNA_254531109_Capacity | Central Valley | Fresno | WAHTOKE 1109 | 254531109 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254531110_Capacity | Central Valley | Fresno | WAHTOKE 1110 | 254531110 | Feeder | None | None | None | 80.34% | 0 | 0% | 12.36 | 9.31 | 75.32% | 0 | 0% | 12.36 | 9.63 | 77.91% | 0 | 0% | 12.36 | 9.73 | 78.72% | 0 | 0% | 12.36 | 9.82 | 79.45% | 0 | 0% | 12.36 | 9.93 | 80.34% | 0 | 0%
GNA_254531111_Capacity | Central Valley | Fresno | WAHTOKE 1111 | 254531111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2544401_Capacity | Central Valley | Fresno | RAINBOW BANK 1 | 2544401 | Bank | None | None | None | 87.91% | 0 | 0% | 29.7 | 20.61 | 69.39% | 0 | 0% | 29.7 | 20.88 | 70.3% | 0 | 0% | 29.7 | 25.46 | 85.72% | 0 | 0% | 29.7 | 25.77 | 86.77% | 0 | 0% | 29.7 | 26.11 | 87.91% | 0 | 0%
GNA_254441103_Capacity | Central Valley | Fresno | RAINBOW 1103 | 254441103 | Feeder | None | None | None | 33.13% | 0 | 0% | 12.83 | 0.09 | 0.7015% | 0 | 0% | 12.83 | 0.05 | 0.3897% | 0 | 0% | 12.83 | 4.25 | 33.13% | 0 | 0% | 12.83 | 4.22 | 32.89% | 0 | 0% | 12.83 | 4.16 | 32.42% | 0 | 0%
GNA_254441105_Capacity | Central Valley | Fresno | RAINBOW 1105 | 254441105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254441106_Capacity | Central Valley | Fresno | RAINBOW 1106 | 254441106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2523501_Capacity | Central Valley | Fresno | SANGER BANK 1 | 2523501 | Bank | Demand Growth | Capacity | 2023 | 103.6% | 1.06 | 3.569% | 29.7 | 29.97 | 100.9% | 0.27 | 0.9091% | 29.7 | 30.06 | 101.2% | 0.36 | 1.212% | 29.7 | 30.17 | 101.6% | 0.47 | 1.582% | 29.7 | 30.42 | 102.4% | 0.72 | 2.424% | 29.7 | 30.76 | 103.6% | 1.06 | 3.569%
GNA_252351108_Capacity | Central Valley | Fresno | SANGER 1108 | 252351108 | Feeder | None | None | None | 89.96% | 0 | 0% | 10.46 | 9.34 | 89.29% | 0 | 0% | 10.46 | 9.32 | 89.1% | 0 | 0% | 10.46 | 9.31 | 89.01% | 0 | 0% | 10.46 | 9.35 | 89.39% | 0 | 0% | 10.46 | 9.41 | 89.96% | 0 | 0%
GNA_252351112_Capacity | Central Valley | Fresno | SANGER 1112 | 252351112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252351114_Capacity | Central Valley | Fresno | SANGER 1114 | 252351114 | Feeder | None | None | None | 87.21% | 0 | 0% | 8.13 | 7.09 | 87.21% | 0 | 0% | 8.13 | 7.06 | 86.84% | 0 | 0% | 8.13 | 7.05 | 86.72% | 0 | 0% | 8.13 | 7.05 | 86.72% | 0 | 0% | 8.13 | 7.07 | 86.96% | 0 | 0%
GNA_252351116_Capacity | Central Valley | Fresno | SANGER 1116 | 252351116 | Feeder | None | None | None | 80.86% | 0 | 0% | 9.09 | 6.95 | 76.46% | 0 | 0% | 9.09 | 7.05 | 77.56% | 0 | 0% | 9.09 | 7.12 | 78.33% | 0 | 0% | 9.09 | 7.24 | 79.65% | 0 | 0% | 9.09 | 7.35 | 80.86% | 0 | 0%
GNA_252351118_Capacity | Central Valley | Fresno | SANGER 1118 | 252351118 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2523503_Capacity | Central Valley | Fresno | SANGER BANK 3 | 2523503 | Bank | Demand Growth | Capacity | 2023 | 106.7% | 1.98 | 6.669% | 29.69 | 31.57 | 106.3% | 1.88 | 6.332% | 29.69 | 31.67 | 106.7% | 1.98 | 6.669% | 29.69 | 27.51 | 92.66% | 0 | 0% | 29.69 | 27.6 | 92.96% | 0 | 0% | 29.69 | 27.72 | 93.36% | 0 | 0%
GNA_252351104_Capacity | Central Valley | Fresno | SANGER 1104 | 252351104 | Feeder | None | None | None | 91.08% | 0 | 0% | 10.76 | 9.52 | 88.48% | 0 | 0% | 10.76 | 9.54 | 88.66% | 0 | 0% | 10.76 | 9.57 | 88.94% | 0 | 0% | 10.76 | 9.66 | 89.78% | 0 | 0% | 10.76 | 9.8 | 91.08% | 0 | 0%
GNA_252351106_Capacity | Central Valley | Fresno | SANGER 1106 | 252351106 | Feeder | Demand Growth | Capacity | 2023 | 144.4% | 4.64 | 44.36% | 10.46 | 15.1 | 144.4% | 4.64 | 44.36% | 10.46 | 15.06 | 144% | 4.6 | 43.98% | 10.46 | 10.79 | 103.2% | 0.33 | 3.155% | 10.46 | 10.77 | 103% | 0.31 | 2.964% | 10.46 | 10.75 | 102.8% | 0.29 | 2.772%
GNA_252351110_Capacity | Central Valley | Fresno | SANGER 1110 | 252351110 | Feeder | None | None | None | 74.41% | 0 | 0% | 9.26 | 6.89 | 74.41% | 0 | 0% | 10.97 | 6.94 | 63.26% | 0 | 0% | 10.97 | 6.96 | 63.45% | 0 | 0% | 10.97 | 6.97 | 63.54% | 0 | 0% | 10.97 | 6.98 | 63.63% | 0 | 0%
GNA_2529401_Capacity | Central Valley | Fresno | TIVY VALLEY BANK 1 | 2529401 | Bank | None | None | None | 78.55% | 0 | 0% | 12.31 | 9.28 | 75.39% | 0 | 0% | 12.31 | 9.67 | 78.55% | 0 | 0% | 12.31 | 9.65 | 78.39% | 0 | 0% | 12.31 | 9.65 | 78.39% | 0 | 0% | 12.31 | 9.66 | 78.47% | 0 | 0%
GNA_252941106_Capacity | Central Valley | Fresno | TIVY VALLEY 1106 | 252941106 | Feeder | None | None | None | 29.52% | 0 | 0% | 8.13 | 2.4 | 29.52% | 0 | 0% | 8.13 | 2.39 | 29.4% | 0 | 0% | 8.13 | 2.38 | 29.27% | 0 | 0% | 8.13 | 2.39 | 29.4% | 0 | 0% | 8.13 | 2.39 | 29.4% | 0 | 0%
GNA_252941107_Capacity | Central Valley | Fresno | TIVY VALLEY 1107 | 252941107 | Feeder | None | None | None | 73.61% | 0 | 0% | 10.46 | 7.32 | 69.98% | 0 | 0% | 10.46 | 7.7 | 73.61% | 0 | 0% | 10.46 | 7.69 | 73.52% | 0 | 0% | 10.46 | 7.68 | 73.42% | 0 | 0% | 10.46 | 7.69 | 73.52% | 0 | 0%
GNA_2522801_Capacity | Central Valley | Fresno | CALIFORNIA AVE BANK 1 | 2522801 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252281110_Capacity | Central Valley | Fresno | CALIFORNIA AVE 1110 | 252281110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252281113_Capacity | Central Valley | Fresno | CALIFORNIA AVE 1113 | 252281113 | Feeder | None | None | None | 93.57% | 0 | 0% | 11.67 | 10.85 | 92.97% | 0 | 0% | 11.67 | 10.87 | 93.14% | 0 | 0% | 11.67 | 10.9 | 93.4% | 0 | 0% | 11.67 | 10.92 | 93.57% | 0 | 0% | 11.67 | 10.89 | 93.32% | 0 | 0%
GNA_252281114_Capacity | Central Valley | Fresno | CALIFORNIA AVE 1114 | 252281114 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252281117_Capacity | Central Valley | Fresno | CALIFORNIA AVE 1117 | 252281117 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2522802_Capacity | Central Valley | Fresno | CALIFORNIA AVE BANK 2 | 2522802 | Bank | None | None | None | 87.68% | 0 | 0% | 44.55 | 36.36 | 81.62% | 0 | 0% | 44.55 | 38.83 | 87.16% | 0 | 0% | 44.55 | 38.95 | 87.43% | 0 | 0% | 44.55 | 39.02 | 87.59% | 0 | 0% | 44.55 | 39.06 | 87.68% | 0 | 0%
GNA_252281106_Capacity | Central Valley | Fresno | CALIFORNIA AVE 1106 | 252281106 | Feeder | Demand Growth | Capacity | 2023 | 114.7% | 1.71 | 14.65% | 11.67 | 13.15 | 112.7% | 1.48 | 12.68% | 11.67 | 13.23 | 113.4% | 1.56 | 13.37% | 11.67 | 13.28 | 113.8% | 1.61 | 13.8% | 11.67 | 13.34 | 114.3% | 1.67 | 14.31% | 11.67 | 13.38 | 114.7% | 1.71 | 14.65%
GNA_252281111_Capacity | Central Valley | Fresno | CALIFORNIA AVE 1111 | 252281111 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252281112_Capacity | Central Valley | Fresno | CALIFORNIA AVE 1112 | 252281112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252281116_Capacity | Central Valley | Fresno | CALIFORNIA AVE 1116 | 252281116 | Feeder | None | None | None | 99.67% | 0 | 0% | 12.19 | 11.98 | 98.28% | 0 | 0% | 12.19 | 12.03 | 98.69% | 0 | 0% | 12.19 | 12.07 | 99.02% | 0 | 0% | 12.19 | 12.1 | 99.26% | 0 | 0% | 12.19 | 12.15 | 99.67% | 0 | 0%
GNA_2522803_Capacity | Central Valley | Fresno | CALIFORNIA AVE BANK 3 | 2522803 | Bank | None | None | None | 76.3% | 0 | 0% | 44.55 | 30.67 | 68.84% | 0 | 0% | 44.55 | 31.44 | 70.57% | 0 | 0% | 44.55 | 32.2 | 72.28% | 0 | 0% | 44.55 | 33.14 | 74.39% | 0 | 0% | 44.55 | 33.99 | 76.3% | 0 | 0%
GNA_252281102_Capacity | Central Valley | Fresno | CALIFORNIA AVE 1102 | 252281102 | Feeder | Demand Growth | Capacity | 2023 | 135.3% | 4.53 | 35.31% | 12.83 | 13.94 | 108.7% | 1.11 | 8.652% | 12.83 | 14.72 | 114.7% | 1.89 | 14.73% | 12.83 | 15.46 | 120.5% | 2.63 | 20.5% | 12.83 | 16.43 | 128.1% | 3.6 | 28.06% | 12.83 | 17.36 | 135.3% | 4.53 | 35.31%
GNA_252281103_Capacity | Central Valley | Fresno | CALIFORNIA AVE 1103 | 252281103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252281104_Capacity | Central Valley | Fresno | CALIFORNIA AVE 1104 | 252281104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252281108_Capacity | Central Valley | Fresno | CALIFORNIA AVE 1108 | 252281108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2542501_Capacity | Central Valley | Fresno | MALAGA BANK 1 | 2542501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254251109_Capacity | Central Valley | Fresno | MALAGA 1109 | 254251109 | Feeder | None | None | None | 100.3% | 0.03 | 0.2788% | 10.76 | 8.63 | 80.2% | 0 | 0% | 10.76 | 10.22 | 94.98% | 0 | 0% | 10.76 | 10.64 | 98.88% | 0 | 0% | 10.76 | 10.71 | 99.54% | 0 | 0% | 10.76 | 10.79 | 100.3% | 0.03 | 0.2788%
GNA_254251110_Capacity | Central Valley | Fresno | MALAGA 1110 | 254251110 | Feeder | Demand Growth | Capacity | 2023 | 106.6% | 0.71 | 6.599% | 10.76 | 11.16 | 103.7% | 0.4 | 3.717% | 10.76 | 11.2 | 104.1% | 0.44 | 4.089% | 10.76 | 11.28 | 104.8% | 0.52 | 4.833% | 10.76 | 11.36 | 105.6% | 0.6 | 5.576% | 10.76 | 11.47 | 106.6% | 0.71 | 6.599%
GNA_254251111_Capacity | Central Valley | Fresno | MALAGA 1111 | 254251111 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2542502_Capacity | Central Valley | Fresno | MALAGA BANK 2 | 2542502 | Bank | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254251106_Capacity | Central Valley | Fresno | MALAGA 1106 | 254251106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254251107_Capacity | Central Valley | Fresno | MALAGA 1107 | 254251107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254251108_Capacity | Central Valley | Fresno | MALAGA 1108 | 254251108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2542503_Capacity | Central Valley | Fresno | MALAGA BANK 3 | 2542503 | Bank | Demand Growth | Capacity | 2027 | 102.6% | 1.17 | 2.627% | 44.53 | 40.12 | 90.1% | 0 | 0% | 44.53 | 43.23 | 97.08% | 0 | 0% | 44.53 | 43.77 | 98.29% | 0 | 0% | 44.53 | 44.23 | 99.33% | 0 | 0% | 44.53 | 45.7 | 102.6% | 1.17 | 2.627%
GNA_254251101_Capacity | Central Valley | Fresno | MALAGA 1101 | 254251101 | Feeder | None | None | None | 71.94% | 0 | 0% | 12.19 | 8.77 | 71.94% | 0 | 0% | 12.19 | 7.8 | 63.99% | 0 | 0% | 12.19 | 8.04 | 65.96% | 0 | 0% | 12.19 | 8.09 | 66.37% | 0 | 0% | 12.19 | 8.17 | 67.02% | 0 | 0%
GNA_254251102_Capacity | Central Valley | Fresno | MALAGA 1102 | 254251102 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254251103_Capacity | Central Valley | Fresno | MALAGA 1103 | 254251103 | Feeder | Demand Growth | Capacity | 2023 | 105.8% | 0.71 | 5.824% | 12.19 | 12.26 | 100.6% | 0.07 | 0.5742% | 12.19 | 12.43 | 102% | 0.24 | 1.969% | 12.19 | 12.53 | 102.8% | 0.34 | 2.789% | 12.19 | 12.71 | 104.3% | 0.52 | 4.266% | 12.19 | 12.9 | 105.8% | 0.71 | 5.824%
GNA_254251104_Capacity | Central Valley | Fresno | MALAGA 1104 | 254251104 | Feeder | None | None | None | 100.5% | 0.06 | 0.4922% | 12.19 | 11.9 | 97.62% | 0 | 0% | 12.19 | 11.9 | 97.62% | 0 | 0% | 12.19 | 11.96 | 98.11% | 0 | 0% | 12.19 | 12.08 | 99.1% | 0 | 0% | 12.19 | 12.25 | 100.5% | 0.06 | 0.4922%
GNA_2548001_Capacity | Central Valley | Fresno | RANCHERS COTTON BANK 1 | 2548001 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254801101_Capacity | Central Valley | Fresno | RANCHERS COTTON 1101 | 254801101 | Feeder | None | None | None | 93.48% | 0 | 0% | 11.97 | 10.97 | 91.65% | 0 | 0% | 11.97 | 11.03 | 92.15% | 0 | 0% | 11.97 | 11.11 | 92.82% | 0 | 0% | 11.97 | 11.15 | 93.15% | 0 | 0% | 11.97 | 11.19 | 93.48% | 0 | 0%
GNA_2537301_Capacity | Central Valley | Fresno | WEST FRESNO BANK 1 | 2537301 | Bank | Demand Growth | Capacity | 2025 | 104.7% | 1.94 | 4.728% | 41.03 | 40.72 | 99.24% | 0 | 0% | 41.03 | 40.96 | 99.83% | 0 | 0% | 41.03 | 41.55 | 101.3% | 0.52 | 1.267% | 41.03 | 42.42 | 103.4% | 1.39 | 3.388% | 41.03 | 42.97 | 104.7% | 1.94 | 4.728%
GNA_253731101_Capacity | Central Valley | Fresno | WEST FRESNO 1101 | 253731101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253731102_Capacity | Central Valley | Fresno | WEST FRESNO 1102 | 253731102 | Feeder | None | None | None | 58.57% | 0 | 0% | 12.19 | 7.14 | 58.57% | 0 | 0% | 12.19 | 6.8 | 55.78% | 0 | 0% | 12.19 | 6.76 | 55.46% | 0 | 0% | 12.19 | 6.74 | 55.29% | 0 | 0% | 12.19 | 6.72 | 55.13% | 0 | 0%
GNA_253731103_Capacity | Central Valley | Fresno | WEST FRESNO 1103 | 253731103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253731104_Capacity | Central Valley | Fresno | WEST FRESNO 1104 | 253731104 | Feeder | None | None | None | 85.89% | 0 | 0% | 12.83 | 10.95 | 85.35% | 0 | 0% | 12.83 | 10.98 | 85.58% | 0 | 0% | 12.83 | 11.02 | 85.89% | 0 | 0% | 12.83 | 11.02 | 85.89% | 0 | 0% | 12.83 | 10.95 | 85.35% | 0 | 0%
GNA_253731109_Capacity | Central Valley | Fresno | WEST FRESNO 1109 | 253731109 | Feeder | Demand Growth | Capacity | 2023 | 131.9% | 3.43 | 31.88% | 10.76 | 12.23 | 113.7% | 1.47 | 13.66% | 10.76 | 12.57 | 116.8% | 1.81 | 16.82% | 10.76 | 13.02 | 121% | 2.26 | 21% | 10.76 | 13.65 | 126.9% | 2.89 | 26.86% | 10.76 | 14.19 | 131.9% | 3.43 | 31.88%
GNA_2537302_Capacity | Central Valley | Fresno | WEST FRESNO BANK 2 | 2537302 | Bank | Demand Growth | Capacity | 2026 | 108.5% | 3.77 | 8.462% | 44.55 | 42.77 | 96% | 0 | 0% | 44.55 | 43.58 | 97.82% | 0 | 0% | 44.55 | 44.64 | 100.2% | 0.09 | 0.202% | 44.55 | 46.22 | 103.7% | 1.67 | 3.749% | 44.55 | 48.32 | 108.5% | 3.77 | 8.462%
GNA_253731105_Capacity | Central Valley | Fresno | WEST FRESNO 1105 | 253731105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253731106_Capacity | Central Valley | Fresno | WEST FRESNO 1106 | 253731106 | Feeder | None | None | None | 55.64% | 0 | 0% | 10.46 | 5.82 | 55.64% | 0 | 0% | 10.46 | 5.79 | 55.35% | 0 | 0% | 10.46 | 5.75 | 54.97% | 0 | 0% | 10.46 | 5.7 | 54.49% | 0 | 0% | 10.46 | 5.65 | 54.02% | 0 | 0%
GNA_253731107_Capacity | Central Valley | Fresno | WEST FRESNO 1107 | 253731107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253731108_Capacity | Central Valley | Fresno | WEST FRESNO 1108 | 253731108 | Feeder | Demand Growth | Capacity | 2026 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253731110_Capacity | Central Valley | Fresno | WEST FRESNO 1110 | 253731110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2537303_Capacity | Central Valley | Fresno | WEST FRESNO BANK 3 | 2537303 | Bank | None | None | None | 56.59% | 0 | 0% | 44.55 | 23.37 | 52.46% | 0 | 0% | 44.55 | 23.42 | 52.57% | 0 | 0% | 44.55 | 24.93 | 55.96% | 0 | 0% | 44.55 | 25.07 | 56.27% | 0 | 0% | 44.55 | 25.21 | 56.59% | 0 | 0%
GNA_253731111_Capacity | Central Valley | Fresno | WEST FRESNO 1111 | 253731111 | Feeder | Demand Growth | Capacity | 2025 | 110.1% | 1.3 | 10.13% | 12.83 | 12.64 | 98.52% | 0 | 0% | 12.83 | 12.65 | 98.6% | 0 | 0% | 12.83 | 14.08 | 109.7% | 1.25 | 9.743% | 12.83 | 14.09 | 109.8% | 1.26 | 9.821% | 12.83 | 14.13 | 110.1% | 1.3 | 10.13%
GNA_253731112_Capacity | Central Valley | Fresno | WEST FRESNO 1112 | 253731112 | Feeder | None | None | None | 87.04% | 0 | 0% | 12.19 | 10.06 | 82.53% | 0 | 0% | 12.19 | 10.09 | 82.77% | 0 | 0% | 12.19 | 10.19 | 83.59% | 0 | 0% | 12.19 | 10.41 | 85.4% | 0 | 0% | 12.19 | 10.61 | 87.04% | 0 | 0%
GNA_2529202_Capacity | Central Valley | Fresno | STONE CORRAL BANK 2 | 2529202 | Bank | None | None | None | 47.74% | 0 | 0% | 12.38 | 5.75 | 46.45% | 0 | 0% | 12.38 | 5.74 | 46.37% | 0 | 0% | 12.38 | 5.73 | 46.28% | 0 | 0% | 12.38 | 5.79 | 46.77% | 0 | 0% | 12.38 | 5.91 | 47.74% | 0 | 0%
GNA_252921108_Capacity | Central Valley | Fresno | STONE CORRAL 1108 | 252921108 | Feeder | None | None | None | 84.55% | 0 | 0% | 6.99 | 5.74 | 82.12% | 0 | 0% | 6.99 | 5.74 | 82.12% | 0 | 0% | 6.99 | 5.73 | 81.97% | 0 | 0% | 6.99 | 5.79 | 82.83% | 0 | 0% | 6.99 | 5.91 | 84.55% | 0 | 0%
GNA_2529203_Capacity | Central Valley | Fresno | STONE CORRAL BANK 3 | 2529203 | Bank | None | None | None | 34.4% | 0 | 0% | 14.36 | 4.94 | 34.4% | 0 | 0% | 14.36 | 4.89 | 34.05% | 0 | 0% | 14.36 | 4.84 | 33.7% | 0 | 0% | 14.36 | 4.79 | 33.36% | 0 | 0% | 14.36 | 4.79 | 33.36% | 0 | 0%
GNA_252921109_Capacity | Central Valley | Fresno | STONE CORRAL 1109 | 252921109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252921110_Capacity | Central Valley | Fresno | STONE CORRAL 1110 | 252921110 | Feeder | None | None | None | 37.01% | 0 | 0% | 10.16 | 3.74 | 36.81% | 0 | 0% | 10.16 | 3.73 | 36.71% | 0 | 0% | 10.16 | 3.73 | 36.71% | 0 | 0% | 10.16 | 3.74 | 36.81% | 0 | 0% | 10.16 | 3.76 | 37.01% | 0 | 0%
GNA_2539601_Capacity | Central Valley | Fresno | BULLARD BANK 1 | 2539601 | Bank | None | None | None | 90.7% | 0 | 0% | 41.3 | 37.4 | 90.56% | 0 | 0% | 41.3 | 37.3 | 90.31% | 0 | 0% | 41.3 | 37.23 | 90.15% | 0 | 0% | 41.3 | 37.33 | 90.39% | 0 | 0% | 41.3 | 37.46 | 90.7% | 0 | 0%
GNA_253962111_Capacity | Central Valley | Fresno | BULLARD 2111 | 253962111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253962112_Capacity | Central Valley | Fresno | BULLARD 2112 | 253962112 | Feeder | None | None | None | 57.78% | 0 | 0% | 21.67 | 12.52 | 57.78% | 0 | 0% | 21.67 | 12.46 | 57.5% | 0 | 0% | 21.67 | 12.42 | 57.31% | 0 | 0% | 21.67 | 12.4 | 57.22% | 0 | 0% | 21.67 | 12.36 | 57.04% | 0 | 0%
GNA_253962114_Capacity | Central Valley | Fresno | BULLARD 2114 | 253962114 | Feeder | None | None | None | 81.2% | 0 | 0% | 20.96 | 16.67 | 79.53% | 0 | 0% | 20.96 | 16.67 | 79.53% | 0 | 0% | 20.96 | 16.73 | 79.82% | 0 | 0% | 20.96 | 16.86 | 80.44% | 0 | 0% | 20.96 | 17.02 | 81.2% | 0 | 0%
GNA_2540803_Capacity | Central Valley | Fresno | CLOVIS BANK 3 | 2540803 | Bank | None | None | None | 87.38% | 0 | 0% | 44.55 | 37.46 | 84.09% | 0 | 0% | 44.55 | 37.52 | 84.22% | 0 | 0% | 44.55 | 38.41 | 86.22% | 0 | 0% | 44.55 | 38.61 | 86.67% | 0 | 0% | 44.55 | 38.93 | 87.38% | 0 | 0%
GNA_254082109_Capacity | Central Valley | Fresno | CLOVIS 2109 | 254082109 | Feeder | None | None | None | 55.19% | 0 | 0% | 21.11 | 11.26 | 53.34% | 0 | 0% | 21.11 | 11.32 | 53.62% | 0 | 0% | 21.11 | 11.45 | 54.24% | 0 | 0% | 21.11 | 11.56 | 54.76% | 0 | 0% | 21.11 | 11.65 | 55.19% | 0 | 0%
GNA_254082110_Capacity | Central Valley | Fresno | CLOVIS 2110 | 254082110 | Feeder | None | None | None | 68.7% | 0 | 0% | 20.96 | 13.11 | 62.55% | 0 | 0% | 20.96 | 13.19 | 62.93% | 0 | 0% | 20.96 | 14.01 | 66.84% | 0 | 0% | 20.96 | 14.14 | 67.46% | 0 | 0% | 20.96 | 14.4 | 68.7% | 0 | 0%
GNA_254082111_Capacity | Central Valley | Fresno | CLOVIS 2111 | 254082111 | Feeder | None | None | None | 77.43% | 0 | 0% | 20.96 | 16.23 | 77.43% | 0 | 0% | 20.96 | 16.16 | 77.1% | 0 | 0% | 20.96 | 16.14 | 77% | 0 | 0% | 20.96 | 16.07 | 76.67% | 0 | 0% | 20.96 | 16.01 | 76.38% | 0 | 0%
GNA_2528501_Capacity | Central Valley | Fresno | PINEDALE BANK 1 | 2528501 | Bank | None | None | None | 94.03% | 0 | 0% | 44.55 | 41.76 | 93.74% | 0 | 0% | 44.55 | 41.49 | 93.13% | 0 | 0% | 44.55 | 41.43 | 93% | 0 | 0% | 44.55 | 41.54 | 93.24% | 0 | 0% | 44.55 | 41.89 | 94.03% | 0 | 0%
GNA_252852101_Capacity | Central Valley | Fresno | PINEDALE 2101 | 252852101 | Feeder | None | None | None | 86.82% | 0 | 0% | 20.48 | 17.54 | 85.64% | 0 | 0% | 20.48 | 17.47 | 85.3% | 0 | 0% | 20.48 | 17.5 | 85.45% | 0 | 0% | 20.48 | 17.58 | 85.84% | 0 | 0% | 20.48 | 17.78 | 86.82% | 0 | 0%
GNA_252852102_Capacity | Central Valley | Fresno | PINEDALE 2102 | 252852102 | Feeder | None | None | None | 80.47% | 0 | 0% | 16.59 | 13.22 | 79.69% | 0 | 0% | 16.59 | 13.05 | 78.66% | 0 | 0% | 16.59 | 12.97 | 78.18% | 0 | 0% | 16.59 | 13.13 | 79.14% | 0 | 0% | 16.59 | 13.35 | 80.47% | 0 | 0%
GNA_252852103_Capacity | Central Valley | Fresno | PINEDALE 2103 | 252852103 | Feeder | None | None | None | 43.82% | 0 | 0% | 21.11 | 9.25 | 43.82% | 0 | 0% | 21.11 | 9.2 | 43.58% | 0 | 0% | 21.11 | 9.17 | 43.44% | 0 | 0% | 21.11 | 9.14 | 43.3% | 0 | 0% | 21.11 | 9.15 | 43.34% | 0 | 0%
GNA_2528502_Capacity | Central Valley | Fresno | PINEDALE BANK 2 | 2528502 | Bank | None | None | None | 97.67% | 0 | 0% | 44.55 | 42.49 | 95.38% | 0 | 0% | 44.55 | 42.63 | 95.69% | 0 | 0% | 44.55 | 42.79 | 96.05% | 0 | 0% | 44.55 | 43.17 | 96.9% | 0 | 0% | 44.55 | 43.51 | 97.67% | 0 | 0%
GNA_252852105_Capacity | Central Valley | Fresno | PINEDALE 2105 | 252852105 | Feeder | None | None | None | 71.92% | 0 | 0% | 20.48 | 14.33 | 69.97% | 0 | 0% | 20.48 | 14.36 | 70.12% | 0 | 0% | 20.48 | 14.4 | 70.31% | 0 | 0% | 20.48 | 14.59 | 71.24% | 0 | 0% | 20.48 | 14.73 | 71.92% | 0 | 0%
GNA_252852106_Capacity | Central Valley | Fresno | PINEDALE 2106 | 252852106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252852107_Capacity | Central Valley | Fresno | PINEDALE 2107 | 252852107 | Feeder | None | None | None | 71.39% | 0 | 0% | 21.11 | 14.82 | 70.2% | 0 | 0% | 21.11 | 14.84 | 70.3% | 0 | 0% | 21.11 | 14.86 | 70.39% | 0 | 0% | 21.11 | 14.97 | 70.91% | 0 | 0% | 21.11 | 15.07 | 71.39% | 0 | 0%
GNA_2528503_Capacity | Central Valley | Fresno | PINEDALE BANK 3 | 2528503 | Bank | None | None | None | 99.57% | 0 | 0% | 44.55 | 43.35 | 97.31% | 0 | 0% | 44.55 | 43.37 | 97.35% | 0 | 0% | 44.55 | 43.72 | 98.14% | 0 | 0% | 44.55 | 44.04 | 98.86% | 0 | 0% | 44.55 | 44.36 | 99.57% | 0 | 0%
GNA_252852109_Capacity | Central Valley | Fresno | PINEDALE 2109 | 252852109 | Feeder | None | None | None | 73.98% | 0 | 0% | 18.37 | 13.59 | 73.98% | 0 | 0% | 18.37 | 13.52 | 73.6% | 0 | 0% | 18.37 | 13.44 | 73.16% | 0 | 0% | 18.37 | 13.38 | 72.84% | 0 | 0% | 18.37 | 13.34 | 72.62% | 0 | 0%
GNA_252852110_Capacity | Central Valley | Fresno | PINEDALE 2110 | 252852110 | Feeder | None | None | None | 92.87% | 0 | 0% | 18.37 | 16.29 | 88.68% | 0 | 0% | 18.37 | 16.32 | 88.84% | 0 | 0% | 18.37 | 16.63 | 90.53% | 0 | 0% | 18.37 | 16.84 | 91.67% | 0 | 0% | 18.37 | 17.06 | 92.87% | 0 | 0%
GNA_252852111_Capacity | Central Valley | Fresno | PINEDALE 2111 | 252852111 | Feeder | None | None | None | 75.88% | 0 | 0% | 18.37 | 13.57 | 73.87% | 0 | 0% | 18.37 | 13.61 | 74.09% | 0 | 0% | 18.37 | 13.69 | 74.52% | 0 | 0% | 18.37 | 13.82 | 75.23% | 0 | 0% | 18.37 | 13.94 | 75.88% | 0 | 0%
GNA_2552501_Capacity | Central Valley | Fresno | RIVER ROCK BANK 1 | 2552501 | Bank | None | None | None | 8.658% | 0 | 0% | 6.93 | 0.11 | 1.587% | 0 | 0% | 6.93 | 0.23 | 3.319% | 0 | 0% | 6.93 | 0.34 | 4.906% | 0 | 0% | 6.93 | 0.48 | 6.926% | 0 | 0% | 6.93 | 0.6 | 8.658% | 0 | 0%
GNA_255251101_Capacity | Central Valley | Fresno | RIVER ROCK 1101 | 255251101 | Feeder | None | None | None | 10.97% | 0 | 0% | 5.47 | 0.11 | 2.011% | 0 | 0% | 5.47 | 0.23 | 4.205% | 0 | 0% | 5.47 | 0.34 | 6.216% | 0 | 0% | 5.47 | 0.48 | 8.775% | 0 | 0% | 5.47 | 0.6 | 10.97% | 0 | 0%
GNA_2520603_Capacity | Central Valley | Fresno | SHEPHERD BANK 3 | 2520603 | Bank | None | None | None | 91.96% | 0 | 0% | 44.55 | 37.55 | 84.29% | 0 | 0% | 44.55 | 40.97 | 91.96% | 0 | 0% | 44.55 | 40.71 | 91.38% | 0 | 0% | 44.55 | 40.11 | 90.03% | 0 | 0% | 44.55 | 39.5 | 88.66% | 0 | 0%
GNA_252062109_Capacity | Central Valley | Fresno | SHEPHERD 2109 | 252062109 | Feeder | None | None | None | 36.23% | 0 | 0% | 22.22 | 7.32 | 32.94% | 0 | 0% | 22.22 | 7.74 | 34.83% | 0 | 0% | 22.22 | 8.05 | 36.23% | 0 | 0% | 22.22 | 7.98 | 35.91% | 0 | 0% | 22.22 | 7.93 | 35.69% | 0 | 0%
GNA_252062110_Capacity | Central Valley | Fresno | SHEPHERD 2110 | 252062110 | Feeder | None | None | None | 66.29% | 0 | 0% | 22.22 | 14.73 | 66.29% | 0 | 0% | 22.22 | 14.55 | 65.48% | 0 | 0% | 22.22 | 14.33 | 64.49% | 0 | 0% | 22.22 | 14.13 | 63.59% | 0 | 0% | 22.22 | 13.9 | 62.56% | 0 | 0%
GNA_252062111_Capacity | Central Valley | Fresno | SHEPHERD 2111 | 252062111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252062112_Capacity | Central Valley | Fresno | SHEPHERD 2112 | 252062112 | Feeder | Demand Growth | Capacity | 2023 | 101.2% | 0.11 | 1.232% | 8.93 | 9.04 | 101.2% | 0.11 | 1.232% | 8.93 | 8.82 | 98.77% | 0 | 0% | 8.93 | 8.65 | 96.86% | 0 | 0% | 8.93 | 8.44 | 94.51% | 0 | 0% | 8.93 | 8.27 | 92.61% | 0 | 0%
GNA_2552901_Capacity | Central Valley | Fresno | WOODWARD BANK 1 | 2552901 | Bank | None | None | None | 94.86% | 0 | 0% | 44.55 | 42.26 | 94.86% | 0 | 0% | 44.55 | 39.66 | 89.02% | 0 | 0% | 44.55 | 39.7 | 89.11% | 0 | 0% | 44.55 | 39.91 | 89.58% | 0 | 0% | 44.55 | 40.21 | 90.26% | 0 | 0%
GNA_255292101_Capacity | Central Valley | Fresno | WOODWARD 2101 | 255292101 | Feeder | None | None | None | 78.02% | 0 | 0% | 21.11 | 16.47 | 78.02% | 0 | 0% | 21.11 | 13.93 | 65.99% | 0 | 0% | 21.11 | 13.97 | 66.18% | 0 | 0% | 21.11 | 14.06 | 66.6% | 0 | 0% | 21.11 | 14.15 | 67.03% | 0 | 0%
GNA_255292102_Capacity | Central Valley | Fresno | WOODWARD 2102 | 255292102 | Feeder | None | None | None | 76.41% | 0 | 0% | 19.63 | 15 | 76.41% | 0 | 0% | 19.63 | 14.87 | 75.75% | 0 | 0% | 19.63 | 14.76 | 75.19% | 0 | 0% | 19.63 | 14.8 | 75.39% | 0 | 0% | 19.63 | 14.94 | 76.11% | 0 | 0%
GNA_255292103_Capacity | Central Valley | Fresno | WOODWARD 2103 | 255292103 | Feeder | None | None | None | 40.25% | 0 | 0% | 20.15 | 7.7 | 38.21% | 0 | 0% | 20.15 | 7.76 | 38.51% | 0 | 0% | 20.15 | 7.87 | 39.06% | 0 | 0% | 20.15 | 7.98 | 39.6% | 0 | 0% | 20.15 | 8.11 | 40.25% | 0 | 0%
GNA_2552902_Capacity | Central Valley | Fresno | WOODWARD BANK 2 | 2552902 | Bank | None | None | None | 89.18% | 0 | 0% | 44.55 | 37.95 | 85.19% | 0 | 0% | 44.55 | 38.24 | 85.84% | 0 | 0% | 44.55 | 38.58 | 86.6% | 0 | 0% | 44.55 | 39.11 | 87.79% | 0 | 0% | 44.55 | 39.73 | 89.18% | 0 | 0%
GNA_255292104_Capacity | Central Valley | Fresno | WOODWARD 2104 | 255292104 | Feeder | None | None | None | 81.81% | 0 | 0% | 21.11 | 16.56 | 78.45% | 0 | 0% | 21.11 | 16.67 | 78.97% | 0 | 0% | 21.11 | 16.81 | 79.63% | 0 | 0% | 21.11 | 17 | 80.53% | 0 | 0% | 21.11 | 17.27 | 81.81% | 0 | 0%
GNA_255292105_Capacity | Central Valley | Fresno | WOODWARD 2105 | 255292105 | Feeder | None | None | None | 71.93% | 0 | 0% | 19.63 | 13.52 | 68.87% | 0 | 0% | 19.63 | 13.63 | 69.43% | 0 | 0% | 19.63 | 13.74 | 69.99% | 0 | 0% | 19.63 | 13.94 | 71.01% | 0 | 0% | 19.63 | 14.12 | 71.93% | 0 | 0%
GNA_255292106_Capacity | Central Valley | Fresno | WOODWARD 2106 | 255292106 | Feeder | None | None | None | 59.45% | 0 | 0% | 17.19 | 9.69 | 56.37% | 0 | 0% | 17.19 | 9.8 | 57.01% | 0 | 0% | 17.19 | 9.91 | 57.65% | 0 | 0% | 17.19 | 10.06 | 58.52% | 0 | 0% | 17.19 | 10.22 | 59.45% | 0 | 0%
GNA_2552903_Capacity | Central Valley | Fresno | WOODWARD BANK 3 | 2552903 | Bank | None | None | None | 80.99% | 0 | 0% | 44.55 | 32.55 | 73.06% | 0 | 0% | 44.55 | 34.42 | 77.26% | 0 | 0% | 44.55 | 34.8 | 78.11% | 0 | 0% | 44.55 | 35.48 | 79.64% | 0 | 0% | 44.55 | 36.08 | 80.99% | 0 | 0%
GNA_255292107_Capacity | Central Valley | Fresno | WOODWARD 2107 | 255292107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_255292108_Capacity | Central Valley | Fresno | WOODWARD 2108 | 255292108 | Feeder | None | None | None | 87.54% | 0 | 0% | 21.11 | 16.58 | 78.54% | 0 | 0% | 21.11 | 18.09 | 85.69% | 0 | 0% | 21.11 | 18.22 | 86.31% | 0 | 0% | 21.11 | 18.35 | 86.93% | 0 | 0% | 21.11 | 18.48 | 87.54% | 0 | 0%
GNA_255292109_Capacity | Central Valley | Fresno | WOODWARD 2109 | 255292109 | Feeder | None | None | None | 64.13% | 0 | 0% | 19.74 | 12.38 | 62.72% | 0 | 0% | 19.74 | 12.39 | 62.77% | 0 | 0% | 19.74 | 12.35 | 62.56% | 0 | 0% | 19.74 | 12.48 | 63.22% | 0 | 0% | 19.74 | 12.66 | 64.13% | 0 | 0%
GNA_1920201_Capacity | North Coast | Humboldt | ARCATA BANK 1 | 1920201 | Bank | None | None | None | 40.44% | 0 | 0% | 29.7 | 10.26 | 34.55% | 0 | 0% | 29.7 | 10.65 | 35.86% | 0 | 0% | 29.7 | 11.08 | 37.31% | 0 | 0% | 29.7 | 11.53 | 38.82% | 0 | 0% | 29.7 | 12.01 | 40.44% | 0 | 0%
GNA_192021105_Capacity | North Coast | Humboldt | ARCATA 1105 | 192021105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192021106_Capacity | North Coast | Humboldt | ARCATA 1106 | 192021106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192021123_Capacity | North Coast | Humboldt | ARCATA 1123 | 192021123 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1920202_Capacity | North Coast | Humboldt | ARCATA BANK 2 | 1920202 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192021121_Capacity | North Coast | Humboldt | ARCATA 1121 | 192021121 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192021122_Capacity | North Coast | Humboldt | ARCATA 1122 | 192021122 | Feeder | None | None | None | 81.56% | 0 | 0% | 10.52 | 7.08 | 67.3% | 0 | 0% | 10.52 | 7.35 | 69.87% | 0 | 0% | 10.52 | 7.58 | 72.05% | 0 | 0% | 10.52 | 8.1 | 77% | 0 | 0% | 10.52 | 8.58 | 81.56% | 0 | 0%
GNA_1921801_Capacity | North Coast | Humboldt | BLUE LAKE BANK 1 | 1921801 | Bank | None | None | None | 37.41% | 0 | 0% | 11.76 | 4.2 | 35.71% | 0 | 0% | 11.76 | 4.25 | 36.14% | 0 | 0% | 11.76 | 4.28 | 36.39% | 0 | 0% | 11.76 | 4.33 | 36.82% | 0 | 0% | 11.76 | 4.4 | 37.41% | 0 | 0%
GNA_192181101_Capacity | North Coast | Humboldt | BLUE LAKE 1101 | 192181101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192181102_Capacity | North Coast | Humboldt | BLUE LAKE 1102 | 192181102 | Feeder | None | None | None | 35.27% | 0 | 0% | 10.69 | 3.58 | 33.49% | 0 | 0% | 10.69 | 3.62 | 33.86% | 0 | 0% | 10.69 | 3.65 | 34.14% | 0 | 0% | 10.69 | 3.7 | 34.61% | 0 | 0% | 10.69 | 3.77 | 35.27% | 0 | 0%
GNA_1923901_Capacity | North Coast | Humboldt | JANES CREEK BANK 1 | 1923901 | Bank | None | None | None | 62.07% | 0 | 0% | 9.28 | 5.36 | 57.76% | 0 | 0% | 9.28 | 5.42 | 58.41% | 0 | 0% | 9.28 | 5.46 | 58.84% | 0 | 0% | 9.28 | 5.55 | 59.81% | 0 | 0% | 9.28 | 5.76 | 62.07% | 0 | 0%
GNA_192391101_Capacity | North Coast | Humboldt | JANES CREEK 1101 | 192391101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192391102_Capacity | North Coast | Humboldt | JANES CREEK 1102 | 192391102 | Feeder | None | None | None | 57.79% | 0 | 0% | 5.71 | 3.24 | 56.74% | 0 | 0% | 5.71 | 3.22 | 56.39% | 0 | 0% | 5.71 | 3.21 | 56.22% | 0 | 0% | 5.71 | 3.23 | 56.57% | 0 | 0% | 5.71 | 3.3 | 57.79% | 0 | 0%
GNA_1923902_Capacity | North Coast | Humboldt | JANES CREEK BANK 2 | 1923902 | Bank | None | None | None | 74.8% | 0 | 0% | 12.5 | 8.85 | 70.8% | 0 | 0% | 12.5 | 8.95 | 71.6% | 0 | 0% | 12.5 | 9.05 | 72.4% | 0 | 0% | 12.5 | 9.21 | 73.68% | 0 | 0% | 12.5 | 9.35 | 74.8% | 0 | 0%
GNA_192391103_Capacity | North Coast | Humboldt | JANES CREEK 1103 | 192391103 | Feeder | None | None | None | 73.81% | 0 | 0% | 10.69 | 7.43 | 69.5% | 0 | 0% | 10.69 | 7.53 | 70.44% | 0 | 0% | 10.69 | 7.62 | 71.28% | 0 | 0% | 10.69 | 7.77 | 72.68% | 0 | 0% | 10.69 | 7.89 | 73.81% | 0 | 0%
GNA_192391104_Capacity | North Coast | Humboldt | JANES CREEK 1104 | 192391104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1923601_Capacity | North Coast | Humboldt | BIG LAGOON BANK 1 | 1923601 | Bank | None | None | None | 12.84% | 0 | 0% | 1.48 | 0.19 | 12.84% | 0 | 0% | 12.5 | 0.19 | 1.52% | 0 | 0% | 12.5 | 0.19 | 1.52% | 0 | 0% | 12.5 | 0.19 | 1.52% | 0 | 0% | 12.5 | 0.19 | 1.52% | 0 | 0%
GNA_192361101_Capacity | North Coast | Humboldt | BIG LAGOON 1101 | 192361101 | Feeder | None | None | None | 8.559% | 0 | 0% | 2.22 | 0.19 | 8.559% | 0 | 0% | 2.22 | 0.19 | 8.559% | 0 | 0% | 2.22 | 0.19 | 8.559% | 0 | 0% | 2.22 | 0.19 | 8.559% | 0 | 0% | 2.22 | 0.19 | 8.559% | 0 | 0%
GNA_1922601_Capacity | North Coast | Humboldt | ORICK BANK 1 | 1922601 | Bank | None | None | None | 42.79% | 0 | 0% | 4.23 | 1.72 | 40.66% | 0 | 0% | 4.23 | 1.76 | 41.61% | 0 | 0% | 4.23 | 1.76 | 41.61% | 0 | 0% | 4.23 | 1.81 | 42.79% | 0 | 0% | 4.23 | 1.81 | 42.79% | 0 | 0%
GNA_192261101_Capacity | North Coast | Humboldt | ORICK 1101 | 192261101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192261102_Capacity | North Coast | Humboldt | ORICK 1102 | 192261102 | Feeder | None | None | None | 30.3% | 0 | 0% | 4.06 | 1.23 | 30.3% | 0 | 0% | 4.06 | 1.22 | 30.05% | 0 | 0% | 4.06 | 1.2 | 29.56% | 0 | 0% | 4.06 | 1.21 | 29.8% | 0 | 0% | 4.06 | 1.23 | 30.3% | 0 | 0%
GNA_1922301_Capacity | North Coast | Humboldt | TRINIDAD BANK 1 | 1922301 | Bank | None | None | None | 45.78% | 0 | 0% | 8.3 | 3.35 | 40.36% | 0 | 0% | 8.3 | 3.46 | 41.69% | 0 | 0% | 8.3 | 3.55 | 42.77% | 0 | 0% | 8.3 | 3.68 | 44.34% | 0 | 0% | 8.3 | 3.8 | 45.78% | 0 | 0%
GNA_192231101_Capacity | North Coast | Humboldt | TRINIDAD 1101 | 192231101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192231102_Capacity | North Coast | Humboldt | TRINIDAD 1102 | 192231102 | Feeder | None | None | None | 50.23% | 0 | 0% | 4.3 | 1.93 | 44.88% | 0 | 0% | 4.3 | 1.99 | 46.28% | 0 | 0% | 4.3 | 2.03 | 47.21% | 0 | 0% | 4.3 | 2.11 | 49.07% | 0 | 0% | 4.3 | 2.16 | 50.23% | 0 | 0%
GNA_1924602_Capacity | North Coast | Humboldt | BRIDGEVILLE BANK 2 | 1924602 | Bank | None | None | None | 83.69% | 0 | 0% | 5.64 | 3.68 | 65.25% | 0 | 0% | 5.64 | 4.68 | 82.98% | 0 | 0% | 5.64 | 4.69 | 83.16% | 0 | 0% | 5.64 | 4.7 | 83.33% | 0 | 0% | 5.64 | 4.72 | 83.69% | 0 | 0%
GNA_192461101_Capacity | North Coast | Humboldt | BRIDGEVILLE 1101 | 192461101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192461102_Capacity | North Coast | Humboldt | BRIDGEVILLE 1102 | 192461102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1924101_Capacity | North Coast | Humboldt | LOW GAP BANK 1 | 1924101 | Bank | None | None | None | 57.43% | 0 | 0% | 2.96 | 1.7 | 57.43% | 0 | 0% | 2.96 | 1.68 | 56.76% | 0 | 0% | 2.96 | 1.67 | 56.42% | 0 | 0% | 2.96 | 1.67 | 56.42% | 0 | 0% | 2.96 | 1.7 | 57.43% | 0 | 0%
GNA_192411101_Capacity | North Coast | Humboldt | LOW GAP 1101 | 192411101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0433601_Capacity | North Coast | Humboldt | HIGHLANDS BANK 1 | 433601 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043361102_Capacity | North Coast | Humboldt | HIGHLANDS 1102 | 43361102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043361103_Capacity | North Coast | Humboldt | HIGHLANDS 1103 | 43361103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0433602_Capacity | North Coast | Humboldt | HIGHLANDS BANK 2 | 433602 | Bank | None | None | None | 31.11% | 0 | 0% | 29.7 | 9.24 | 31.11% | 0 | 0% | 29.7 | 9.19 | 30.94% | 0 | 0% | 29.7 | 9.18 | 30.91% | 0 | 0% | 29.7 | 9.17 | 30.88% | 0 | 0% | 29.7 | 9.2 | 30.98% | 0 | 0%
GNA_043361104_Capacity | North Coast | Humboldt | HIGHLANDS 1104 | 43361104 | Feeder | None | None | None | 72.8% | 0 | 0% | 12.83 | 9.34 | 72.8% | 0 | 0% | 12.83 | 9.3 | 72.49% | 0 | 0% | 12.83 | 9.28 | 72.33% | 0 | 0% | 12.83 | 9.27 | 72.25% | 0 | 0% | 12.83 | 9.3 | 72.49% | 0 | 0%
GNA_0431901_Capacity | North Coast | Humboldt | REDBUD BANK 1 | 431901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043191101_Capacity | North Coast | Humboldt | REDBUD 1101 | 43191101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0431903_Capacity | North Coast | Humboldt | REDBUD BANK 3 | 431903 | Bank | None | None | None | 73.71% | 0 | 0% | 12.4 | 7.09 | 57.18% | 0 | 0% | 12.4 | 7.18 | 57.9% | 0 | 0% | 12.4 | 8.79 | 70.89% | 0 | 0% | 12.4 | 8.93 | 72.02% | 0 | 0% | 12.4 | 9.14 | 73.71% | 0 | 0%
GNA_043191102_Capacity | North Coast | Humboldt | REDBUD 1102 | 43191102 | Feeder | None | None | None | 87.86% | 0 | 0% | 10.46 | 7.15 | 68.36% | 0 | 0% | 10.46 | 7.24 | 69.22% | 0 | 0% | 10.46 | 8.84 | 84.51% | 0 | 0% | 10.46 | 8.99 | 85.95% | 0 | 0% | 10.46 | 9.19 | 87.86% | 0 | 0%
GNA_0421401_Capacity | North Coast | Humboldt | CLEAR LAKE BANK 1 | 421401 | Bank | Demand Growth | Capacity | 2024 | 121.1% | 1.96 | 21.14% | 9.27 | 8.92 | 96.22% | 0 | 0% | 9.27 | 11.21 | 120.9% | 1.94 | 20.93% | 9.27 | 11.2 | 120.8% | 1.93 | 20.82% | 9.27 | 11.2 | 120.8% | 1.93 | 20.82% | 9.27 | 11.23 | 121.1% | 1.96 | 21.14%
GNA_042141101_Capacity | North Coast | Humboldt | CLEAR LAKE 1101 | 42141101 | Feeder | None | None | None | 97% | 0 | 0% | 11.67 | 9.01 | 77.21% | 0 | 0% | 11.67 | 11.3 | 96.83% | 0 | 0% | 11.67 | 11.29 | 96.74% | 0 | 0% | 11.67 | 11.29 | 96.74% | 0 | 0% | 11.67 | 11.32 | 97% | 0 | 0%
GNA_0421402_Capacity | North Coast | Humboldt | CLEAR LAKE BANK 2 | 421402 | Bank | None | None | None | 83.33% | 0 | 0% | 9.9 | 7.9 | 79.8% | 0 | 0% | 9.9 | 8.22 | 83.03% | 0 | 0% | 9.9 | 8.21 | 82.93% | 0 | 0% | 9.9 | 8.22 | 83.03% | 0 | 0% | 9.9 | 8.25 | 83.33% | 0 | 0%
GNA_042141102_Capacity | North Coast | Humboldt | CLEAR LAKE 1102 | 42141102 | Feeder | None | None | None | 71.81% | 0 | 0% | 11.67 | 8.03 | 68.81% | 0 | 0% | 11.67 | 8.35 | 71.55% | 0 | 0% | 11.67 | 8.34 | 71.47% | 0 | 0% | 11.67 | 8.35 | 71.55% | 0 | 0% | 11.67 | 8.38 | 71.81% | 0 | 0%
GNA_0432101_Capacity | North Coast | Humboldt | HARTLEY BANK 1 | 432101 | Bank | None | None | None | 77.1% | 0 | 0% | 12.4 | 9.56 | 77.1% | 0 | 0% | 12.4 | 9.42 | 75.97% | 0 | 0% | 12.4 | 9.22 | 74.35% | 0 | 0% | 12.4 | 9.22 | 74.35% | 0 | 0% | 12.4 | 9.31 | 75.08% | 0 | 0%
GNA_043211101_Capacity | North Coast | Humboldt | HARTLEY 1101 | 43211101 | Feeder | None | None | None | 85.31% | 0 | 0% | 10.69 | 9.12 | 85.31% | 0 | 0% | 10.69 | 8.98 | 84% | 0 | 0% | 10.69 | 8.79 | 82.23% | 0 | 0% | 10.69 | 8.8 | 82.32% | 0 | 0% | 10.69 | 8.9 | 83.26% | 0 | 0%
GNA_0432102_Capacity | North Coast | Humboldt | HARTLEY BANK 2 | 432102 | Bank | None | None | None | 92.9% | 0 | 0% | 6.2 | 5.32 | 85.81% | 0 | 0% | 6.2 | 5.42 | 87.42% | 0 | 0% | 6.2 | 5.51 | 88.87% | 0 | 0% | 6.2 | 5.61 | 90.48% | 0 | 0% | 6.2 | 5.76 | 92.9% | 0 | 0%
GNA_043211102_Capacity | North Coast | Humboldt | HARTLEY 1102 | 43211102 | Feeder | None | None | None | 73.19% | 0 | 0% | 8.13 | 5.51 | 67.77% | 0 | 0% | 8.13 | 5.61 | 69% | 0 | 0% | 8.13 | 5.7 | 70.11% | 0 | 0% | 8.13 | 5.81 | 71.46% | 0 | 0% | 8.13 | 5.95 | 73.19% | 0 | 0%
GNA_0433102_Capacity | North Coast | Humboldt | KONOCTI BANK 2 | 433102 | Bank | Demand Growth | Capacity | 2023 | 104.3% | 0.45 | 4.327% | 10.4 | 10.73 | 103.2% | 0.33 | 3.173% | 10.4 | 10.73 | 103.2% | 0.33 | 3.173% | 10.4 | 10.72 | 103.1% | 0.32 | 3.077% | 10.4 | 10.77 | 103.6% | 0.37 | 3.558% | 10.4 | 10.85 | 104.3% | 0.45 | 4.327%
GNA_043311102_Capacity | North Coast | Humboldt | KONOCTI 1102 | 43311102 | Feeder | Demand Growth | Capacity | 2027 | 101.2% | 0.13 | 1.216% | 10.69 | 10.7 | 100.1% | 0.01 | 0.09355% | 10.69 | 10.7 | 100.1% | 0.01 | 0.09355% | 10.69 | 10.7 | 100.1% | 0.01 | 0.09355% | 10.69 | 10.74 | 100.5% | 0.05 | 0.4677% | 10.69 | 10.82 | 101.2% | 0.13 | 1.216%
GNA_0433103_Capacity | North Coast | Humboldt | KONOCTI BANK 3 | 433103 | Bank | None | None | None | 56.54% | 0 | 0% | 12.38 | 6.91 | 55.82% | 0 | 0% | 12.38 | 6.87 | 55.49% | 0 | 0% | 12.38 | 6.87 | 55.49% | 0 | 0% | 12.38 | 6.92 | 55.9% | 0 | 0% | 12.38 | 7 | 56.54% | 0 | 0%
GNA_043311108_Capacity | North Coast | Humboldt | KONOCTI 1108 | 43311108 | Feeder | None | None | None | 70.36% | 0 | 0% | 10.46 | 7.27 | 69.5% | 0 | 0% | 10.46 | 7.22 | 69.02% | 0 | 0% | 10.46 | 7.22 | 69.02% | 0 | 0% | 10.46 | 7.27 | 69.5% | 0 | 0% | 10.46 | 7.36 | 70.36% | 0 | 0%
GNA_0433501_Capacity | North Coast | Humboldt | LUCERNE BANK 1 | 433501 | Bank | None | None | None | 63.47% | 0 | 0% | 12.4 | 7.46 | 60.16% | 0 | 0% | 12.4 | 7.57 | 61.05% | 0 | 0% | 12.4 | 7.66 | 61.77% | 0 | 0% | 12.4 | 7.76 | 62.58% | 0 | 0% | 12.4 | 7.87 | 63.47% | 0 | 0%
GNA_043351103_Capacity | North Coast | Humboldt | LUCERNE 1103 | 43351103 | Feeder | None | None | None | 73.23% | 0 | 0% | 10.76 | 7.46 | 69.33% | 0 | 0% | 10.76 | 7.58 | 70.45% | 0 | 0% | 10.76 | 7.66 | 71.19% | 0 | 0% | 10.76 | 7.77 | 72.21% | 0 | 0% | 10.76 | 7.88 | 73.23% | 0 | 0%
GNA_0433502_Capacity | North Coast | Humboldt | LUCERNE BANK 2 | 433502 | Bank | None | None | None | 54.48% | 0 | 0% | 15.84 | 8.18 | 51.64% | 0 | 0% | 15.84 | 8.27 | 52.21% | 0 | 0% | 15.84 | 8.35 | 52.71% | 0 | 0% | 15.84 | 8.46 | 53.41% | 0 | 0% | 15.84 | 8.63 | 54.48% | 0 | 0%
GNA_043351106_Capacity | North Coast | Humboldt | LUCERNE 1106 | 43351106 | Feeder | None | None | None | 79% | 0 | 0% | 10.76 | 8.05 | 74.81% | 0 | 0% | 10.76 | 8.14 | 75.65% | 0 | 0% | 10.76 | 8.21 | 76.3% | 0 | 0% | 10.76 | 8.33 | 77.42% | 0 | 0% | 10.76 | 8.5 | 79% | 0 | 0%
GNA_0428701_Capacity | North Coast | Humboldt | UPPER LAKE BANK 1 | 428701 | Bank | Demand Growth | Capacity | 2023 | 124.1% | 0.78 | 24.07% | 3.24 | 3.77 | 116.4% | 0.53 | 16.36% | 3.24 | 3.98 | 122.8% | 0.74 | 22.84% | 3.24 | 3.97 | 122.5% | 0.73 | 22.53% | 3.24 | 3.98 | 122.8% | 0.74 | 22.84% | 3.24 | 4.02 | 124.1% | 0.78 | 24.07%
GNA_042871101_Capacity | North Coast | Humboldt | UPPER LAKE 1101 | 42871101 | Feeder | None | None | None | 77.2% | 0 | 0% | 5.35 | 3.89 | 72.71% | 0 | 0% | 5.35 | 4.09 | 76.45% | 0 | 0% | 5.35 | 4.08 | 76.26% | 0 | 0% | 5.35 | 4.09 | 76.45% | 0 | 0% | 5.35 | 4.13 | 77.2% | 0 | 0%
GNA_1924301_Capacity | North Coast | Humboldt | HARRIS BANK 1 | 1924301 | Bank | None | None | None | 42.8% | 0 | 0% | 15.84 | 5.99 | 37.82% | 0 | 0% | 15.84 | 6.13 | 38.7% | 0 | 0% | 15.84 | 6.27 | 39.58% | 0 | 0% | 15.84 | 6.51 | 41.1% | 0 | 0% | 15.84 | 6.78 | 42.8% | 0 | 0%
GNA_192431109_Capacity | North Coast | Humboldt | HARRIS 1109 | 192431109 | Feeder | None | None | None | 66.7% | 0 | 0% | 10.69 | 6.34 | 59.31% | 0 | 0% | 10.69 | 6.47 | 60.52% | 0 | 0% | 10.69 | 6.61 | 61.83% | 0 | 0% | 10.69 | 6.85 | 64.08% | 0 | 0% | 10.69 | 7.13 | 66.7% | 0 | 0%
GNA_1924302_Capacity | North Coast | Humboldt | HARRIS BANK 2 | 1924302 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192431108_Capacity | North Coast | Humboldt | HARRIS 1108 | 192431108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1923411_Capacity | North Coast | Humboldt | HUM BAY BANK NO. BANK 11 | 1923411 | Bank | None | None | None | 56.44% | 0 | 0% | 10.4 | 5.18 | 49.81% | 0 | 0% | 10.4 | 5.3 | 50.96% | 0 | 0% | 10.4 | 5.42 | 52.12% | 0 | 0% | 10.4 | 5.62 | 54.04% | 0 | 0% | 10.4 | 5.87 | 56.44% | 0 | 0%
GNA_192341101_Capacity | North Coast | Humboldt | HUMBOLDT BAY 1101 | 192341101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192341102_Capacity | North Coast | Humboldt | HUMBOLDT BAY 1102 | 192341102 | Feeder | None | None | None | 61.65% | 0 | 0% | 6.91 | 3.99 | 57.74% | 0 | 0% | 6.91 | 4.02 | 58.18% | 0 | 0% | 6.91 | 4.05 | 58.61% | 0 | 0% | 6.91 | 4.12 | 59.62% | 0 | 0% | 6.91 | 4.26 | 61.65% | 0 | 0%
GNA_1921201_Capacity | North Coast | Humboldt | EUREKA A BANK 1 | 1921201 | Bank | None | None | None | 79.6% | 0 | 0% | 12.4 | 9.56 | 77.1% | 0 | 0% | 12.4 | 9.62 | 77.58% | 0 | 0% | 12.4 | 9.67 | 77.98% | 0 | 0% | 12.4 | 9.78 | 78.87% | 0 | 0% | 12.4 | 9.87 | 79.6% | 0 | 0%
GNA_192121103_Capacity | North Coast | Humboldt | EUREKA A 1103 | 192121103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192121106_Capacity | North Coast | Humboldt | EUREKA A 1106 | 192121106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192121107_Capacity | North Coast | Humboldt | EUREKA A 1107 | 192121107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1923301_Capacity | North Coast | Humboldt | EUREKA E BANK 1 | 1923301 | Bank | None | None | None | 64.81% | 0 | 0% | 19.75 | 9.18 | 46.48% | 0 | 0% | 19.75 | 9.35 | 47.34% | 0 | 0% | 19.75 | 9.5 | 48.1% | 0 | 0% | 19.75 | 10.66 | 53.97% | 0 | 0% | 19.75 | 12.8 | 64.81% | 0 | 0%
GNA_192331101_Capacity | North Coast | Humboldt | EUREKA E 1101 | 192331101 | Feeder | None | None | None | 32.53% | 0 | 0% | 9.99 | 3.12 | 31.23% | 0 | 0% | 9.99 | 3.12 | 31.23% | 0 | 0% | 9.99 | 3.13 | 31.33% | 0 | 0% | 9.99 | 3.18 | 31.83% | 0 | 0% | 9.99 | 3.25 | 32.53% | 0 | 0%
GNA_192331104_Capacity | North Coast | Humboldt | EUREKA E 1104 | 192331104 | Feeder | None | None | None | 52% | 0 | 0% | 10.52 | 3.83 | 36.41% | 0 | 0% | 10.52 | 3.86 | 36.69% | 0 | 0% | 10.52 | 3.91 | 37.17% | 0 | 0% | 10.52 | 4.55 | 43.25% | 0 | 0% | 10.52 | 5.47 | 52% | 0 | 0%
GNA_192331105_Capacity | North Coast | Humboldt | EUREKA E 1105 | 192331105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1924501_Capacity | North Coast | Humboldt | FAIRHAVEN BANK 1 | 1924501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192451103_Capacity | North Coast | Humboldt | FAIRHAVEN 1103 | 192451103 | Feeder | None | None | None | 12.44% | 0 | 0% | 10.69 | 1.24 | 11.6% | 0 | 0% | 10.69 | 1.25 | 11.69% | 0 | 0% | 10.69 | 1.28 | 11.97% | 0 | 0% | 10.69 | 1.29 | 12.07% | 0 | 0% | 10.69 | 1.33 | 12.44% | 0 | 0%
GNA_192451104_Capacity | North Coast | Humboldt | FAIRHAVEN 1104 | 192451104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1923201_Capacity | North Coast | Humboldt | FORT SEWARD BANK 1 | 1923201 | Bank | None | None | None | 25.49% | 0 | 0% | 5.61 | 1.4 | 24.96% | 0 | 0% | 5.61 | 1.39 | 24.78% | 0 | 0% | 5.61 | 1.4 | 24.96% | 0 | 0% | 5.61 | 1.42 | 25.31% | 0 | 0% | 5.61 | 1.43 | 25.49% | 0 | 0%
GNA_192321121_Capacity | North Coast | Humboldt | FORT SEWARD 1121 | 192321121 | Feeder | None | None | None | 34.27% | 0 | 0% | 3.21 | 1.09 | 33.96% | 0 | 0% | 3.21 | 1.09 | 33.96% | 0 | 0% | 3.21 | 1.09 | 33.96% | 0 | 0% | 3.21 | 1.09 | 33.96% | 0 | 0% | 3.21 | 1.1 | 34.27% | 0 | 0%
GNA_192321122_Capacity | North Coast | Humboldt | FORT SEWARD 1122 | 192321122 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1923101_Capacity | North Coast | Humboldt | FRUITLAND BANK 1 | 1923101 | Bank | Demand Growth | Capacity | 2025 | 128.3% | 1.59 | 28.34% | 5.61 | 4.29 | 76.47% | 0 | 0% | 5.61 | 4.75 | 84.67% | 0 | 0% | 5.61 | 6.85 | 122.1% | 1.24 | 22.1% | 5.61 | 7.03 | 125.3% | 1.42 | 25.31% | 5.61 | 7.2 | 128.3% | 1.59 | 28.34%
GNA_192311141_Capacity | North Coast | Humboldt | FRUITLAND 1141 | 192311141 | Feeder | None | None | None | 21.02% | 0 | 0% | 6.09 | 0.82 | 13.46% | 0 | 0% | 6.09 | 0.93 | 15.27% | 0 | 0% | 6.09 | 1.04 | 17.08% | 0 | 0% | 6.09 | 1.16 | 19.05% | 0 | 0% | 6.09 | 1.28 | 21.02% | 0 | 0%
GNA_192311142_Capacity | North Coast | Humboldt | FRUITLAND 1142 | 192311142 | Feeder | None | None | None | 99.18% | 0 | 0% | 6.09 | 3.73 | 61.25% | 0 | 0% | 6.09 | 3.95 | 64.86% | 0 | 0% | 6.09 | 5.93 | 97.37% | 0 | 0% | 6.09 | 6 | 98.52% | 0 | 0% | 6.09 | 6.04 | 99.18% | 0 | 0%
GNA_1922201_Capacity | North Coast | Humboldt | GARBERVILLE BANK 1 | 1922201 | Bank | Demand Growth | Capacity | 2023 | 176.1% | 9.38 | 76.14% | 12.32 | 12.94 | 105% | 0.62 | 5.032% | 12.32 | 17.17 | 139.4% | 4.85 | 39.37% | 12.32 | 21.26 | 172.6% | 8.94 | 72.56% | 12.32 | 21.47 | 174.3% | 9.15 | 74.27% | 12.32 | 21.7 | 176.1% | 9.38 | 76.14%
GNA_192221101_Capacity | North Coast | Humboldt | GARBERVILLE 1101 | 192221101 | Feeder | None | None | None | 95.33% | 0 | 0% | 8.13 | 4.22 | 51.91% | 0 | 0% | 8.13 | 7.46 | 91.76% | 0 | 0% | 8.13 | 7.55 | 92.87% | 0 | 0% | 8.13 | 7.65 | 94.1% | 0 | 0% | 8.13 | 7.75 | 95.33% | 0 | 0%
GNA_192221102_Capacity | North Coast | Humboldt | GARBERVILLE 1102 | 192221102 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192221103_Capacity | North Coast | Humboldt | GARBERVILLE 1103 | 192221103 | Feeder | None | None | None | 26.69% | 0 | 0% | 8.13 | 2.17 | 26.69% | 0 | 0% | 8.13 | 2.17 | 26.69% | 0 | 0% | 8.13 | 2.17 | 26.69% | 0 | 0% | 8.13 | 2.17 | 26.69% | 0 | 0% | 8.13 | 2.17 | 26.69% | 0 | 0%
GNA_0422501_Capacity | North Coast | Humboldt | HOPLAND BANK 1 | 422501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042251101_Capacity | North Coast | Humboldt | HOPLAND 1101 | 42251101 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1921001_Capacity | North Coast | Humboldt | MAPLE CREEK BANK 1 | 1921001 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192101101_Capacity | North Coast | Humboldt | MAPLE CREEK 1101 | 192101101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0430801_Capacity | North Coast | Humboldt | BIG RIVER BANK 1 | 430801 | Bank | Demand Growth | Capacity | 2027 | 101.2% | 0.06 | 1.212% | 4.95 | 4.41 | 89.09% | 0 | 0% | 4.95 | 4.52 | 91.31% | 0 | 0% | 4.95 | 4.64 | 93.74% | 0 | 0% | 4.95 | 4.83 | 97.58% | 0 | 0% | 4.95 | 5.01 | 101.2% | 0.06 | 1.212%
GNA_043081101_Capacity | North Coast | Humboldt | BIG RIVER 1101 | 43081101 | Feeder | None | None | None | 65.65% | 0 | 0% | 7.57 | 4.37 | 57.73% | 0 | 0% | 7.57 | 4.47 | 59.05% | 0 | 0% | 7.57 | 4.59 | 60.63% | 0 | 0% | 7.57 | 4.78 | 63.14% | 0 | 0% | 7.57 | 4.97 | 65.65% | 0 | 0%
GNA_0429801_Capacity | North Coast | Humboldt | ELK BANK 1 | 429801 | Bank | None | None | None | 38.56% | 0 | 0% | 9.88 | 3.37 | 34.11% | 0 | 0% | 9.88 | 3.5 | 35.43% | 0 | 0% | 9.88 | 3.6 | 36.44% | 0 | 0% | 9.88 | 3.7 | 37.45% | 0 | 0% | 9.88 | 3.81 | 38.56% | 0 | 0%
GNA_042981101_Capacity | North Coast | Humboldt | ELK 1101 | 42981101 | Feeder | None | None | None | 87.37% | 0 | 0% | 4.83 | 3.78 | 78.26% | 0 | 0% | 4.83 | 3.92 | 81.16% | 0 | 0% | 4.83 | 4.01 | 83.02% | 0 | 0% | 4.83 | 4.11 | 85.09% | 0 | 0% | 4.83 | 4.22 | 87.37% | 0 | 0%
GNA_0427601_Capacity | North Coast | Humboldt | FORT BRAGG A BANK 1 | 427601 | Bank | None | None | None | 43.4% | 0 | 0% | 29.7 | 12.34 | 41.55% | 0 | 0% | 29.7 | 12.58 | 42.36% | 0 | 0% | 29.7 | 12.61 | 42.46% | 0 | 0% | 29.7 | 12.7 | 42.76% | 0 | 0% | 29.7 | 12.89 | 43.4% | 0 | 0%
GNA_042761101_Capacity | North Coast | Humboldt | FORT BRAGG A 1101 | 42761101 | Feeder | None | None | None | 73.85% | 0 | 0% | 6.5 | 4.48 | 68.92% | 0 | 0% | 6.5 | 4.54 | 69.85% | 0 | 0% | 6.5 | 4.61 | 70.92% | 0 | 0% | 6.5 | 4.67 | 71.85% | 0 | 0% | 6.5 | 4.8 | 73.85% | 0 | 0%
GNA_042761102_Capacity | North Coast | Humboldt | FORT BRAGG A 1102 | 42761102 | Feeder | None | None | None | 66.55% | 0 | 0% | 8.64 | 5.45 | 63.08% | 0 | 0% | 8.64 | 5.72 | 66.2% | 0 | 0% | 8.64 | 5.69 | 65.86% | 0 | 0% | 8.64 | 5.71 | 66.09% | 0 | 0% | 8.64 | 5.75 | 66.55% | 0 | 0%
GNA_042761103_Capacity | North Coast | Humboldt | FORT BRAGG A 1103 | 42761103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0427602_Capacity | North Coast | Humboldt | FORT BRAGG A BANK 2 | 427602 | Bank | None | None | None | 12.49% | 0 | 0% | 29.7 | 3.66 | 12.32% | 0 | 0% | 29.7 | 3.65 | 12.29% | 0 | 0% | 29.7 | 3.68 | 12.39% | 0 | 0% | 29.7 | 3.71 | 12.49% | 0 | 0% | 29.7 | 3.71 | 12.49% | 0 | 0%
GNA_042761104_Capacity | North Coast | Humboldt | FORT BRAGG A 1104 | 42761104 | Feeder | None | None | None | 51.47% | 0 | 0% | 7.48 | 3.81 | 50.94% | 0 | 0% | 7.48 | 3.8 | 50.8% | 0 | 0% | 7.48 | 3.83 | 51.2% | 0 | 0% | 7.48 | 3.85 | 51.47% | 0 | 0% | 7.48 | 3.85 | 51.47% | 0 | 0%
GNA_0428601_Capacity | North Coast | Humboldt | ANNAPOLIS BANK 1 | 428601 | Bank | None | None | None | 25.53% | 0 | 0% | 1.88 | 0.44 | 23.4% | 0 | 0% | 1.88 | 0.45 | 23.94% | 0 | 0% | 1.88 | 0.45 | 23.94% | 0 | 0% | 1.88 | 0.46 | 24.47% | 0 | 0% | 1.88 | 0.48 | 25.53% | 0 | 0%
GNA_042861101_Capacity | North Coast | Humboldt | ANNAPOLIS 1101 | 42861101 | Feeder | None | None | None | 21.54% | 0 | 0% | 2.46 | 0.49 | 19.92% | 0 | 0% | 2.46 | 0.5 | 20.33% | 0 | 0% | 2.46 | 0.5 | 20.33% | 0 | 0% | 2.46 | 0.51 | 20.73% | 0 | 0% | 2.46 | 0.53 | 21.54% | 0 | 0%
GNA_0428401_Capacity | North Coast | Humboldt | GUALALA BANK 1 | 428401 | Bank | None | None | None | 73.13% | 0 | 0% | 4.95 | 3.21 | 64.85% | 0 | 0% | 4.95 | 3.3 | 66.67% | 0 | 0% | 4.95 | 3.39 | 68.48% | 0 | 0% | 4.95 | 3.51 | 70.91% | 0 | 0% | 4.95 | 3.62 | 73.13% | 0 | 0%
GNA_042841111_Capacity | North Coast | Humboldt | GUALALA 1111 | 42841111 | Feeder | None | None | None | 50.42% | 0 | 0% | 7.12 | 3.17 | 44.52% | 0 | 0% | 7.12 | 3.26 | 45.79% | 0 | 0% | 7.12 | 3.36 | 47.19% | 0 | 0% | 7.12 | 3.47 | 48.74% | 0 | 0% | 7.12 | 3.59 | 50.42% | 0 | 0%
GNA_0428402_Capacity | North Coast | Humboldt | GUALALA BANK 2 | 428402 | Bank | None | None | None | 25.69% | 0 | 0% | 6.19 | 1.52 | 24.56% | 0 | 0% | 6.19 | 1.52 | 24.56% | 0 | 0% | 6.19 | 1.53 | 24.72% | 0 | 0% | 6.19 | 1.55 | 25.04% | 0 | 0% | 6.19 | 1.59 | 25.69% | 0 | 0%
GNA_042841112_Capacity | North Coast | Humboldt | GUALALA 1112 | 42841112 | Feeder | None | None | None | 23.46% | 0 | 0% | 7.12 | 1.6 | 22.47% | 0 | 0% | 7.12 | 1.6 | 22.47% | 0 | 0% | 7.12 | 1.61 | 22.61% | 0 | 0% | 7.12 | 1.63 | 22.89% | 0 | 0% | 7.12 | 1.67 | 23.46% | 0 | 0%
GNA_0433801_Capacity | North Coast | Humboldt | POINT ARENA BANK 1 | 433801 | Bank | None | None | None | 80.66% | 0 | 0% | 2.12 | 1.69 | 79.72% | 0 | 0% | 2.12 | 1.69 | 79.72% | 0 | 0% | 2.12 | 1.69 | 79.72% | 0 | 0% | 2.12 | 1.69 | 79.72% | 0 | 0% | 2.12 | 1.71 | 80.66% | 0 | 0%
GNA_043381101_Capacity | North Coast | Humboldt | POINT ARENA 1101 | 43381101 | Feeder | None | None | None | 51.64% | 0 | 0% | 3.04 | 1.55 | 50.99% | 0 | 0% | 3.04 | 1.55 | 50.99% | 0 | 0% | 3.04 | 1.55 | 50.99% | 0 | 0% | 3.04 | 1.55 | 50.99% | 0 | 0% | 3.04 | 1.57 | 51.64% | 0 | 0%
GNA_0431401_Capacity | North Coast | Humboldt | MIDDLETOWN BANK 1 | 431401 | Bank | None | None | None | 33.05% | 0 | 0% | 19.73 | 6.11 | 30.97% | 0 | 0% | 19.73 | 6.13 | 31.07% | 0 | 0% | 19.73 | 6.24 | 31.63% | 0 | 0% | 19.73 | 6.36 | 32.24% | 0 | 0% | 19.73 | 6.52 | 33.05% | 0 | 0%
GNA_043141101_Capacity | North Coast | Humboldt | MIDDLETOWN 1101 | 43141101 | Feeder | None | None | None | 59.21% | 0 | 0% | 10.69 | 6.33 | 59.21% | 0 | 0% | 10.69 | 6.25 | 58.47% | 0 | 0% | 10.69 | 6.26 | 58.56% | 0 | 0% | 10.69 | 6.28 | 58.75% | 0 | 0% | 10.69 | 6.33 | 59.21% | 0 | 0%
GNA_043141103_Capacity | North Coast | Humboldt | MIDDLETOWN 1103 | 43141103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0431402_Capacity | North Coast | Humboldt | MIDDLETOWN BANK 2 | 431402 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043141102_Capacity | North Coast | Humboldt | MIDDLETOWN 1102 | 43141102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1922901_Capacity | North Coast | Humboldt | CARLOTTA BANK 1 | 1922901 | Bank | Demand Growth | Capacity | 2025 | 126.2% | 0.74 | 26.24% | 2.82 | 1.82 | 64.54% | 0 | 0% | 2.82 | 1.85 | 65.6% | 0 | 0% | 2.82 | 3.32 | 117.7% | 0.5 | 17.73% | 2.82 | 3.42 | 121.3% | 0.6 | 21.28% | 2.82 | 3.56 | 126.2% | 0.74 | 26.24%
GNA_192291121_Capacity | North Coast | Humboldt | CARLOTTA 1121 | 192291121 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1923801_Capacity | North Coast | Humboldt | EEL RIVER BANK 1 | 1923801 | Bank | None | None | None | 98.27% | 0 | 0% | 9.27 | 8.67 | 93.53% | 0 | 0% | 9.27 | 8.84 | 95.36% | 0 | 0% | 9.27 | 8.99 | 96.98% | 0 | 0% | 9.27 | 9.02 | 97.3% | 0 | 0% | 9.27 | 9.11 | 98.27% | 0 | 0%
GNA_192381102_Capacity | North Coast | Humboldt | EEL RIVER 1102 | 192381102 | Feeder | None | None | None | 98.82% | 0 | 0% | 9.34 | 8.79 | 94.11% | 0 | 0% | 9.34 | 8.96 | 95.93% | 0 | 0% | 9.34 | 9.11 | 97.54% | 0 | 0% | 9.34 | 9.14 | 97.86% | 0 | 0% | 9.34 | 9.23 | 98.82% | 0 | 0%
GNA_1923802_Capacity | North Coast | Humboldt | EEL RIVER BANK 2 | 1923802 | Bank | None | None | None | 21.53% | 0 | 0% | 15.84 | 3.38 | 21.34% | 0 | 0% | 15.84 | 3.38 | 21.34% | 0 | 0% | 15.84 | 3.37 | 21.28% | 0 | 0% | 15.84 | 3.39 | 21.4% | 0 | 0% | 15.84 | 3.41 | 21.53% | 0 | 0%
GNA_192381103_Capacity | North Coast | Humboldt | EEL RIVER 1103 | 192381103 | Feeder | None | None | None | 44.62% | 0 | 0% | 8.36 | 3.7 | 44.26% | 0 | 0% | 8.36 | 3.69 | 44.14% | 0 | 0% | 8.36 | 3.69 | 44.14% | 0 | 0% | 8.36 | 3.7 | 44.26% | 0 | 0% | 8.36 | 3.73 | 44.62% | 0 | 0%
GNA_1921501_Capacity | North Coast | Humboldt | NEWBURG BANK 1 | 1921501 | Bank | None | None | None | 83.93% | 0 | 0% | 12.32 | 6.7 | 54.38% | 0 | 0% | 12.32 | 8.96 | 72.73% | 0 | 0% | 12.32 | 9.15 | 74.27% | 0 | 0% | 12.32 | 9.39 | 76.22% | 0 | 0% | 12.32 | 10.34 | 83.93% | 0 | 0%
GNA_192151131_Capacity | North Coast | Humboldt | NEWBURG 1131 | 192151131 | Feeder | None | None | None | 86.59% | 0 | 0% | 9.99 | 6.17 | 61.76% | 0 | 0% | 9.99 | 8.32 | 83.28% | 0 | 0% | 9.99 | 8.42 | 84.28% | 0 | 0% | 9.99 | 8.54 | 85.49% | 0 | 0% | 9.99 | 8.65 | 86.59% | 0 | 0%
GNA_192151133_Capacity | North Coast | Humboldt | NEWBURG 1133 | 192151133 | Feeder | None | None | None | 30.46% | 0 | 0% | 6.5 | 0.85 | 13.08% | 0 | 0% | 6.5 | 0.94 | 14.46% | 0 | 0% | 6.5 | 1.04 | 16% | 0 | 0% | 6.5 | 1.14 | 17.54% | 0 | 0% | 6.5 | 1.98 | 30.46% | 0 | 0%
GNA_1921502_Capacity | North Coast | Humboldt | NEWBURG BANK 2 | 1921502 | Bank | None | None | None | 99.9% | 0 | 0% | 9.88 | 7.92 | 80.16% | 0 | 0% | 9.88 | 8.34 | 84.41% | 0 | 0% | 9.88 | 8.94 | 90.49% | 0 | 0% | 9.88 | 9.55 | 96.66% | 0 | 0% | 9.88 | 9.87 | 99.9% | 0 | 0%
GNA_192151132_Capacity | North Coast | Humboldt | NEWBURG 1132 | 192151132 | Feeder | None | None | None | 95.23% | 0 | 0% | 10.69 | 8.29 | 77.55% | 0 | 0% | 10.69 | 8.72 | 81.57% | 0 | 0% | 10.69 | 9.31 | 87.09% | 0 | 0% | 10.69 | 9.92 | 92.8% | 0 | 0% | 10.69 | 10.18 | 95.23% | 0 | 0%
GNA_1922501_Capacity | North Coast | Humboldt | RIO DELL BANK 1 | 1922501 | Bank | Demand Growth | Capacity | 2025 | 146.8% | 4.86 | 46.78% | 10.39 | 8.21 | 79.02% | 0 | 0% | 10.39 | 9.38 | 90.28% | 0 | 0% | 10.39 | 14.81 | 142.5% | 4.42 | 42.54% | 10.39 | 15.02 | 144.6% | 4.63 | 44.56% | 10.39 | 15.25 | 146.8% | 4.86 | 46.78%
GNA_192251101_Capacity | North Coast | Humboldt | RIO DELL 1101 | 192251101 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192251102_Capacity | North Coast | Humboldt | RIO DELL 1102 | 192251102 | Feeder | None | None | None | 63.85% | 0 | 0% | 6.86 | 2.79 | 40.67% | 0 | 0% | 6.86 | 2.89 | 42.13% | 0 | 0% | 6.86 | 4.16 | 60.64% | 0 | 0% | 6.86 | 4.27 | 62.24% | 0 | 0% | 6.86 | 4.38 | 63.85% | 0 | 0%
GNA_0426001_Capacity | North Coast | Humboldt | PHILO BANK 1 | 426001 | Bank | None | None | None | 79.74% | 0 | 0% | 4.69 | 3.74 | 79.74% | 0 | 0% | 4.69 | 3.68 | 78.46% | 0 | 0% | 4.69 | 3.61 | 76.97% | 0 | 0% | 4.69 | 3.58 | 76.33% | 0 | 0% | 4.69 | 3.56 | 75.91% | 0 | 0%
GNA_042601101_Capacity | North Coast | Humboldt | PHILO 1101 | 42601101 | Feeder | None | None | None | 42.43% | 0 | 0% | 5.35 | 2.27 | 42.43% | 0 | 0% | 5.35 | 2.25 | 42.06% | 0 | 0% | 5.35 | 2.24 | 41.87% | 0 | 0% | 5.35 | 2.24 | 41.87% | 0 | 0% | 5.35 | 2.24 | 41.87% | 0 | 0%
GNA_042601102_Capacity | North Coast | Humboldt | PHILO 1102 | 42601102 | Feeder | None | None | None | 56.31% | 0 | 0% | 2.93 | 1.65 | 56.31% | 0 | 0% | 2.93 | 1.61 | 54.95% | 0 | 0% | 2.93 | 1.56 | 53.24% | 0 | 0% | 2.93 | 1.53 | 52.22% | 0 | 0% | 2.93 | 1.56 | 53.24% | 0 | 0%
GNA_0422804_Capacity | North Coast | Humboldt | POTTER VALLEY P H BANK 4 | 422804 | Bank | None | None | None | 0% | 0 | 0% | 1.75 | 0 | 0% | 0 | 0% | 1.75 | 0 | 0% | 0 | 0% | 1.75 | 0 | 0% | 0 | 0% | 1.75 | 0 | 0% | 0 | 0% | 1.75 | 0 | 0% | 0 | 0%
GNA_042281104_Capacity | North Coast | Humboldt | POTTER VALLEY P H 1104 | 42281104 | Feeder | None | None | None | 0% | 0 | 0% | 1.8 | 0 | 0% | 0 | 0% | 1.8 | 0 | 0% | 0 | 0% | 1.8 | 0 | 0% | 0 | 0% | 1.8 | 0 | 0% | 0 | 0% | 1.8 | 0 | 0% | 0 | 0%
GNA_0422805_Capacity | North Coast | Humboldt | POTTER VALLEY P H BANK 5 | 422805 | Bank | Demand Growth | Capacity | 2024 | 137.6% | 1.46 | 37.63% | 3.88 | 3.84 | 98.97% | 0 | 0% | 3.88 | 4.03 | 103.9% | 0.15 | 3.866% | 3.88 | 4.02 | 103.6% | 0.14 | 3.608% | 3.88 | 5.32 | 137.1% | 1.44 | 37.11% | 3.88 | 5.34 | 137.6% | 1.46 | 37.63%
GNA_042281105_Capacity | North Coast | Humboldt | POTTER VALLEY P H 1105 | 42281105 | Feeder | Demand Growth | Capacity | 2026 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0434101_Capacity | North Coast | Humboldt | CALPELLA BANK 1 | 434101 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043411101_Capacity | North Coast | Humboldt | CALPELLA 1101 | 43411101 | Feeder | None | None | None | 92.04% | 0 | 0% | 12.19 | 11.22 | 92.04% | 0 | 0% | 12.19 | 11.09 | 90.98% | 0 | 0% | 12.19 | 10.93 | 89.66% | 0 | 0% | 12.19 | 10.91 | 89.5% | 0 | 0% | 12.19 | 10.92 | 89.58% | 0 | 0%
GNA_043411102_Capacity | North Coast | Humboldt | CALPELLA 1102 | 43411102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0429502_Capacity | North Coast | Humboldt | MENDOCINO BANK 2 | 429502 | Bank | None | None | None | 89.53% | 0 | 0% | 4.87 | 4.36 | 89.53% | 0 | 0% | 4.87 | 4.29 | 88.09% | 0 | 0% | 4.87 | 4.27 | 87.68% | 0 | 0% | 4.87 | 4.29 | 88.09% | 0 | 0% | 4.87 | 4.36 | 89.53% | 0 | 0%
GNA_042951101_Capacity | North Coast | Humboldt | MENDOCINO 1101 | 42951101 | Feeder | None | None | None | 65.09% | 0 | 0% | 7.42 | 4.83 | 65.09% | 0 | 0% | 7.42 | 4.75 | 64.02% | 0 | 0% | 7.42 | 4.73 | 63.75% | 0 | 0% | 7.42 | 4.75 | 64.02% | 0 | 0% | 7.42 | 4.8 | 64.69% | 0 | 0%
GNA_0427701_Capacity | North Coast | Humboldt | UKIAH BANK 1 | 427701 | Bank | None | None | None | 93.48% | 0 | 0% | 15.8 | 14.77 | 93.48% | 0 | 0% | 15.8 | 14.41 | 91.2% | 0 | 0% | 15.8 | 14.32 | 90.63% | 0 | 0% | 15.8 | 14.29 | 90.44% | 0 | 0% | 15.8 | 14.36 | 90.89% | 0 | 0%
GNA_042771113_Capacity | North Coast | Humboldt | UKIAH 1113 | 42771113 | Feeder | None | None | None | 33.46% | 0 | 0% | 10.46 | 3.5 | 33.46% | 0 | 0% | 10.46 | 3.43 | 32.79% | 0 | 0% | 10.46 | 3.4 | 32.5% | 0 | 0% | 10.46 | 3.39 | 32.41% | 0 | 0% | 10.46 | 3.41 | 32.6% | 0 | 0%
GNA_042771114_Capacity | North Coast | Humboldt | UKIAH 1114 | 42771114 | Feeder | None | None | None | 55.57% | 0 | 0% | 9.43 | 5.24 | 55.57% | 0 | 0% | 9.43 | 5.12 | 54.29% | 0 | 0% | 9.43 | 5.07 | 53.76% | 0 | 0% | 9.43 | 5.06 | 53.66% | 0 | 0% | 9.43 | 5.1 | 54.08% | 0 | 0%
GNA_042771115_Capacity | North Coast | Humboldt | UKIAH 1115 | 42771115 | Feeder | None | None | None | 64.91% | 0 | 0% | 10.46 | 6.79 | 64.91% | 0 | 0% | 10.46 | 6.64 | 63.48% | 0 | 0% | 10.46 | 6.59 | 63% | 0 | 0% | 10.46 | 6.57 | 62.81% | 0 | 0% | 10.46 | 6.59 | 63% | 0 | 0%
GNA_0427702_Capacity | North Coast | Humboldt | UKIAH BANK 2 | 427702 | Bank | None | None | None | 59.76% | 0 | 0% | 12.4 | 7.41 | 59.76% | 0 | 0% | 12.4 | 7.36 | 59.35% | 0 | 0% | 12.4 | 7.31 | 58.95% | 0 | 0% | 12.4 | 7.28 | 58.71% | 0 | 0% | 12.4 | 7.26 | 58.55% | 0 | 0%
GNA_042771111_Capacity | North Coast | Humboldt | UKIAH 1111 | 42771111 | Feeder | None | None | None | 71.51% | 0 | 0% | 10.46 | 7.48 | 71.51% | 0 | 0% | 10.46 | 7.43 | 71.03% | 0 | 0% | 10.46 | 7.38 | 70.55% | 0 | 0% | 10.46 | 7.35 | 70.27% | 0 | 0% | 10.46 | 7.32 | 69.98% | 0 | 0%
GNA_0430601_Capacity | North Coast | Humboldt | COVELO BANK 1 | 430601 | Bank | None | None | None | 61% | 0 | 0% | 5.41 | 3.3 | 61% | 0 | 0% | 5.41 | 3.23 | 59.7% | 0 | 0% | 5.41 | 3.14 | 58.04% | 0 | 0% | 5.41 | 3.05 | 56.38% | 0 | 0% | 5.41 | 3.01 | 55.64% | 0 | 0%
GNA_043061101_Capacity | North Coast | Humboldt | COVELO 1101 | 43061101 | Feeder | None | None | None | 48.39% | 0 | 0% | 6.84 | 3.31 | 48.39% | 0 | 0% | 6.84 | 3.23 | 47.22% | 0 | 0% | 6.84 | 3.14 | 45.91% | 0 | 0% | 6.84 | 3.05 | 44.59% | 0 | 0% | 6.84 | 3.01 | 44.01% | 0 | 0%
GNA_0426801_Capacity | North Coast | Humboldt | LAYTONVILLE BANK 1 | 426801 | Bank | None | None | None | 56.12% | 0 | 0% | 7.52 | 4.22 | 56.12% | 0 | 0% | 7.52 | 4.14 | 55.05% | 0 | 0% | 7.52 | 4 | 53.19% | 0 | 0% | 7.52 | 4.02 | 53.46% | 0 | 0% | 7.52 | 4.04 | 53.72% | 0 | 0%
GNA_042681101_Capacity | North Coast | Humboldt | LAYTONVILLE 1101 | 42681101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042681102_Capacity | North Coast | Humboldt | LAYTONVILLE 1102 | 42681102 | Feeder | None | None | None | 33.25% | 0 | 0% | 7.85 | 2.61 | 33.25% | 0 | 0% | 7.85 | 2.55 | 32.48% | 0 | 0% | 7.85 | 2.48 | 31.59% | 0 | 0% | 7.85 | 2.5 | 31.85% | 0 | 0% | 7.85 | 2.51 | 31.97% | 0 | 0%
GNA_0426601_Capacity | North Coast | Humboldt | WILLITS BANK 1 | 426601 | Bank | Demand Growth | Capacity | 2025 | 113.3% | 2.19 | 13.34% | 16.42 | 15.57 | 94.82% | 0 | 0% | 16.42 | 16.14 | 98.29% | 0 | 0% | 16.42 | 17.89 | 109% | 1.47 | 8.952% | 16.42 | 18.22 | 111% | 1.8 | 10.96% | 16.42 | 18.61 | 113.3% | 2.19 | 13.34%
GNA_042661102_Capacity | North Coast | Humboldt | WILLITS 1102 | 42661102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042661103_Capacity | North Coast | Humboldt | WILLITS 1103 | 42661103 | Feeder | None | None | None | 81.42% | 0 | 0% | 8.02 | 5.2 | 64.84% | 0 | 0% | 8.02 | 6.17 | 76.93% | 0 | 0% | 8.02 | 6.24 | 77.81% | 0 | 0% | 8.02 | 6.36 | 79.3% | 0 | 0% | 8.02 | 6.53 | 81.42% | 0 | 0%
GNA_042661104_Capacity | North Coast | Humboldt | WILLITS 1104 | 42661104 | Feeder | None | None | None | 71.08% | 0 | 0% | 10.65 | 7.41 | 69.58% | 0 | 0% | 10.65 | 7.12 | 66.85% | 0 | 0% | 10.65 | 7.24 | 67.98% | 0 | 0% | 10.65 | 7.4 | 69.48% | 0 | 0% | 10.65 | 7.57 | 71.08% | 0 | 0%
GNA_1924001_Capacity | North Coast | Humboldt | HOOPA BANK 1 | 1924001 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192401101_Capacity | North Coast | Humboldt | HOOPA 1101 | 192401101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1921701_Capacity | North Coast | Humboldt | WILLOW CREEK BANK 1 | 1921701 | Bank | None | None | None | 100.2% | 0.02 | 0.2153% | 9.29 | 8.29 | 89.24% | 0 | 0% | 9.29 | 9.12 | 98.17% | 0 | 0% | 9.29 | 9.14 | 98.39% | 0 | 0% | 9.29 | 9.23 | 99.35% | 0 | 0% | 9.29 | 9.31 | 100.2% | 0.02 | 0.2153%
GNA_192171101_Capacity | North Coast | Humboldt | WILLOW CREEK 1101 | 192171101 | Feeder | Demand Growth | Capacity | 2027 | 101.3% | 0.06 | 1.325% | 4.53 | 4.52 | 99.78% | 0 | 0% | 4.53 | 4.52 | 99.78% | 0 | 0% | 4.53 | 4.53 | 100% | 0 | 0% | 4.53 | 4.55 | 100.4% | 0.02 | 0.4415% | 4.53 | 4.59 | 101.3% | 0.06 | 1.325%
GNA_192171102_Capacity | North Coast | Humboldt | WILLOW CREEK 1102 | 192171102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_192171103_Capacity | North Coast | Humboldt | WILLOW CREEK 1103 | 192171103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2538001_Capacity | Central Valley | Kern | ARVIN BANK 1 | 2538001 | Bank | Demand Growth | Capacity | 2023 | 140.5% | 4.76 | 40.48% | 11.76 | 16 | 136.1% | 4.24 | 36.05% | 11.76 | 16.51 | 140.4% | 4.75 | 40.39% | 11.76 | 16.51 | 140.4% | 4.75 | 40.39% | 11.76 | 16.52 | 140.5% | 4.76 | 40.48% | 11.76 | 16.51 | 140.4% | 4.75 | 40.39%
GNA_253801101_Capacity | Central Valley | Kern | ARVIN 1101 | 253801101 | Feeder | None | None | None | 76.86% | 0 | 0% | 10.46 | 7.78 | 74.38% | 0 | 0% | 10.46 | 8.03 | 76.77% | 0 | 0% | 10.46 | 8.04 | 76.86% | 0 | 0% | 10.46 | 8.04 | 76.86% | 0 | 0% | 10.46 | 8.04 | 76.86% | 0 | 0%
GNA_253801102_Capacity | Central Valley | Kern | ARVIN 1102 | 253801102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253801103_Capacity | Central Valley | Kern | ARVIN 1103 | 253801103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2534101_Capacity | Central Valley | Kern | LAKEVIEW BANK 1 | 2534101 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253411102_Capacity | Central Valley | Kern | LAKEVIEW 1102 | 253411102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253411103_Capacity | Central Valley | Kern | LAKEVIEW 1103 | 253411103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2534102_Capacity | Central Valley | Kern | LAKEVIEW BANK 2 | 2534102 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253411106_Capacity | Central Valley | Kern | LAKEVIEW 1106 (old 1103) | 253411106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253411107_Capacity | Central Valley | Kern | LAKEVIEW 1107 (old 1101) | 253411107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2528201_Capacity | Central Valley | Kern | OLD RIVER BANK 1 (old Bank 2 feeders) | 2528201 | Bank | None | None | None | 90.74% | 0 | 0% | 29.69 | 24.24 | 81.64% | 0 | 0% | 29.69 | 24.6 | 82.86% | 0 | 0% | 29.69 | 24.77 | 83.43% | 0 | 0% | 29.69 | 26.56 | 89.46% | 0 | 0% | 29.69 | 26.94 | 90.74% | 0 | 0%
GNA_252821101_Capacity | Central Valley | Kern | OLD RIVER 1101 | 252821101 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252821102_Capacity | Central Valley | Kern | OLD RIVER 1102 | 252821102 | Feeder | Demand Growth | Capacity | 2026 | 114% | 1.46 | 13.96% | 10.46 | 8.37 | 80.02% | 0 | 0% | 10.46 | 8.83 | 84.42% | 0 | 0% | 10.46 | 9.14 | 87.38% | 0 | 0% | 10.46 | 11.35 | 108.5% | 0.89 | 8.509% | 10.46 | 11.92 | 114% | 1.46 | 13.96%
GNA_252821105_Capacity | Central Valley | Kern | OLD RIVER 1105 | 252821105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2528202_Capacity | Central Valley | Kern | OLD RIVER BANK 2 (old Bank 1 feeders) | 2528202 | Bank | Demand Growth | Capacity | 2023 | 144.9% | 7.12 | 44.95% | 15.84 | 21.84 | 137.9% | 6 | 37.88% | 15.84 | 22.79 | 143.9% | 6.95 | 43.88% | 15.84 | 22.94 | 144.8% | 7.1 | 44.82% | 15.84 | 22.94 | 144.8% | 7.1 | 44.82% | 15.84 | 22.96 | 144.9% | 7.12 | 44.95%
GNA_252821103_Capacity | Central Valley | Kern | OLD RIVER 1103 | 252821103 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252821104_Capacity | Central Valley | Kern | OLD RIVER 1104 | 252821104 | Feeder | None | None | None | 81.79% | 0 | 0% | 12.19 | 9.7 | 79.57% | 0 | 0% | 12.19 | 9.78 | 80.23% | 0 | 0% | 12.19 | 9.95 | 81.62% | 0 | 0% | 12.19 | 9.96 | 81.71% | 0 | 0% | 12.19 | 9.97 | 81.79% | 0 | 0%
GNA_2531901_Capacity | Central Valley | Kern | SAN BERNARD BANK 1 | 2531901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253191101_Capacity | Central Valley | Kern | SAN BERNARD 1101 | 253191101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253191102_Capacity | Central Valley | Kern | SAN BERNARD 1102 | 253191102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253191104_Capacity | Central Valley | Kern | SAN BERNARD 1104 | 253191104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2529301_Capacity | Central Valley | Kern | TEJON BANK 1 | 2529301 | Bank | Demand Growth | Capacity | 2023 | 140.2% | 7.08 | 40.16% | 17.63 | 18.98 | 107.7% | 1.35 | 7.657% | 17.63 | 22.3 | 126.5% | 4.67 | 26.49% | 17.63 | 24.49 | 138.9% | 6.86 | 38.91% | 17.63 | 24.59 | 139.5% | 6.96 | 39.48% | 17.63 | 24.71 | 140.2% | 7.08 | 40.16%
GNA_252931102_Capacity | Central Valley | Kern | TEJON 1102 | 252931102 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252931103_Capacity | Central Valley | Kern | TEJON 1103 | 252931103 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2529302_Capacity | Central Valley | Kern | TEJON BANK 2 | 2529302 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252931105_Capacity | Central Valley | Kern | TEJON 1105 | 252931105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252931106_Capacity | Central Valley | Kern | TEJON 1106 | 252931106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252931107_Capacity | Central Valley | Kern | TEJON 1107 | 252931107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2534801_Capacity | Central Valley | Kern | WHEELER RIDGE BANK 1 | 2534801 | Bank | Demand Growth | Capacity | 2025 | 144% | 12.78 | 44.01% | 29.04 | 28.08 | 96.69% | 0 | 0% | 29.04 | 26.68 | 91.87% | 0 | 0% | 29.04 | 30.21 | 104% | 1.17 | 4.029% | 29.04 | 39.13 | 134.7% | 10.09 | 34.75% | 29.04 | 41.82 | 144% | 12.78 | 44.01%
GNA_253481101_Capacity | Central Valley | Kern | WHEELER RIDGE 1101 | 253481101 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253481102_Capacity | Central Valley | Kern | WHEELER RIDGE 1102 | 253481102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253481103_Capacity | Central Valley | Kern | WHEELER RIDGE 1103 | 253481103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2520201_Capacity | Central Valley | Kern | ANTELOPE BANK 1 | 2520201 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252021101_Capacity | Central Valley | Kern | ANTELOPE 1101 | 252021101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252021102_Capacity | Central Valley | Kern | ANTELOPE 1102 | 252021102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2546801_Capacity | Central Valley | Kern | BLACKWELL BANK 1 | 2546801 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254681102_Capacity | Central Valley | Kern | BLACKWELL 1102 | 254681102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254682101_Capacity | Central Valley | Kern | BLACKWELL 2101 | 254682101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2523201_Capacity | Central Valley | Kern | CARNERAS BANK 1 | 2523201 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252321102_Capacity | Central Valley | Kern | CARNERAS 1102 | 252321102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252321103_Capacity | Central Valley | Kern | CARNERAS 1103 | 252321103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2544001_Capacity | Central Valley | Kern | TWISSELMAN BANK 1 | 2544001 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254401102_Capacity | Central Valley | Kern | TWISSELMAN 1102 | 254401102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2544002_Capacity | Central Valley | Kern | TWISSELMAN BANK 2 | 2544002 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254402105_Capacity | Central Valley | Kern | TWISSELMAN 2105 | 254402105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2534601_Capacity | Central Valley | Kern | CARRIZO PLAINS BANK 1 | 2534601 | Bank | None | None | None | 35.86% | 0 | 0% | 1.98 | 0.71 | 35.86% | 0 | 0% | 1.98 | 0.71 | 35.86% | 0 | 0% | 1.98 | 0.71 | 35.86% | 0 | 0% | 1.98 | 0.71 | 35.86% | 0 | 0% | 1.98 | 0.71 | 35.86% | 0 | 0%
GNA_253461101_Capacity | Central Valley | Kern | CARRIZO PLAINS 1101 | 253461101 | Feeder | None | None | None | 22.57% | 0 | 0% | 3.19 | 0.72 | 22.57% | 0 | 0% | 3.19 | 0.72 | 22.57% | 0 | 0% | 3.19 | 0.71 | 22.26% | 0 | 0% | 3.19 | 0.71 | 22.26% | 0 | 0% | 3.19 | 0.72 | 22.57% | 0 | 0%
GNA_2531401_Capacity | Central Valley | Kern | CUYAMA BANK 1 | 2531401 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253141103_Capacity | Central Valley | Kern | CUYAMA 1103 | 253141103 | Feeder | None | None | None | 29.28% | 0 | 0% | 10.69 | 3.12 | 29.19% | 0 | 0% | 10.69 | 3.13 | 29.28% | 0 | 0% | 10.69 | 3.12 | 29.19% | 0 | 0% | 10.69 | 3.12 | 29.19% | 0 | 0% | 10.69 | 3.12 | 29.19% | 0 | 0%
GNA_253141104_Capacity | Central Valley | Kern | CUYAMA 1104 | 253141104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253142102_Capacity | Central Valley | Kern | CUYAMA 2102 | 253142102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2531402_Capacity | Central Valley | Kern | CUYAMA BANK 2 | 2531402 | Bank | None | None | None | 70.14% | 0 | 0% | 15.84 | 11.11 | 70.14% | 0 | 0% | 15.84 | 11.1 | 70.08% | 0 | 0% | 15.84 | 11.1 | 70.08% | 0 | 0% | 15.84 | 11.1 | 70.08% | 0 | 0% | 15.84 | 11.1 | 70.08% | 0 | 0%
GNA_253142101_Capacity | Central Valley | Kern | CUYAMA 2101 | 253142101 | Feeder | None | None | None | 49.23% | 0 | 0% | 22.22 | 10.94 | 49.23% | 0 | 0% | 22.22 | 10.93 | 49.19% | 0 | 0% | 22.22 | 10.93 | 49.19% | 0 | 0% | 22.22 | 10.92 | 49.14% | 0 | 0% | 22.22 | 10.92 | 49.14% | 0 | 0%
GNA_2539101_Capacity | Central Valley | Kern | LAMONT BANK 1 | 2539101 | Bank | Demand Growth | Capacity | 2025 | 101.3% | 0.38 | 1.279% | 29.7 | 29.75 | 100.2% | 0.05 | 0.1684% | 29.7 | 29.83 | 100.4% | 0.13 | 0.4377% | 29.7 | 29.89 | 100.6% | 0.19 | 0.6397% | 29.7 | 29.98 | 100.9% | 0.28 | 0.9428% | 29.7 | 30.08 | 101.3% | 0.38 | 1.279%
GNA_253911102_Capacity | Central Valley | Kern | LAMONT 1102 | 253911102 | Feeder | None | None | None | 86.14% | 0 | 0% | 12.19 | 10.5 | 86.14% | 0 | 0% | 12.19 | 10.49 | 86.05% | 0 | 0% | 12.19 | 10.46 | 85.81% | 0 | 0% | 12.19 | 10.45 | 85.73% | 0 | 0% | 12.19 | 10.43 | 85.56% | 0 | 0%
GNA_253911103_Capacity | Central Valley | Kern | LAMONT 1103 | 253911103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253911104_Capacity | Central Valley | Kern | LAMONT 1104 | 253911104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2539103_Capacity | Central Valley | Kern | LAMONT BANK 3 | 2539103 | Bank | None | None | None | 73.54% | 0 | 0% | 36.32 | 26.42 | 72.74% | 0 | 0% | 36.32 | 26.47 | 72.88% | 0 | 0% | 36.32 | 26.52 | 73.02% | 0 | 0% | 36.32 | 26.6 | 73.24% | 0 | 0% | 36.32 | 26.71 | 73.54% | 0 | 0%
GNA_253911105_Capacity | Central Valley | Kern | LAMONT 1105 | 253911105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253911106_Capacity | Central Valley | Kern | LAMONT 1106 | 253911106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253911107_Capacity | Central Valley | Kern | LAMONT 1107 | 253911107 | Feeder | None | None | None | 88.02% | 0 | 0% | 12.19 | 10.73 | 88.02% | 0 | 0% | 12.19 | 10.66 | 87.45% | 0 | 0% | 12.19 | 10.66 | 87.45% | 0 | 0% | 12.19 | 10.68 | 87.61% | 0 | 0% | 12.19 | 10.71 | 87.86% | 0 | 0%
GNA_2529701_Capacity | Central Valley | Kern | WEEDPATCH BANK 1 | 2529701 | Bank | None | None | None | 95.99% | 0 | 0% | 29.7 | 27.6 | 92.93% | 0 | 0% | 29.7 | 27.7 | 93.27% | 0 | 0% | 29.7 | 27.8 | 93.6% | 0 | 0% | 29.7 | 28.1 | 94.61% | 0 | 0% | 29.7 | 28.51 | 95.99% | 0 | 0%
GNA_252971101_Capacity | Central Valley | Kern | WEEDPATCH 1101 | 252971101 | Feeder | None | None | None | 73.39% | 0 | 0% | 7.63 | 5.19 | 68.02% | 0 | 0% | 7.63 | 5.28 | 69.2% | 0 | 0% | 7.63 | 5.37 | 70.38% | 0 | 0% | 7.63 | 5.48 | 71.82% | 0 | 0% | 7.63 | 5.6 | 73.39% | 0 | 0%
GNA_252971102_Capacity | Central Valley | Kern | WEEDPATCH 1102 | 252971102 | Feeder | Demand Growth | Capacity | 2027 | 100.6% | 0.07 | 0.5998% | 11.67 | 11.56 | 99.06% | 0 | 0% | 11.67 | 11.57 | 99.14% | 0 | 0% | 11.67 | 11.57 | 99.14% | 0 | 0% | 11.67 | 11.59 | 99.31% | 0 | 0% | 11.67 | 11.74 | 100.6% | 0.07 | 0.5998%
GNA_252971103_Capacity | Central Valley | Kern | WEEDPATCH 1103 | 252971103 | Feeder | None | None | None | 95.98% | 0 | 0% | 10.46 | 10.04 | 95.98% | 0 | 0% | 10.46 | 10.04 | 95.98% | 0 | 0% | 10.46 | 9.99 | 95.51% | 0 | 0% | 10.46 | 9.88 | 94.46% | 0 | 0% | 10.46 | 9.79 | 93.59% | 0 | 0%
GNA_252971105_Capacity | Central Valley | Kern | WEEDPATCH 1105 | 252971105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252971106_Capacity | Central Valley | Kern | WEEDPATCH 1106 | 252971106 | Feeder | Demand Growth | Capacity | 2023 | 110.7% | 1.12 | 10.71% | 10.46 | 11.58 | 110.7% | 1.12 | 10.71% | 10.46 | 11.57 | 110.6% | 1.11 | 10.61% | 10.46 | 11.56 | 110.5% | 1.1 | 10.52% | 10.46 | 11.56 | 110.5% | 1.1 | 10.52% | 10.46 | 11.55 | 110.4% | 1.09 | 10.42%
GNA_2542901_Capacity | Central Valley | Kern | WELLFIELD BANK 1 | 2542901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254291103_Capacity | Central Valley | Kern | WELLFIELD 1103 | 254291103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254291104_Capacity | Central Valley | Kern | WELLFIELD 1104 | 254291104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2542902_Capacity | Central Valley | Kern | WELLFIELD BANK 2 | 2542902 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254291102_Capacity | Central Valley | Kern | WELLFIELD 1102 | 254291102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2524401_Capacity | Central Valley | Kern | ELK HILLS BANK 1 | 2524401 | Bank | None | None | None | 43.98% | 0 | 0% | 12.12 | 5.31 | 43.81% | 0 | 0% | 12.12 | 5.3 | 43.73% | 0 | 0% | 12.12 | 5.3 | 43.73% | 0 | 0% | 12.12 | 5.3 | 43.73% | 0 | 0% | 12.12 | 5.33 | 43.98% | 0 | 0%
GNA_252441104_Capacity | Central Valley | Kern | ELK HILLS 1104 | 252441104 | Feeder | None | None | None | 45.51% | 0 | 0% | 10.46 | 4.76 | 45.51% | 0 | 0% | 10.46 | 4.75 | 45.41% | 0 | 0% | 10.46 | 4.75 | 45.41% | 0 | 0% | 10.46 | 4.75 | 45.41% | 0 | 0% | 10.46 | 4.76 | 45.51% | 0 | 0%
GNA_252441106_Capacity | Central Valley | Kern | ELK HILLS 1106 | 252441106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2534901_Capacity | Central Valley | Kern | LERDO BANK 2 (old Bank 1) | 2534901 | Bank | None | None | None | 64.36% | 0 | 0% | 44.53 | 25.96 | 58.3% | 0 | 0% | 44.53 | 27.13 | 60.93% | 0 | 0% | 44.53 | 28.66 | 64.36% | 0 | 0% | 44.53 | 28.65 | 64.34% | 0 | 0% | 44.53 | 28.65 | 64.34% | 0 | 0%
GNA_253491111_Capacity | Central Valley | Kern | LERDO 1111 (OLD 1103) | 253491111 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253491110_Capacity | Central Valley | Kern | LERDO 1110 (OLD 1104) | 253491110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253491112_Capacity | Central Valley | Kern | LERDO 1112 (OLD 1105) | 253491112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2534902_Capacity | Central Valley | Kern | LERDO BANK 3 (old Bank 2) | 2534902 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253491113_Capacity | Central Valley | Kern | LERDO 1113 (OLD 1106) | 253491113 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253491116_Capacity | Central Valley | Kern | LERDO 1116 (OLD 1107) | 253491116 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253491114_Capacity | Central Valley | Kern | LERDO 1114 (OLD 1108) | 253491114 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253491115_Capacity | Central Valley | Kern | LERDO 1115 (OLD 1109) | 253491115 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2526107_Capacity | Central Valley | Kern | MIDWAY BANK 7 | 2526107 | Bank | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252611101_Capacity | Central Valley | Kern | MIDWAY 1101 | 252611101 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252611103_Capacity | Central Valley | Kern | MIDWAY 1103 | 252611103 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2526108_Capacity | Central Valley | Kern | MIDWAY BANK 8 | 2526108 | Bank | Demand Growth | Capacity | 2023 | 108.5% | 1.05 | 8.523% | 12.32 | 13.37 | 108.5% | 1.05 | 8.523% | 12.32 | 13.37 | 108.5% | 1.05 | 8.523% | 12.32 | 13.34 | 108.3% | 1.02 | 8.279% | 12.32 | 13.33 | 108.2% | 1.01 | 8.198% | 12.32 | 13.32 | 108.1% | 1 | 8.117%
GNA_252611102_Capacity | Central Valley | Kern | MIDWAY 1102 | 252611102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252611104_Capacity | Central Valley | Kern | MIDWAY 1104 | 252611104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2546901_Capacity | Central Valley | Kern | NORCO BANK 1 | 2546901 | Bank | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254691101_Capacity | Central Valley | Kern | NORCO 1101 | 254691101 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254691102_Capacity | Central Valley | Kern | NORCO 1102 | 254691102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2528602_Capacity | Central Valley | Kern | RIO BRAVO BANK 2 | 2528602 | Bank | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252861102_Capacity | Central Valley | Kern | RIO BRAVO 1102 | 252861102 | Feeder | None | None | None | 94.42% | 0 | 0% | 12.19 | 11.12 | 91.22% | 0 | 0% | 12.19 | 11.23 | 92.12% | 0 | 0% | 12.19 | 11.3 | 92.7% | 0 | 0% | 12.19 | 11.39 | 93.44% | 0 | 0% | 12.19 | 11.51 | 94.42% | 0 | 0%
GNA_252861104_Capacity | Central Valley | Kern | RIO BRAVO 1104 | 252861104 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252861106_Capacity | Central Valley | Kern | RIO BRAVO 1106 | 252861106 | Feeder | None | None | None | 100.4% | 0.05 | 0.4284% | 11.67 | 11.7 | 100.3% | 0.03 | 0.2571% | 11.67 | 11.68 | 100.1% | 0.01 | 0.08569% | 11.67 | 11.67 | 100% | 0 | 0% | 11.67 | 11.68 | 100.1% | 0.01 | 0.08569% | 11.67 | 11.72 | 100.4% | 0.05 | 0.4284%
GNA_2528603_Capacity | Central Valley | Kern | RIO BRAVO BANK 3 | 2528603 | Bank | None | None | None | 69.26% | 0 | 0% | 17.63 | 12.21 | 69.26% | 0 | 0% | 17.63 | 12.19 | 69.14% | 0 | 0% | 17.63 | 12.17 | 69.03% | 0 | 0% | 17.63 | 12.17 | 69.03% | 0 | 0% | 17.63 | 12.16 | 68.97% | 0 | 0%
GNA_252861101_Capacity | Central Valley | Kern | RIO BRAVO 1101 | 252861101 | Feeder | None | None | None | 42.82% | 0 | 0% | 12.19 | 5.22 | 42.82% | 0 | 0% | 12.19 | 5.21 | 42.74% | 0 | 0% | 12.19 | 5.19 | 42.58% | 0 | 0% | 12.19 | 5.19 | 42.58% | 0 | 0% | 12.19 | 5.18 | 42.49% | 0 | 0%
GNA_252861103_Capacity | Central Valley | Kern | RIO BRAVO 1103 | 252861103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2536501_Capacity | Central Valley | Kern | SHAFTER BANK 1 | 2536501 | Bank | None | None | None | 47.74% | 0 | 0% | 44.53 | 20.13 | 45.21% | 0 | 0% | 44.53 | 20.5 | 46.04% | 0 | 0% | 44.53 | 20.89 | 46.91% | 0 | 0% | 44.53 | 21.06 | 47.29% | 0 | 0% | 44.53 | 21.26 | 47.74% | 0 | 0%
GNA_253651102_Capacity | Central Valley | Kern | SHAFTER 1102 | 253651102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253651103_Capacity | Central Valley | Kern | SHAFTER 1103 | 253651103 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253651104_Capacity | Central Valley | Kern | SHAFTER 1104 | 253651104 | Feeder | None | None | None | 63.67% | 0 | 0% | 10.46 | 5.8 | 55.45% | 0 | 0% | 10.46 | 6.13 | 58.6% | 0 | 0% | 10.46 | 6.46 | 61.76% | 0 | 0% | 10.46 | 6.55 | 62.62% | 0 | 0% | 10.46 | 6.66 | 63.67% | 0 | 0%
GNA_2536503_Capacity | Central Valley | Kern | SHAFTER BANK 3 | 2536503 | Bank | None | None | None | 44.58% | 0 | 0% | 44.55 | 18.86 | 42.33% | 0 | 0% | 44.55 | 19.26 | 43.23% | 0 | 0% | 44.55 | 19.68 | 44.18% | 0 | 0% | 44.55 | 19.79 | 44.42% | 0 | 0% | 44.55 | 19.86 | 44.58% | 0 | 0%
GNA_253651111_Capacity | Central Valley | Kern | SHAFTER 1111 | 253651111 | Feeder | None | None | None | 66.54% | 0 | 0% | 13.6 | 7.98 | 58.68% | 0 | 0% | 13.6 | 8.4 | 61.76% | 0 | 0% | 13.6 | 8.86 | 65.15% | 0 | 0% | 13.6 | 8.96 | 65.88% | 0 | 0% | 13.6 | 9.05 | 66.54% | 0 | 0%
GNA_253651112_Capacity | Central Valley | Kern | SHAFTER 1112 (Old 1101) | 253651112 | Feeder | Demand Growth | Capacity | 2023 | 108.9% | 0.93 | 8.891% | 10.46 | 11.39 | 108.9% | 0.93 | 8.891% | 10.46 | 11.37 | 108.7% | 0.91 | 8.7% | 10.46 | 11.36 | 108.6% | 0.9 | 8.604% | 10.46 | 11.36 | 108.6% | 0.9 | 8.604% | 10.46 | 11.34 | 108.4% | 0.88 | 8.413%
GNA_2545601_Capacity | Central Valley | Kern | TUPMAN BANK 1 | 2545601 | Bank | Demand Growth | Capacity | 2023 | 125.3% | 4 | 25.25% | 15.84 | 17.82 | 112.5% | 1.98 | 12.5% | 15.84 | 17.81 | 112.4% | 1.97 | 12.44% | 15.84 | 19.84 | 125.3% | 4 | 25.25% | 15.84 | 19.81 | 125.1% | 3.97 | 25.06% | 15.84 | 19.8 | 125% | 3.96 | 25%
GNA_254561103_Capacity | Central Valley | Kern | TUPMAN 1103 | 254561103 | Feeder | None | None | None | 81.05% | 0 | 0% | 12.19 | 9.88 | 81.05% | 0 | 0% | 12.19 | 9.87 | 80.97% | 0 | 0% | 12.19 | 9.86 | 80.89% | 0 | 0% | 12.19 | 9.86 | 80.89% | 0 | 0% | 12.19 | 9.84 | 80.72% | 0 | 0%
GNA_254561104_Capacity | Central Valley | Kern | TUPMAN 1104 | 254561104 | Feeder | None | None | None | 99.34% | 0 | 0% | 12.19 | 9.28 | 76.13% | 0 | 0% | 12.19 | 9.28 | 76.13% | 0 | 0% | 12.19 | 12.11 | 99.34% | 0 | 0% | 12.19 | 12.09 | 99.18% | 0 | 0% | 12.19 | 12.08 | 99.1% | 0 | 0%
GNA_2545602_Capacity | Central Valley | Kern | TUPMAN BANK 2 | 2545602 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254561105_Capacity | Central Valley | Kern | TUPMAN 1105 | 254561105 | Feeder | None | None | None | 50.77% | 0 | 0% | 14.26 | 7.24 | 50.77% | 0 | 0% | 14.26 | 7.24 | 50.77% | 0 | 0% | 14.26 | 7.24 | 50.77% | 0 | 0% | 14.26 | 7.22 | 50.63% | 0 | 0% | 14.26 | 7.22 | 50.63% | 0 | 0%
GNA_254561106_Capacity | Central Valley | Kern | TUPMAN 1106 | 254561106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2527801_Capacity | Central Valley | Kern | MCKITTRICK BANK 1 | 2527801 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252781101_Capacity | Central Valley | Kern | MCKITTRICK 1101 | 252781101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2525501_Capacity | Central Valley | Kern | TEMBLOR BANK 1 | 2525501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252551104_Capacity | Central Valley | Kern | TEMBLOR 1104 | 252551104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252552103_Capacity | Central Valley | Kern | TEMBLOR 2103 | 252552103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2536401_Capacity | Central Valley | Kern | POSO MOUNTAIN BANK 1 | 2536401 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253642101_Capacity | Central Valley | Kern | POSO MOUNTAIN 2101 | 253642101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2536402_Capacity | Central Valley | Kern | POSO MOUNTAIN BANK 2 | 2536402 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253642103_Capacity | Central Valley | Kern | POSO MOUNTAIN 2103 | 253642103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253642104_Capacity | Central Valley | Kern | POSO MOUNTAIN 2104 | 253642104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2538701_Capacity | Central Valley | Kern | COPUS BANK 1 | 2538701 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253871102_Capacity | Central Valley | Kern | COPUS 1102 | 253871102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253871103_Capacity | Central Valley | Kern | COPUS 1103 | 253871103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2538702_Capacity | Central Valley | Kern | COPUS BANK 2 | 2538702 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253871104_Capacity | Central Valley | Kern | COPUS 1104 | 253871104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2542401_Capacity | Central Valley | Kern | FELLOWS BANK 1 | 2542401 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254242103_Capacity | Central Valley | Kern | FELLOWS 2103 | 254242103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2542402_Capacity | Central Valley | Kern | FELLOWS BANK 2 | 2542402 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254242104_Capacity | Central Valley | Kern | FELLOWS 2104 | 254242104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2542101_Capacity | Central Valley | Kern | MARICOPA BANK 1 | 2542101 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254211101_Capacity | Central Valley | Kern | MARICOPA 1101 | 254211101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254211102_Capacity | Central Valley | Kern | MARICOPA 1102 | 254211102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2520803_Capacity | Central Valley | Kern | TAFT BANK 3 | 2520803 | Bank | None | None | None | 93.85% | 0 | 0% | 10.4 | 9.76 | 93.85% | 0 | 0% | 10.4 | 9.75 | 93.75% | 0 | 0% | 10.4 | 9.74 | 93.65% | 0 | 0% | 10.4 | 9.75 | 93.75% | 0 | 0% | 10.4 | 9.74 | 93.65% | 0 | 0%
GNA_252081101_Capacity | Central Valley | Kern | TAFT 1101 | 252081101 | Feeder | None | None | None | 51.38% | 0 | 0% | 10.16 | 5.21 | 51.28% | 0 | 0% | 10.16 | 5.22 | 51.38% | 0 | 0% | 10.16 | 5.22 | 51.38% | 0 | 0% | 10.16 | 5.22 | 51.38% | 0 | 0% | 10.16 | 5.22 | 51.38% | 0 | 0%
GNA_252081103_Capacity | Central Valley | Kern | TAFT 1103 | 252081103 | Feeder | None | None | None | 57.94% | 0 | 0% | 8.25 | 4.78 | 57.94% | 0 | 0% | 8.25 | 4.77 | 57.82% | 0 | 0% | 8.25 | 4.76 | 57.7% | 0 | 0% | 8.25 | 4.76 | 57.7% | 0 | 0% | 8.25 | 4.76 | 57.7% | 0 | 0%
GNA_2520804_Capacity | Central Valley | Kern | TAFT BANK 4 | 2520804 | Bank | None | None | None | 75.95% | 0 | 0% | 15.84 | 12.03 | 75.95% | 0 | 0% | 15.84 | 12 | 75.76% | 0 | 0% | 15.84 | 12 | 75.76% | 0 | 0% | 15.84 | 11.98 | 75.63% | 0 | 0% | 15.84 | 11.97 | 75.57% | 0 | 0%
GNA_252081104_Capacity | Central Valley | Kern | TAFT 1104 | 252081104 | Feeder | None | None | None | 80.4% | 0 | 0% | 10.46 | 8.41 | 80.4% | 0 | 0% | 10.46 | 8.4 | 80.31% | 0 | 0% | 10.46 | 8.39 | 80.21% | 0 | 0% | 10.46 | 8.38 | 80.11% | 0 | 0% | 10.46 | 8.37 | 80.02% | 0 | 0%
GNA_252081106_Capacity | Central Valley | Kern | TAFT 1106 | 252081106 | Feeder | None | None | None | 31.2% | 0 | 0% | 10.16 | 3.17 | 31.2% | 0 | 0% | 10.16 | 3.17 | 31.2% | 0 | 0% | 10.16 | 3.16 | 31.1% | 0 | 0% | 10.16 | 3.16 | 31.1% | 0 | 0% | 10.16 | 3.15 | 31% | 0 | 0%
GNA_252081108_Capacity | Central Valley | Kern | TAFT 1108 | 252081108 | Feeder | None | None | None | 16.04% | 0 | 0% | 10.16 | 1.63 | 16.04% | 0 | 0% | 10.16 | 1.63 | 16.04% | 0 | 0% | 10.16 | 1.63 | 16.04% | 0 | 0% | 10.16 | 1.63 | 16.04% | 0 | 0% | 10.16 | 1.63 | 16.04% | 0 | 0%
GNA_2533701_Capacity | Central Valley | Kern | BAKERSFIELD BANK 1 | 2533701 | Bank | None | None | None | 57.05% | 0 | 0% | 74.25 | 42.36 | 57.05% | 0 | 0% | 74.25 | 42.24 | 56.89% | 0 | 0% | 74.25 | 42.11 | 56.71% | 0 | 0% | 74.25 | 42.04 | 56.62% | 0 | 0% | 74.25 | 42.02 | 56.59% | 0 | 0%
GNA_2533706_Capacity | Central Valley | Kern | BAKERSFIELD BANK 6 | 2533706 | Bank | None | None | None | 91.72% | 0 | 0% | 29.7 | 27.24 | 91.72% | 0 | 0% | 29.7 | 27.07 | 91.14% | 0 | 0% | 29.7 | 26.89 | 90.54% | 0 | 0% | 29.7 | 26.79 | 90.2% | 0 | 0% | 29.7 | 26.68 | 89.83% | 0 | 0%
GNA_253371102_Capacity | Central Valley | Kern | BAKERSFIELD 1102 | 253371102 | Feeder | None | None | None | 86.14% | 0 | 0% | 12.19 | 10.5 | 86.14% | 0 | 0% | 12.19 | 10.39 | 85.23% | 0 | 0% | 12.19 | 10.32 | 84.66% | 0 | 0% | 12.19 | 10.37 | 85.07% | 0 | 0% | 12.19 | 10.43 | 85.56% | 0 | 0%
GNA_253371106_Capacity | Central Valley | Kern | BAKERSFIELD 1106 | 253371106 | Feeder | None | None | None | 89.85% | 0 | 0% | 11.33 | 10.18 | 89.85% | 0 | 0% | 11.33 | 10.14 | 89.5% | 0 | 0% | 11.33 | 10.11 | 89.23% | 0 | 0% | 11.33 | 10.09 | 89.06% | 0 | 0% | 11.33 | 10.05 | 88.7% | 0 | 0%
GNA_253371110_Capacity | Central Valley | Kern | BAKERSFIELD 1110 | 253371110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253372104_Capacity | Central Valley | Kern | BAKERSFIELD 2104 | 253372104 | Feeder | None | None | None | 89.43% | 0 | 0% | 18.63 | 16.66 | 89.43% | 0 | 0% | 18.63 | 16.65 | 89.37% | 0 | 0% | 18.63 | 16.61 | 89.16% | 0 | 0% | 18.63 | 16.5 | 88.57% | 0 | 0% | 18.63 | 16.43 | 88.19% | 0 | 0%
GNA_2533702_Capacity | Central Valley | Kern | BAKERSFIELD BANK 2 | 2533702 | Bank | None | None | None | 63.82% | 0 | 0% | 74.25 | 47.39 | 63.82% | 0 | 0% | 74.25 | 47.16 | 63.52% | 0 | 0% | 74.25 | 46.95 | 63.23% | 0 | 0% | 74.25 | 46.76 | 62.98% | 0 | 0% | 74.25 | 46.55 | 62.69% | 0 | 0%
GNA_2533705_Capacity | Central Valley | Kern | BAKERSFIELD BANK 5 | 2533705 | Bank | None | None | None | 86.41% | 0 | 0% | 34.28 | 29.62 | 86.41% | 0 | 0% | 34.28 | 29.45 | 85.91% | 0 | 0% | 34.28 | 29.27 | 85.39% | 0 | 0% | 34.28 | 29.12 | 84.95% | 0 | 0% | 34.28 | 28.93 | 84.39% | 0 | 0%
GNA_253371114_Capacity | Central Valley | Kern | BAKERSFIELD 1114 | 253371114 | Feeder | None | None | None | 85.52% | 0 | 0% | 11.67 | 9.98 | 85.52% | 0 | 0% | 11.67 | 9.9 | 84.83% | 0 | 0% | 11.67 | 9.81 | 84.06% | 0 | 0% | 11.67 | 9.71 | 83.2% | 0 | 0% | 11.67 | 9.63 | 82.52% | 0 | 0%
GNA_253371116_Capacity | Central Valley | Kern | BAKERSFIELD 1116 | 253371116 | Feeder | None | None | None | 95.49% | 0 | 0% | 12.19 | 11.64 | 95.49% | 0 | 0% | 12.19 | 11.54 | 94.67% | 0 | 0% | 12.19 | 11.43 | 93.77% | 0 | 0% | 12.19 | 11.38 | 93.36% | 0 | 0% | 12.19 | 11.4 | 93.52% | 0 | 0%
GNA_253371118_Capacity | Central Valley | Kern | BAKERSFIELD 1118 | 253371118 | Feeder | None | None | None | 85.18% | 0 | 0% | 11.67 | 9.94 | 85.18% | 0 | 0% | 11.67 | 9.85 | 84.4% | 0 | 0% | 11.67 | 9.79 | 83.89% | 0 | 0% | 11.67 | 9.72 | 83.29% | 0 | 0% | 11.67 | 9.65 | 82.69% | 0 | 0%
GNA_253372106_Capacity | Central Valley | Kern | BAKERSFIELD 2106 | 253372106 | Feeder | None | None | None | 67.68% | 0 | 0% | 21.63 | 14.64 | 67.68% | 0 | 0% | 21.63 | 14.49 | 66.99% | 0 | 0% | 21.63 | 14.35 | 66.34% | 0 | 0% | 21.63 | 14.16 | 65.46% | 0 | 0% | 21.63 | 13.96 | 64.54% | 0 | 0%
GNA_2533703_Capacity | Central Valley | Kern | BAKERSFIELD BANK 3 | 2533703 | Bank | None | None | None | 70.98% | 0 | 0% | 74.25 | 52.7 | 70.98% | 0 | 0% | 74.25 | 52.27 | 70.4% | 0 | 0% | 74.25 | 51.82 | 69.79% | 0 | 0% | 74.25 | 51.3 | 69.09% | 0 | 0% | 74.25 | 50.84 | 68.47% | 0 | 0%
GNA_253372109_Capacity | Central Valley | Kern | BAKERSFIELD 2109 | 253372109 | Feeder | None | None | None | 97.63% | 0 | 0% | 18.11 | 17.68 | 97.63% | 0 | 0% | 18.11 | 17.61 | 97.24% | 0 | 0% | 18.11 | 17.54 | 96.85% | 0 | 0% | 18.11 | 17.44 | 96.3% | 0 | 0% | 18.11 | 17.36 | 95.86% | 0 | 0%
GNA_2533704_Capacity | Central Valley | Kern | BAKERSFIELD BANK 4 | 2533704 | Bank | None | None | None | 98.79% | 0 | 0% | 34.65 | 34.23 | 98.79% | 0 | 0% | 34.65 | 34 | 98.12% | 0 | 0% | 34.65 | 33.75 | 97.4% | 0 | 0% | 34.65 | 33.54 | 96.8% | 0 | 0% | 34.65 | 33.41 | 96.42% | 0 | 0%
GNA_253371101_Capacity | Central Valley | Kern | BAKERSFIELD 1101 | 253371101 | Feeder | None | None | None | 43.31% | 0 | 0% | 10.46 | 4.53 | 43.31% | 0 | 0% | 10.46 | 4.5 | 43.02% | 0 | 0% | 10.46 | 4.5 | 43.02% | 0 | 0% | 10.46 | 4.5 | 43.02% | 0 | 0% | 10.46 | 4.53 | 43.31% | 0 | 0%
GNA_253371105_Capacity | Central Valley | Kern | BAKERSFIELD 1105 | 253371105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253371107_Capacity | Central Valley | Kern | BAKERSFIELD 1107 | 253371107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253371115_Capacity | Central Valley | Kern | BAKERSFIELD 1115 | 253371115 | Feeder | None | None | None | 80.48% | 0 | 0% | 12.19 | 9.81 | 80.48% | 0 | 0% | 12.19 | 9.77 | 80.15% | 0 | 0% | 12.19 | 9.74 | 79.9% | 0 | 0% | 12.19 | 9.72 | 79.74% | 0 | 0% | 12.19 | 9.68 | 79.41% | 0 | 0%
GNA_2554501_Capacity | Central Valley | Kern | CAL WATER BANK 1 | 2554501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_255451102_Capacity | Central Valley | Kern | CAL WATER 1102 | 255451102 | Feeder | None | None | None | 99.19% | 0 | 0% | 13.6 | 12.67 | 93.16% | 0 | 0% | 13.6 | 12.83 | 94.34% | 0 | 0% | 13.6 | 13 | 95.59% | 0 | 0% | 13.6 | 13.23 | 97.28% | 0 | 0% | 13.6 | 13.49 | 99.19% | 0 | 0%
GNA_255451103_Capacity | Central Valley | Kern | CAL WATER 1103 | 255451103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2539501_Capacity | Central Valley | Kern | COLUMBUS BANK 1 | 2539501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253951103_Capacity | Central Valley | Kern | COLUMBUS 1103 | 253951103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253951104_Capacity | Central Valley | Kern | COLUMBUS 1104 | 253951104 | Feeder | None | None | None | 97.4% | 0 | 0% | 10.76 | 10.48 | 97.4% | 0 | 0% | 10.76 | 10.42 | 96.84% | 0 | 0% | 10.76 | 10.33 | 96% | 0 | 0% | 10.76 | 10.28 | 95.54% | 0 | 0% | 10.76 | 10.26 | 95.35% | 0 | 0%
GNA_2539502_Capacity | Central Valley | Kern | COLUMBUS BANK 2 | 2539502 | Bank | None | None | None | 99.05% | 0 | 0% | 15.84 | 15.69 | 99.05% | 0 | 0% | 15.84 | 15.58 | 98.36% | 0 | 0% | 15.84 | 15.58 | 98.36% | 0 | 0% | 15.84 | 15.68 | 98.99% | 0 | 0% | 15.84 | 14.57 | 91.98% | 0 | 0%
GNA_253951105_Capacity | Central Valley | Kern | COLUMBUS 1105 | 253951105 | Feeder | None | None | None | 59.46% | 0 | 0% | 10.46 | 6.08 | 58.13% | 0 | 0% | 10.46 | 6.09 | 58.22% | 0 | 0% | 10.46 | 6.1 | 58.32% | 0 | 0% | 10.46 | 6.14 | 58.7% | 0 | 0% | 10.46 | 6.22 | 59.46% | 0 | 0%
GNA_253951106_Capacity | Central Valley | Kern | COLUMBUS 1106 | 253951106 | Feeder | None | None | None | 82.61% | 0 | 0% | 12.19 | 10.07 | 82.61% | 0 | 0% | 12.19 | 9.96 | 81.71% | 0 | 0% | 12.19 | 9.93 | 81.46% | 0 | 0% | 12.19 | 9.99 | 81.95% | 0 | 0% | 12.19 | 8.8 | 72.19% | 0 | 0%
GNA_2539503_Capacity | Central Valley | Kern | COLUMBUS BANK 3 | 2539503 | Bank | None | None | None | 99.62% | 0 | 0% | 23.66 | 22.88 | 96.7% | 0 | 0% | 23.66 | 22.9 | 96.79% | 0 | 0% | 23.66 | 22.99 | 97.17% | 0 | 0% | 23.66 | 23.28 | 98.39% | 0 | 0% | 23.66 | 23.57 | 99.62% | 0 | 0%
GNA_253951109_Capacity | Central Valley | Kern | COLUMBUS 1109 | 253951109 | Feeder | None | None | None | 92.92% | 0 | 0% | 14.26 | 12.55 | 88.01% | 0 | 0% | 14.26 | 12.65 | 88.71% | 0 | 0% | 14.26 | 12.76 | 89.48% | 0 | 0% | 14.26 | 13.01 | 91.23% | 0 | 0% | 14.26 | 13.25 | 92.92% | 0 | 0%
GNA_253951110_Capacity | Central Valley | Kern | COLUMBUS 1110 | 253951110 | Feeder | None | None | None | 83.18% | 0 | 0% | 12.19 | 10.14 | 83.18% | 0 | 0% | 12.19 | 10.08 | 82.69% | 0 | 0% | 12.19 | 10.04 | 82.36% | 0 | 0% | 12.19 | 10.04 | 82.36% | 0 | 0% | 12.19 | 10.05 | 82.44% | 0 | 0%
GNA_2527701_Capacity | Central Valley | Kern | MAGUNDEN BANK 1 | 2527701 | Bank | None | None | None | 96.32% | 0 | 0% | 44.55 | 42.18 | 94.68% | 0 | 0% | 44.55 | 42.13 | 94.57% | 0 | 0% | 44.55 | 42.1 | 94.5% | 0 | 0% | 44.55 | 42.43 | 95.24% | 0 | 0% | 44.55 | 42.91 | 96.32% | 0 | 0%
GNA_252771101_Capacity | Central Valley | Kern | MAGUNDEN 1101 | 252771101 | Feeder | None | None | None | 92.71% | 0 | 0% | 14.26 | 13.22 | 92.71% | 0 | 0% | 14.26 | 13.05 | 91.51% | 0 | 0% | 14.26 | 12.91 | 90.53% | 0 | 0% | 14.26 | 12.8 | 89.76% | 0 | 0% | 14.26 | 12.7 | 89.06% | 0 | 0%
GNA_252771104_Capacity | Central Valley | Kern | MAGUNDEN 1104 | 252771104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252771105_Capacity | Central Valley | Kern | MAGUNDEN 1105 | 252771105 | Feeder | None | None | None | 64.53% | 0 | 0% | 10.46 | 6.52 | 62.33% | 0 | 0% | 10.46 | 6.54 | 62.52% | 0 | 0% | 10.46 | 6.57 | 62.81% | 0 | 0% | 10.46 | 6.63 | 63.38% | 0 | 0% | 10.46 | 6.75 | 64.53% | 0 | 0%
GNA_252771106_Capacity | Central Valley | Kern | MAGUNDEN 1106 | 252771106 | Feeder | None | None | None | 35.48% | 0 | 0% | 14.26 | 4.89 | 34.29% | 0 | 0% | 14.26 | 4.9 | 34.36% | 0 | 0% | 14.26 | 4.9 | 34.36% | 0 | 0% | 14.26 | 4.96 | 34.78% | 0 | 0% | 14.26 | 5.06 | 35.48% | 0 | 0%
GNA_252771108_Capacity | Central Valley | Kern | MAGUNDEN 1108 | 252771108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2527703_Capacity | Central Valley | Kern | MAGUNDEN BANK 3 | 2527703 | Bank | None | None | None | 70.62% | 0 | 0% | 44.55 | 31.46 | 70.62% | 0 | 0% | 44.55 | 31.19 | 70.01% | 0 | 0% | 44.55 | 30.93 | 69.43% | 0 | 0% | 44.55 | 30.56 | 68.6% | 0 | 0% | 44.55 | 30.29 | 67.99% | 0 | 0%
GNA_252772108_Capacity | Central Valley | Kern | MAGUNDEN 2108 | 252772108 | Feeder | None | None | None | 100.3% | 0.07 | 0.315% | 22.22 | 22.29 | 100.3% | 0.07 | 0.315% | 22.22 | 22.11 | 99.5% | 0 | 0% | 22.22 | 21.95 | 98.78% | 0 | 0% | 22.22 | 21.65 | 97.43% | 0 | 0% | 22.22 | 21.34 | 96.04% | 0 | 0%
GNA_252772109_Capacity | Central Valley | Kern | MAGUNDEN 2109 | 252772109 | Feeder | None | None | None | 37.23% | 0 | 0% | 21.11 | 7.86 | 37.23% | 0 | 0% | 21.11 | 7.82 | 37.04% | 0 | 0% | 21.11 | 7.77 | 36.81% | 0 | 0% | 21.11 | 7.73 | 36.62% | 0 | 0% | 21.11 | 7.63 | 36.14% | 0 | 0%
GNA_2537001_Capacity | Central Valley | Kern | WESTPARK BANK 1 | 2537001 | Bank | None | None | None | 82.54% | 0 | 0% | 37.62 | 31.05 | 82.54% | 0 | 0% | 37.62 | 30.83 | 81.95% | 0 | 0% | 37.62 | 30.66 | 81.5% | 0 | 0% | 37.62 | 30.51 | 81.1% | 0 | 0% | 37.62 | 30.43 | 80.89% | 0 | 0%
GNA_253701101_Capacity | Central Valley | Kern | WESTPARK 1101 | 253701101 | Feeder | None | None | None | 64.4% | 0 | 0% | 12.19 | 7.85 | 64.4% | 0 | 0% | 12.19 | 7.78 | 63.82% | 0 | 0% | 12.19 | 7.74 | 63.49% | 0 | 0% | 12.19 | 7.68 | 63% | 0 | 0% | 12.19 | 7.64 | 62.67% | 0 | 0%
GNA_253701102_Capacity | Central Valley | Kern | WESTPARK 1102 | 253701102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253701103_Capacity | Central Valley | Kern | WESTPARK 1103 | 253701103 | Feeder | None | None | None | 93.59% | 0 | 0% | 10.76 | 10.07 | 93.59% | 0 | 0% | 10.76 | 10.01 | 93.03% | 0 | 0% | 10.76 | 9.95 | 92.47% | 0 | 0% | 10.76 | 9.9 | 92.01% | 0 | 0% | 10.76 | 9.85 | 91.54% | 0 | 0%
GNA_253701104_Capacity | Central Valley | Kern | WESTPARK 1104 | 253701104 | Feeder | None | None | None | 77.63% | 0 | 0% | 10.46 | 8.12 | 77.63% | 0 | 0% | 10.46 | 8.05 | 76.96% | 0 | 0% | 10.46 | 8.02 | 76.67% | 0 | 0% | 10.46 | 8 | 76.48% | 0 | 0% | 10.46 | 8.02 | 76.67% | 0 | 0%
GNA_2537002_Capacity | Central Valley | Kern | WESTPARK BANK 2 | 2537002 | Bank | None | None | None | 70.24% | 0 | 0% | 44.55 | 31.29 | 70.24% | 0 | 0% | 44.55 | 31.03 | 69.65% | 0 | 0% | 44.55 | 30.79 | 69.11% | 0 | 0% | 44.55 | 30.55 | 68.57% | 0 | 0% | 44.55 | 30.21 | 67.81% | 0 | 0%
GNA_253701105_Capacity | Central Valley | Kern | WESTPARK 1105 | 253701105 | Feeder | None | None | None | 48.73% | 0 | 0% | 12.19 | 5.94 | 48.73% | 0 | 0% | 12.19 | 5.92 | 48.56% | 0 | 0% | 12.19 | 5.88 | 48.24% | 0 | 0% | 12.19 | 5.86 | 48.07% | 0 | 0% | 12.19 | 5.82 | 47.74% | 0 | 0%
GNA_253701106_Capacity | Central Valley | Kern | WESTPARK 1106 | 253701106 | Feeder | None | None | None | 58.18% | 0 | 0% | 10.76 | 6.26 | 58.18% | 0 | 0% | 10.76 | 6.16 | 57.25% | 0 | 0% | 10.76 | 6.11 | 56.78% | 0 | 0% | 10.76 | 6.08 | 56.51% | 0 | 0% | 10.76 | 6.02 | 55.95% | 0 | 0%
GNA_253701107_Capacity | Central Valley | Kern | WESTPARK 1107 | 253701107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253701108_Capacity | Central Valley | Kern | WESTPARK 1108 | 253701108 | Feeder | None | None | None | 96.03% | 0 | 0% | 11.33 | 10.88 | 96.03% | 0 | 0% | 11.33 | 10.83 | 95.59% | 0 | 0% | 11.33 | 10.79 | 95.23% | 0 | 0% | 11.33 | 10.7 | 94.44% | 0 | 0% | 11.33 | 10.64 | 93.91% | 0 | 0%
GNA_2537003_Capacity | Central Valley | Kern | WESTPARK BANK 3 | 2537003 | Bank | None | None | None | 97.34% | 0 | 0% | 29.7 | 28.91 | 97.34% | 0 | 0% | 29.7 | 28.72 | 96.7% | 0 | 0% | 29.7 | 28.51 | 95.99% | 0 | 0% | 29.7 | 28.3 | 95.29% | 0 | 0% | 29.7 | 28.09 | 94.58% | 0 | 0%
GNA_253701109_Capacity | Central Valley | Kern | WESTPARK 1109 | 253701109 | Feeder | None | None | None | 88.02% | 0 | 0% | 12.19 | 10.73 | 88.02% | 0 | 0% | 12.19 | 10.66 | 87.45% | 0 | 0% | 12.19 | 10.61 | 87.04% | 0 | 0% | 12.19 | 10.56 | 86.63% | 0 | 0% | 12.19 | 10.49 | 86.05% | 0 | 0%
GNA_253701110_Capacity | Central Valley | Kern | WESTPARK 1110 | 253701110 | Feeder | None | None | None | 86.71% | 0 | 0% | 10.76 | 9.33 | 86.71% | 0 | 0% | 10.76 | 9.28 | 86.25% | 0 | 0% | 10.76 | 9.25 | 85.97% | 0 | 0% | 10.76 | 9.19 | 85.41% | 0 | 0% | 10.76 | 9.11 | 84.67% | 0 | 0%
GNA_253701111_Capacity | Central Valley | Kern | WESTPARK 1111 | 253701111 | Feeder | None | None | None | 48.14% | 0 | 0% | 10.76 | 5.18 | 48.14% | 0 | 0% | 10.76 | 5.15 | 47.86% | 0 | 0% | 10.76 | 5.12 | 47.58% | 0 | 0% | 10.76 | 5.08 | 47.21% | 0 | 0% | 10.76 | 5.07 | 47.12% | 0 | 0%
GNA_253701112_Capacity | Central Valley | Kern | WESTPARK 1112 | 253701112 | Feeder | None | None | None | 42.47% | 0 | 0% | 10.76 | 4.57 | 42.47% | 0 | 0% | 10.76 | 4.53 | 42.1% | 0 | 0% | 10.76 | 4.48 | 41.64% | 0 | 0% | 10.76 | 4.44 | 41.26% | 0 | 0% | 10.76 | 4.41 | 40.99% | 0 | 0%
GNA_2527201_Capacity | Central Valley | Kern | KERN OIL BANK 1 | 2527201 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252721103_Capacity | Central Valley | Kern | KERN OIL 1103 | 252721103 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252721107_Capacity | Central Valley | Kern | KERN OIL 1107 | 252721107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252721109_Capacity | Central Valley | Kern | KERN OIL 1109 | 252721109 | Feeder | Demand Growth | Capacity | 2023 | 101.5% | 0.16 | 1.53% | 10.46 | 10.62 | 101.5% | 0.16 | 1.53% | 10.46 | 10.56 | 101% | 0.1 | 0.956% | 10.46 | 10.47 | 100.1% | 0.01 | 0.0956% | 10.46 | 10.4 | 99.43% | 0 | 0% | 10.46 | 10.35 | 98.95% | 0 | 0%
GNA_2527202_Capacity | Central Valley | Kern | KERN OIL BANK 2 | 2527202 | Bank | None | None | None | 78.36% | 0 | 0% | 34.24 | 26.83 | 78.36% | 0 | 0% | 34.24 | 26.77 | 78.18% | 0 | 0% | 34.24 | 26.72 | 78.04% | 0 | 0% | 34.24 | 26.76 | 78.15% | 0 | 0% | 34.24 | 26.81 | 78.3% | 0 | 0%
GNA_252721110_Capacity | Central Valley | Kern | KERN OIL 1110 | 252721110 | Feeder | Demand Growth | Capacity | 2023 | 113% | 1.36 | 13% | 10.46 | 11.82 | 113% | 1.36 | 13% | 10.46 | 11.68 | 111.7% | 1.22 | 11.66% | 10.46 | 11.55 | 110.4% | 1.09 | 10.42% | 10.46 | 11.46 | 109.6% | 1 | 9.56% | 10.46 | 11.5 | 109.9% | 1.04 | 9.943%
GNA_252721114_Capacity | Central Valley | Kern | KERN OIL 1114 | 252721114 | Feeder | None | None | None | 74.88% | 0 | 0% | 10.31 | 7.54 | 73.13% | 0 | 0% | 10.31 | 7.58 | 73.52% | 0 | 0% | 10.31 | 7.61 | 73.81% | 0 | 0% | 10.31 | 7.68 | 74.49% | 0 | 0% | 10.31 | 7.72 | 74.88% | 0 | 0%
GNA_252721116_Capacity | Central Valley | Kern | KERN OIL 1116 | 252721116 | Feeder | None | None | None | 99.56% | 0 | 0% | 11.33 | 11.02 | 97.26% | 0 | 0% | 11.33 | 11.06 | 97.62% | 0 | 0% | 11.33 | 11.1 | 97.97% | 0 | 0% | 11.33 | 11.2 | 98.85% | 0 | 0% | 11.33 | 11.28 | 99.56% | 0 | 0%
GNA_2527203_Capacity | Central Valley | Kern | KERN OIL BANK 3 | 2527203 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252721104_Capacity | Central Valley | Kern | KERN OIL 1104 | 252721104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252721106_Capacity | Central Valley | Kern | KERN OIL 1106 | 252721106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252721108_Capacity | Central Valley | Kern | KERN OIL 1108 | 252721108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2545801_Capacity | Central Valley | Kern | 7TH STANDARD BANK 1 | 2545801 | Bank | Demand Growth | Capacity | 2024 | 138.4% | 17.1 | 38.38% | 44.55 | 44.53 | 99.96% | 0 | 0% | 44.55 | 47.29 | 106.2% | 2.74 | 6.15% | 44.55 | 59.63 | 133.8% | 15.08 | 33.85% | 44.55 | 60.01 | 134.7% | 15.46 | 34.7% | 44.55 | 61.65 | 138.4% | 17.1 | 38.38%
GNA_254582101_Capacity | Central Valley | Kern | 7TH STANDARD 2101 | 254582101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254582102_Capacity | Central Valley | Kern | 7TH STANDARD 2102 | 254582102 | Feeder | Demand Growth | Capacity | 2024 | 179.6% | 17.05 | 79.64% | 21.41 | 20.91 | 97.66% | 0 | 0% | 21.41 | 23.2 | 108.4% | 1.79 | 8.361% | 21.41 | 36.92 | 172.4% | 15.51 | 72.44% | 21.41 | 36.98 | 172.7% | 15.57 | 72.72% | 21.41 | 38.46 | 179.6% | 17.05 | 79.64%
GNA_254582103_Capacity | Central Valley | Kern | 7TH STANDARD 2103 | 254582103 | Feeder | Demand Growth | Capacity | 2023 | 112.4% | 1.09 | 12.37% | 8.81 | 9.05 | 102.7% | 0.24 | 2.724% | 8.81 | 9.55 | 108.4% | 0.74 | 8.4% | 8.81 | 9.65 | 109.5% | 0.84 | 9.535% | 8.81 | 9.77 | 110.9% | 0.96 | 10.9% | 8.81 | 9.9 | 112.4% | 1.09 | 12.37%
GNA_2533901_Capacity | Central Valley | Kern | FRUITVALE BANK 1 | 2533901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253391101_Capacity | Central Valley | Kern | FRUITVALE 1101 | 253391101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253391103_Capacity | Central Valley | Kern | FRUITVALE 1103 | 253391103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2533902_Capacity | Central Valley | Kern | FRUITVALE BANK 2 | 2533902 | Bank | None | None | None | 87.85% | 0 | 0% | 29.7 | 25.21 | 84.88% | 0 | 0% | 29.7 | 25.31 | 85.22% | 0 | 0% | 29.7 | 25.43 | 85.62% | 0 | 0% | 29.7 | 25.75 | 86.7% | 0 | 0% | 29.7 | 26.09 | 87.85% | 0 | 0%
GNA_253391104_Capacity | Central Valley | Kern | FRUITVALE 1104 | 253391104 | Feeder | None | None | None | 94.85% | 0 | 0% | 13.6 | 12.61 | 92.72% | 0 | 0% | 13.6 | 12.63 | 92.87% | 0 | 0% | 13.6 | 12.64 | 92.94% | 0 | 0% | 13.6 | 12.76 | 93.82% | 0 | 0% | 13.6 | 12.9 | 94.85% | 0 | 0%
GNA_253391106_Capacity | Central Valley | Kern | FRUITVALE 1106 | 253391106 | Feeder | None | None | None | 85.17% | 0 | 0% | 11.33 | 9.48 | 83.67% | 0 | 0% | 11.33 | 9.46 | 83.5% | 0 | 0% | 11.33 | 9.48 | 83.67% | 0 | 0% | 11.33 | 9.57 | 84.47% | 0 | 0% | 11.33 | 9.65 | 85.17% | 0 | 0%
GNA_253392108_Capacity | Central Valley | Kern | FRUITVALE 2108 | 253392108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2552606_Capacity | Central Valley | Kern | KERN POWER BANK 6 | 2552606 | Bank | None | None | None | 93.12% | 0 | 0% | 44.45 | 41.39 | 93.12% | 0 | 0% | 44.45 | 41.21 | 92.71% | 0 | 0% | 44.45 | 41.04 | 92.33% | 0 | 0% | 44.45 | 41.07 | 92.4% | 0 | 0% | 44.45 | 41.15 | 92.58% | 0 | 0%
GNA_255262101_Capacity | Central Valley | Kern | KERN POWER 2101 | 255262101 | Feeder | None | None | None | 71.86% | 0 | 0% | 24.7 | 17.21 | 69.68% | 0 | 0% | 24.7 | 17.22 | 69.72% | 0 | 0% | 24.7 | 17.31 | 70.08% | 0 | 0% | 24.7 | 17.51 | 70.89% | 0 | 0% | 24.7 | 17.75 | 71.86% | 0 | 0%
GNA_255262102_Capacity | Central Valley | Kern | KERN POWER 2102 | 255262102 | Feeder | None | None | None | 23.89% | 0 | 0% | 24.7 | 5.9 | 23.89% | 0 | 0% | 24.7 | 5.85 | 23.68% | 0 | 0% | 24.7 | 5.8 | 23.48% | 0 | 0% | 24.7 | 5.77 | 23.36% | 0 | 0% | 24.7 | 5.72 | 23.16% | 0 | 0%
GNA_255262103_Capacity | Central Valley | Kern | KERN POWER 2103 | 255262103 | Feeder | None | None | None | 94.9% | 0 | 0% | 24.7 | 23.44 | 94.9% | 0 | 0% | 24.7 | 23.17 | 93.81% | 0 | 0% | 24.7 | 22.9 | 92.71% | 0 | 0% | 24.7 | 22.68 | 91.82% | 0 | 0% | 24.7 | 22.59 | 91.46% | 0 | 0%
GNA_2552607_Capacity | Central Valley | Kern | KERN POWER BANK 7 | 2552607 | Bank | None | None | None | 90.95% | 0 | 0% | 44.55 | 40.52 | 90.95% | 0 | 0% | 44.55 | 38.66 | 86.78% | 0 | 0% | 44.55 | 38.41 | 86.22% | 0 | 0% | 44.55 | 38.21 | 85.77% | 0 | 0% | 44.55 | 38.17 | 85.68% | 0 | 0%
GNA_255262104_Capacity | Central Valley | Kern | KERN POWER 2104 | 255262104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_255262105_Capacity | Central Valley | Kern | KERN POWER 2105 | 255262105 | Feeder | None | None | None | 95.38% | 0 | 0% | 24.7 | 23.56 | 95.38% | 0 | 0% | 24.7 | 21.82 | 88.34% | 0 | 0% | 24.7 | 21.66 | 87.69% | 0 | 0% | 24.7 | 21.5 | 87.04% | 0 | 0% | 24.7 | 21.46 | 86.88% | 0 | 0%
GNA_2545701_Capacity | Central Valley | Kern | RENFRO BANK 1 | 2545701 | Bank | None | None | None | 96.39% | 0 | 0% | 44.55 | 41.63 | 93.45% | 0 | 0% | 44.55 | 41.81 | 93.85% | 0 | 0% | 44.55 | 42.03 | 94.34% | 0 | 0% | 44.55 | 42.45 | 95.29% | 0 | 0% | 44.55 | 42.94 | 96.39% | 0 | 0%
GNA_254572101_Capacity | Central Valley | Kern | RENFRO 2101 | 254572101 | Feeder | Demand Growth | Capacity | 2023 | 107.1% | 1.67 | 7.088% | 23.56 | 24.85 | 105.5% | 1.29 | 5.475% | 23.56 | 24.87 | 105.6% | 1.31 | 5.56% | 23.56 | 24.9 | 105.7% | 1.34 | 5.688% | 23.56 | 25.05 | 106.3% | 1.49 | 6.324% | 23.56 | 25.23 | 107.1% | 1.67 | 7.088%
GNA_254572102_Capacity | Central Valley | Kern | RENFRO 2102 | 254572102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254572103_Capacity | Central Valley | Kern | RENFRO 2103 | 254572103 | Feeder | None | None | None | 84.75% | 0 | 0% | 12.26 | 9.88 | 80.59% | 0 | 0% | 12.26 | 9.98 | 81.4% | 0 | 0% | 12.26 | 10.07 | 82.14% | 0 | 0% | 12.26 | 10.22 | 83.36% | 0 | 0% | 12.26 | 10.39 | 84.75% | 0 | 0%
GNA_2545702_Capacity | Central Valley | Kern | RENFRO BANK 2 | 2545702 | Bank | None | None | None | 79.67% | 0 | 0% | 44.52 | 33.18 | 74.53% | 0 | 0% | 44.52 | 34.85 | 78.28% | 0 | 0% | 44.52 | 34.94 | 78.48% | 0 | 0% | 44.52 | 35.17 | 79% | 0 | 0% | 44.52 | 35.47 | 79.67% | 0 | 0%
GNA_254572105_Capacity | Central Valley | Kern | RENFRO 2105 | 254572105 | Feeder | None | None | None | 62.15% | 0 | 0% | 24.7 | 15.35 | 62.15% | 0 | 0% | 24.7 | 15.25 | 61.74% | 0 | 0% | 24.7 | 15.15 | 61.34% | 0 | 0% | 24.7 | 15.11 | 61.17% | 0 | 0% | 24.7 | 15.09 | 61.09% | 0 | 0%
GNA_254572107_Capacity | Central Valley | Kern | RENFRO 2107 | 254572107 | Feeder | None | None | None | 81.3% | 0 | 0% | 24.7 | 17.89 | 72.43% | 0 | 0% | 24.7 | 19.61 | 79.39% | 0 | 0% | 24.7 | 19.71 | 79.8% | 0 | 0% | 24.7 | 19.88 | 80.49% | 0 | 0% | 24.7 | 20.08 | 81.3% | 0 | 0%
GNA_2547601_Capacity | Central Valley | Kern | ROSEDALE BANK 1 | 2547601 | Bank | None | None | None | 70.47% | 0 | 0% | 29.7 | 20.93 | 70.47% | 0 | 0% | 29.7 | 20.74 | 69.83% | 0 | 0% | 29.7 | 20.49 | 68.99% | 0 | 0% | 29.7 | 20.34 | 68.48% | 0 | 0% | 29.7 | 20.23 | 68.11% | 0 | 0%
GNA_254761101_Capacity | Central Valley | Kern | ROSEDALE 1101 | 254761101 | Feeder | None | None | None | 63.74% | 0 | 0% | 15.14 | 9.65 | 63.74% | 0 | 0% | 15.14 | 9.54 | 63.01% | 0 | 0% | 15.14 | 9.48 | 62.62% | 0 | 0% | 15.14 | 9.52 | 62.88% | 0 | 0% | 15.14 | 9.58 | 63.28% | 0 | 0%
GNA_254762102_Capacity | Central Valley | Kern | ROSEDALE 2102 | 254762102 | Feeder | None | None | None | 60.76% | 0 | 0% | 21.38 | 12.99 | 60.76% | 0 | 0% | 21.38 | 12.9 | 60.34% | 0 | 0% | 21.38 | 12.77 | 59.73% | 0 | 0% | 21.38 | 12.62 | 59.03% | 0 | 0% | 21.38 | 12.47 | 58.33% | 0 | 0%
GNA_2534201_Capacity | Central Valley | Kern | PANAMA BANK 1 | 2534201 | Bank | Demand Growth | Capacity | 2024 | 107% | 3.12 | 7.003% | 44.55 | 44.16 | 99.12% | 0 | 0% | 44.55 | 45.06 | 101.1% | 0.51 | 1.145% | 44.55 | 47.65 | 107% | 3.1 | 6.958% | 44.55 | 47.53 | 106.7% | 2.98 | 6.689% | 44.55 | 47.67 | 107% | 3.12 | 7.003%
GNA_253422101_Capacity | Central Valley | Kern | PANAMA 2101 | 253422101 | Feeder | Demand Growth | Capacity | 2025 | 108.6% | 1.96 | 8.563% | 22.89 | 21.08 | 92.09% | 0 | 0% | 22.89 | 22.06 | 96.37% | 0 | 0% | 22.89 | 24.72 | 108% | 1.83 | 7.995% | 22.89 | 24.73 | 108% | 1.84 | 8.038% | 22.89 | 24.85 | 108.6% | 1.96 | 8.563%
GNA_253422102_Capacity | Central Valley | Kern | PANAMA 2102 | 253422102 | Feeder | None | None | None | 96.77% | 0 | 0% | 23.56 | 22.8 | 96.77% | 0 | 0% | 23.56 | 22.72 | 96.43% | 0 | 0% | 23.56 | 22.65 | 96.14% | 0 | 0% | 23.56 | 22.54 | 95.67% | 0 | 0% | 23.56 | 22.68 | 96.26% | 0 | 0%
GNA_2540701_Capacity | Central Valley | Kern | STOCKDALE BANK 1 | 2540701 | Bank | None | None | None | 77.24% | 0 | 0% | 29.7 | 22.87 | 77% | 0 | 0% | 29.7 | 22.94 | 77.24% | 0 | 0% | 29.7 | 22.92 | 77.17% | 0 | 0% | 29.7 | 22.89 | 77.07% | 0 | 0% | 29.7 | 22.88 | 77.04% | 0 | 0%
GNA_254071109_Capacity | Central Valley | Kern | STOCKDALE 1109 | 254071109 | Feeder | None | None | None | 74.94% | 0 | 0% | 13.21 | 9.55 | 72.29% | 0 | 0% | 13.21 | 9.71 | 73.5% | 0 | 0% | 13.21 | 9.77 | 73.96% | 0 | 0% | 13.21 | 9.83 | 74.41% | 0 | 0% | 13.21 | 9.9 | 74.94% | 0 | 0%
GNA_254071110_Capacity | Central Valley | Kern | STOCKDALE 1110 | 254071110 | Feeder | None | None | None | 62.6% | 0 | 0% | 13.21 | 8.27 | 62.6% | 0 | 0% | 13.21 | 8.23 | 62.3% | 0 | 0% | 13.21 | 8.19 | 62% | 0 | 0% | 13.21 | 8.15 | 61.7% | 0 | 0% | 13.21 | 8.11 | 61.39% | 0 | 0%
GNA_254071111_Capacity | Central Valley | Kern | STOCKDALE 1111 | 254071111 | Feeder | None | None | None | 68.87% | 0 | 0% | 10.76 | 7.41 | 68.87% | 0 | 0% | 10.76 | 7.36 | 68.4% | 0 | 0% | 10.76 | 7.36 | 68.4% | 0 | 0% | 10.76 | 7.36 | 68.4% | 0 | 0% | 10.76 | 7.37 | 68.49% | 0 | 0%
GNA_2540702_Capacity | Central Valley | Kern | STOCKDALE BANK 2 | 2540702 | Bank | None | None | None | 92.89% | 0 | 0% | 74.25 | 68.97 | 92.89% | 0 | 0% | 74.25 | 68.03 | 91.62% | 0 | 0% | 74.25 | 67.49 | 90.9% | 0 | 0% | 74.25 | 67.18 | 90.48% | 0 | 0% | 74.25 | 67.08 | 90.34% | 0 | 0%
GNA_254072108_Capacity | Central Valley | Kern | STOCKDALE 2108 | 254072108 | Feeder | None | None | None | 65.87% | 0 | 0% | 24.7 | 16.27 | 65.87% | 0 | 0% | 24.7 | 16.06 | 65.02% | 0 | 0% | 24.7 | 15.93 | 64.49% | 0 | 0% | 24.7 | 15.85 | 64.17% | 0 | 0% | 24.7 | 15.83 | 64.09% | 0 | 0%
GNA_254072109_Capacity | Central Valley | Kern | STOCKDALE 2109 | 254072109 | Feeder | None | None | None | 96.7% | 0 | 0% | 22.11 | 21.35 | 96.56% | 0 | 0% | 22.11 | 21.33 | 96.47% | 0 | 0% | 22.11 | 21.32 | 96.43% | 0 | 0% | 22.11 | 21.32 | 96.43% | 0 | 0% | 22.11 | 21.38 | 96.7% | 0 | 0%
GNA_254072110_Capacity | Central Valley | Kern | STOCKDALE 2110 | 254072110 | Feeder | None | None | None | 63.76% | 0 | 0% | 21.41 | 13.65 | 63.76% | 0 | 0% | 21.41 | 13.45 | 62.82% | 0 | 0% | 21.41 | 13.27 | 61.98% | 0 | 0% | 21.41 | 13.08 | 61.09% | 0 | 0% | 21.41 | 12.97 | 60.58% | 0 | 0%
GNA_254072111_Capacity | Central Valley | Kern | STOCKDALE 2111 | 254072111 | Feeder | None | None | None | 74.59% | 0 | 0% | 21.41 | 15.97 | 74.59% | 0 | 0% | 21.41 | 15.64 | 73.05% | 0 | 0% | 21.41 | 15.38 | 71.84% | 0 | 0% | 21.41 | 15.11 | 70.57% | 0 | 0% | 21.41 | 15.05 | 70.29% | 0 | 0%
GNA_2540703_Capacity | Central Valley | Kern | STOCKDALE BANK 3 | 2540703 | Bank | None | None | None | 94.95% | 0 | 0% | 74.25 | 70.04 | 94.33% | 0 | 0% | 74.25 | 70.24 | 94.6% | 0 | 0% | 74.25 | 70.5 | 94.95% | 0 | 0% | 74.25 | 70.37 | 94.77% | 0 | 0% | 74.25 | 70.31 | 94.69% | 0 | 0%
GNA_254072112_Capacity | Central Valley | Kern | STOCKDALE 2112 | 254072112 | Feeder | Demand Growth | Capacity | 2023 | 119.3% | 4.54 | 19.27% | 23.56 | 27.98 | 118.8% | 4.42 | 18.76% | 23.56 | 27.97 | 118.7% | 4.41 | 18.72% | 23.56 | 27.97 | 118.7% | 4.41 | 18.72% | 23.56 | 27.98 | 118.8% | 4.42 | 18.76% | 23.56 | 28.1 | 119.3% | 4.54 | 19.27%
GNA_254072113_Capacity | Central Valley | Kern | STOCKDALE 2113 | 254072113 | Feeder | None | None | None | 80.65% | 0 | 0% | 22.89 | 18.46 | 80.65% | 0 | 0% | 22.89 | 18.3 | 79.95% | 0 | 0% | 22.89 | 18.11 | 79.12% | 0 | 0% | 22.89 | 17.99 | 78.59% | 0 | 0% | 22.89 | 17.88 | 78.11% | 0 | 0%
GNA_254072114_Capacity | Central Valley | Kern | STOCKDALE 2114 | 254072114 | Feeder | None | None | None | 57.1% | 0 | 0% | 22.89 | 13.07 | 57.1% | 0 | 0% | 22.89 | 12.96 | 56.62% | 0 | 0% | 22.89 | 12.9 | 56.36% | 0 | 0% | 22.89 | 12.88 | 56.27% | 0 | 0% | 22.89 | 12.86 | 56.18% | 0 | 0%
GNA_254072115_Capacity | Central Valley | Kern | STOCKDALE 2115 | 254072115 | Feeder | None | None | None | 77.55% | 0 | 0% | 22.67 | 16.77 | 73.97% | 0 | 0% | 22.67 | 17.17 | 75.74% | 0 | 0% | 22.67 | 17.58 | 77.55% | 0 | 0% | 22.67 | 17.55 | 77.42% | 0 | 0% | 22.67 | 17.55 | 77.42% | 0 | 0%
GNA_2540704_Capacity | Central Valley | Kern | STOCKDALE BANK 4 | 2540704 | Bank | None | None | None | 18.5% | 0 | 0% | 44.55 | 8.24 | 18.5% | 0 | 0% | 44.55 | 8.21 | 18.43% | 0 | 0% | 44.55 | 8.15 | 18.29% | 0 | 0% | 44.55 | 8.13 | 18.25% | 0 | 0% | 44.55 | 8.14 | 18.27% | 0 | 0%
GNA_254071108_Capacity | Central Valley | Kern | STOCKDALE 1108 | 254071108 | Feeder | None | None | None | 78.75% | 0 | 0% | 10.73 | 8.45 | 78.75% | 0 | 0% | 10.73 | 8.41 | 78.38% | 0 | 0% | 10.73 | 8.36 | 77.91% | 0 | 0% | 10.73 | 8.34 | 77.73% | 0 | 0% | 10.73 | 8.35 | 77.82% | 0 | 0%
GNA_2540706_Capacity | Central Valley | Kern | STOCKDALE BANK 6 | 2540706 | Bank | None | None | None | 92.59% | 0 | 0% | 74.25 | 68.75 | 92.59% | 0 | 0% | 74.25 | 68.49 | 92.24% | 0 | 0% | 74.25 | 68.2 | 91.85% | 0 | 0% | 74.25 | 68.13 | 91.76% | 0 | 0% | 74.25 | 68.01 | 91.6% | 0 | 0%
GNA_254072105_Capacity | Central Valley | Kern | STOCKDALE 2105 | 254072105 | Feeder | None | None | None | 96.31% | 0 | 0% | 23.56 | 22.69 | 96.31% | 0 | 0% | 23.56 | 22.58 | 95.84% | 0 | 0% | 23.56 | 22.42 | 95.16% | 0 | 0% | 23.56 | 22.36 | 94.91% | 0 | 0% | 23.56 | 22.3 | 94.65% | 0 | 0%
GNA_254072106_Capacity | Central Valley | Kern | STOCKDALE 2106 | 254072106 | Feeder | None | None | None | 42.64% | 0 | 0% | 22.89 | 9.76 | 42.64% | 0 | 0% | 22.89 | 9.62 | 42.03% | 0 | 0% | 22.89 | 9.56 | 41.76% | 0 | 0% | 22.89 | 9.53 | 41.63% | 0 | 0% | 22.89 | 9.44 | 41.24% | 0 | 0%
GNA_254072107_Capacity | Central Valley | Kern | STOCKDALE 2107 | 254072107 | Feeder | None | None | None | 89.16% | 0 | 0% | 18.63 | 16.61 | 89.16% | 0 | 0% | 18.63 | 16.42 | 88.14% | 0 | 0% | 18.63 | 16.22 | 87.06% | 0 | 0% | 18.63 | 16.16 | 86.74% | 0 | 0% | 18.63 | 16.18 | 86.85% | 0 | 0%
GNA_2540705_Capacity | Central Valley | Kern | STOCKDALE BANK 5 | 2540705 | Bank | None | None | None | 71.41% | 0 | 0% | 29.7 | 21.21 | 71.41% | 0 | 0% | 29.7 | 21.19 | 71.35% | 0 | 0% | 29.7 | 21.19 | 71.35% | 0 | 0% | 29.7 | 21.15 | 71.21% | 0 | 0% | 29.7 | 21.19 | 71.35% | 0 | 0%
GNA_254071105_Capacity | Central Valley | Kern | STOCKDALE 1105 | 254071105 | Feeder | None | None | None | 95.15% | 0 | 0% | 13.6 | 12.92 | 95% | 0 | 0% | 13.6 | 12.9 | 94.85% | 0 | 0% | 13.6 | 12.92 | 95% | 0 | 0% | 13.6 | 12.91 | 94.93% | 0 | 0% | 13.6 | 12.94 | 95.15% | 0 | 0%
GNA_254071106_Capacity | Central Valley | Kern | STOCKDALE 1106 | 254071106 | Feeder | None | None | None | 74.69% | 0 | 0% | 12.25 | 9.15 | 74.69% | 0 | 0% | 12.25 | 9.09 | 74.2% | 0 | 0% | 12.25 | 9.03 | 73.71% | 0 | 0% | 12.25 | 8.97 | 73.22% | 0 | 0% | 12.25 | 9.01 | 73.55% | 0 | 0%
GNA_2553201_Capacity | Central Valley | Kern | TEVIS BANK 1 | 2553201 | Bank | Demand Growth | Capacity | 2027 | 101.1% | 0.47 | 1.058% | 44.44 | 44.49 | 100.1% | 0.05 | 0.1125% | 44.44 | 44.07 | 99.17% | 0 | 0% | 44.44 | 44.17 | 99.39% | 0 | 0% | 44.44 | 44.47 | 100.1% | 0.03 | 0.06751% | 44.44 | 44.91 | 101.1% | 0.47 | 1.058%
GNA_255322101_Capacity | Central Valley | Kern | TEVIS 2101 | 255322101 | Feeder | None | None | None | 100% | 0 | 0% | 18.85 | 18.67 | 99.05% | 0 | 0% | 18.85 | 18.22 | 96.66% | 0 | 0% | 18.85 | 18.51 | 98.2% | 0 | 0% | 18.85 | 18.67 | 99.05% | 0 | 0% | 18.85 | 18.85 | 100% | 0 | 0%
GNA_255322102_Capacity | Central Valley | Kern | TEVIS 2102 | 255322102 | Feeder | None | None | None | 62.12% | 0 | 0% | 18.11 | 11.12 | 61.4% | 0 | 0% | 18.11 | 11.24 | 62.07% | 0 | 0% | 18.11 | 11.19 | 61.79% | 0 | 0% | 18.11 | 11.17 | 61.68% | 0 | 0% | 18.11 | 11.25 | 62.12% | 0 | 0%
GNA_255322103_Capacity | Central Valley | Kern | TEVIS 2103 | 255322103 | Feeder | None | None | None | 69.02% | 0 | 0% | 18.11 | 12.5 | 69.02% | 0 | 0% | 18.11 | 12.48 | 68.91% | 0 | 0% | 18.11 | 12.45 | 68.75% | 0 | 0% | 18.11 | 12.45 | 68.75% | 0 | 0% | 18.11 | 12.49 | 68.97% | 0 | 0%
GNA_2553202_Capacity | Central Valley | Kern | TEVIS BANK 2 | 2553202 | Bank | None | None | None | 99.17% | 0 | 0% | 44.55 | 41.89 | 94.03% | 0 | 0% | 44.55 | 43.91 | 98.56% | 0 | 0% | 44.55 | 43.84 | 98.41% | 0 | 0% | 44.55 | 43.96 | 98.68% | 0 | 0% | 44.55 | 44.18 | 99.17% | 0 | 0%
GNA_255322104_Capacity | Central Valley | Kern | TEVIS 2104 | 255322104 | Feeder | None | None | None | 99.32% | 0 | 0% | 23.56 | 22.42 | 95.16% | 0 | 0% | 23.56 | 23.11 | 98.09% | 0 | 0% | 23.56 | 23.12 | 98.13% | 0 | 0% | 23.56 | 23.24 | 98.64% | 0 | 0% | 23.56 | 23.4 | 99.32% | 0 | 0%
GNA_255322105_Capacity | Central Valley | Kern | TEVIS 2105 | 255322105 | Feeder | Demand Growth | Capacity | 2024 | 101.4% | 0.32 | 1.358% | 23.56 | 22.55 | 95.71% | 0 | 0% | 23.56 | 23.88 | 101.4% | 0.32 | 1.358% | 23.56 | 23.81 | 101.1% | 0.25 | 1.061% | 23.56 | 23.81 | 101.1% | 0.25 | 1.061% | 23.56 | 23.88 | 101.4% | 0.32 | 1.358%
GNA_2545001_Capacity | Central Valley | Kern | CHARCA BANK 1 | 2545001 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254501102_Capacity | Central Valley | Kern | CHARCA 1102 | 254501102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254501103_Capacity | Central Valley | Kern | CHARCA 1103 | 254501103 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2545002_Capacity | Central Valley | Kern | CHARCA BANK 2 | 2545002 | Bank | None | None | None | 97.47% | 0 | 0% | 9.5 | 8.73 | 91.89% | 0 | 0% | 9.5 | 8.69 | 91.47% | 0 | 0% | 9.5 | 8.77 | 92.32% | 0 | 0% | 9.5 | 8.98 | 94.53% | 0 | 0% | 9.5 | 9.26 | 97.47% | 0 | 0%
GNA_254501106_Capacity | Central Valley | Kern | CHARCA 1106 | 254501106 | Feeder | None | None | None | 74.65% | 0 | 0% | 12.19 | 8.55 | 70.14% | 0 | 0% | 12.19 | 8.52 | 69.89% | 0 | 0% | 12.19 | 8.6 | 70.55% | 0 | 0% | 12.19 | 8.81 | 72.27% | 0 | 0% | 12.19 | 9.1 | 74.65% | 0 | 0%
GNA_2524601_Capacity | Central Valley | Kern | FAMOSO BANK 1 | 2524601 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252461101_Capacity | Central Valley | Kern | FAMOSO 1101 | 252461101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252461102_Capacity | Central Valley | Kern | FAMOSO 1102 | 252461102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252461103_Capacity | Central Valley | Kern | FAMOSO 1103 | 252461103 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252461105_Capacity | Central Valley | Kern | FAMOSO 1105 | 252461105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252461107_Capacity | Central Valley | Kern | FAMOSO 1107 | 252461107 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2545401_Capacity | Central Valley | Kern | GANSO BANK 1 | 2545401 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254541103_Capacity | Central Valley | Kern | GANSO 1103 | 254541103 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254541104_Capacity | Central Valley | Kern | GANSO 1104 | 254541104 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2542001_Capacity | Central Valley | Kern | GOOSE LAKE BANK 1 | 2542001 | Bank | Demand Growth | Capacity | 2025 | 127% | 4.28 | 27.02% | 15.84 | 15.39 | 97.16% | 0 | 0% | 15.84 | 15.47 | 97.66% | 0 | 0% | 15.84 | 19.94 | 125.9% | 4.1 | 25.88% | 15.84 | 20.04 | 126.5% | 4.2 | 26.52% | 15.84 | 20.12 | 127% | 4.28 | 27.02%
GNA_254201103_Capacity | Central Valley | Kern | GOOSE LAKE 1103 | 254201103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254202104_Capacity | Central Valley | Kern | GOOSE LAKE 2104 | 254202104 | Feeder | Demand Growth | Capacity | 2025 | 151.2% | 5.97 | 51.16% | 11.67 | 9.26 | 79.35% | 0 | 0% | 11.67 | 9.35 | 80.12% | 0 | 0% | 11.67 | 17.47 | 149.7% | 5.8 | 49.7% | 11.67 | 17.56 | 150.5% | 5.89 | 50.47% | 11.67 | 17.64 | 151.2% | 5.97 | 51.16%
GNA_2542002_Capacity | Central Valley | Kern | GOOSE LAKE BANK 2 | 2542002 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254201106_Capacity | Central Valley | Kern | GOOSE LAKE 1106 | 254201106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2531801_Capacity | Central Valley | Kern | MC FARLAND BANK 1 | 2531801 | Bank | None | None | None | 88.51% | 0 | 0% | 15.84 | 14.02 | 88.51% | 0 | 0% | 15.84 | 14.01 | 88.45% | 0 | 0% | 15.84 | 14.01 | 88.45% | 0 | 0% | 15.84 | 14.01 | 88.45% | 0 | 0% | 15.84 | 14 | 88.38% | 0 | 0%
GNA_253181101_Capacity | Central Valley | Kern | MC FARLAND 1101 | 253181101 | Feeder | None | None | None | 67.5% | 0 | 0% | 10.46 | 7.06 | 67.5% | 0 | 0% | 10.46 | 7.05 | 67.4% | 0 | 0% | 10.46 | 7.05 | 67.4% | 0 | 0% | 10.46 | 7.06 | 67.5% | 0 | 0% | 10.46 | 7.04 | 67.3% | 0 | 0%
GNA_253181102_Capacity | Central Valley | Kern | MC FARLAND 1102 | 253181102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2531802_Capacity | Central Valley | Kern | MC FARLAND BANK 2 | 2531802 | Bank | Demand Growth | Capacity | 2023 | 102% | 0.32 | 2.02% | 15.84 | 16.16 | 102% | 0.32 | 2.02% | 15.84 | 16.14 | 101.9% | 0.3 | 1.894% | 15.84 | 16.13 | 101.8% | 0.29 | 1.831% | 15.84 | 16.11 | 101.7% | 0.27 | 1.705% | 15.84 | 16.1 | 101.6% | 0.26 | 1.641%
GNA_253181105_Capacity | Central Valley | Kern | MC FARLAND 1105 | 253181105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253181104_Capacity | Central Valley | Kern | MC FARLAND 1104 | 253181104 | Feeder | Demand Growth | Capacity | 2023 | 108.7% | 1.02 | 8.74% | 11.67 | 12.69 | 108.7% | 1.02 | 8.74% | 11.67 | 12.69 | 108.7% | 1.02 | 8.74% | 11.67 | 12.68 | 108.7% | 1.01 | 8.655% | 11.67 | 12.67 | 108.6% | 1 | 8.569% | 11.67 | 12.67 | 108.6% | 1 | 8.569%
GNA_2529003_Capacity | Central Valley | Kern | SEMITROPIC BANK 3 | 2529003 | Bank | Demand Growth | Capacity | 2023 | 142.6% | 12.66 | 42.64% | 29.69 | 40.6 | 136.7% | 10.91 | 36.75% | 29.69 | 41.86 | 141% | 12.17 | 40.99% | 29.69 | 41.95 | 141.3% | 12.26 | 41.29% | 29.69 | 42.13 | 141.9% | 12.44 | 41.9% | 29.69 | 42.35 | 142.6% | 12.66 | 42.64%
GNA_252901104_Capacity | Central Valley | Kern | SEMITROPIC 1104 | 252901104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252901106_Capacity | Central Valley | Kern | SEMITROPIC 1106 | 252901106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252901108_Capacity | Central Valley | Kern | SEMITROPIC 1108 | 252901108 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252901110_Capacity | Central Valley | Kern | SEMITROPIC 1110 | 252901110 | Feeder | Demand Growth | Capacity | 2023 | 119.9% | 2.42 | 19.85% | 12.19 | 13.75 | 112.8% | 1.56 | 12.8% | 12.19 | 14.1 | 115.7% | 1.91 | 15.67% | 12.19 | 14.2 | 116.5% | 2.01 | 16.49% | 12.19 | 14.4 | 118.1% | 2.21 | 18.13% | 12.19 | 14.61 | 119.9% | 2.42 | 19.85%
GNA_252901112_Capacity | Central Valley | Kern | SEMITROPIC 1112 | 252901112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2535501_Capacity | Central Valley | Kern | SMYRNA BANK 1 | 2535501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253551101_Capacity | Central Valley | Kern | SMYRNA 1101 | 253551101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253551102_Capacity | Central Valley | Kern | SMYRNA 1102 | 253551102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2535502_Capacity | Central Valley | Kern | SMYRNA BANK 2 | 2535502 | Bank | None | None | None | 95.89% | 0 | 0% | 29.7 | 28.35 | 95.45% | 0 | 0% | 29.7 | 28.48 | 95.89% | 0 | 0% | 29.7 | 28.43 | 95.72% | 0 | 0% | 29.7 | 28.41 | 95.66% | 0 | 0% | 29.7 | 28.39 | 95.59% | 0 | 0%
GNA_253551104_Capacity | Central Valley | Kern | SMYRNA 1104 | 253551104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253551105_Capacity | Central Valley | Kern | SMYRNA 1105 | 253551105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253551106_Capacity | Central Valley | Kern | SMYRNA 1106 | 253551106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2529601_Capacity | Central Valley | Kern | WASCO BANK 1 | 2529601 | Bank | Demand Growth | Capacity | 2027 | 101.5% | 0.27 | 1.531% | 17.63 | 17.05 | 96.71% | 0 | 0% | 17.63 | 17.17 | 97.39% | 0 | 0% | 17.63 | 17.34 | 98.36% | 0 | 0% | 17.63 | 17.62 | 99.94% | 0 | 0% | 17.63 | 17.9 | 101.5% | 0.27 | 1.531%
GNA_252961101_Capacity | Central Valley | Kern | WASCO 1101 | 252961101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252961102_Capacity | Central Valley | Kern | WASCO 1102 | 252961102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252961104_Capacity | Central Valley | Kern | WASCO 1104 | 252961104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1825601_Capacity | South Bay and Central Coast | Los Padres | CHOLAME BANK 1 | 1825601 | Bank | None | None | None | 57.22% | 0 | 0% | 12.32 | 7.05 | 57.22% | 0 | 0% | 12.32 | 6.96 | 56.49% | 0 | 0% | 12.32 | 6.96 | 56.49% | 0 | 0% | 12.32 | 6.97 | 56.57% | 0 | 0% | 12.32 | 6.99 | 56.74% | 0 | 0%
GNA_182561101_Capacity | South Bay and Central Coast | Los Padres | CHOLAME 1101 | 182561101 | Feeder | None | None | None | 88.56% | 0 | 0% | 8.13 | 7.2 | 88.56% | 0 | 0% | 8.13 | 7.12 | 87.58% | 0 | 0% | 8.13 | 7.11 | 87.45% | 0 | 0% | 8.13 | 7.12 | 87.58% | 0 | 0% | 8.13 | 7.14 | 87.82% | 0 | 0%
GNA_1825602_Capacity | South Bay and Central Coast | Los Padres | CHOLAME BANK 2 | 1825602 | Bank | None | None | None | 82.11% | 0 | 0% | 12.35 | 7.44 | 60.24% | 0 | 0% | 12.35 | 7.42 | 60.08% | 0 | 0% | 12.35 | 7.41 | 60% | 0 | 0% | 12.35 | 10.14 | 82.11% | 0 | 0% | 12.35 | 10.13 | 82.02% | 0 | 0%
GNA_182562102_Capacity | South Bay and Central Coast | Los Padres | CHOLAME 2102 | 182562102 | Feeder | None | None | None | 74.7% | 0 | 0% | 14.07 | 7.84 | 55.72% | 0 | 0% | 14.07 | 7.82 | 55.58% | 0 | 0% | 14.07 | 7.81 | 55.51% | 0 | 0% | 14.07 | 10.51 | 74.7% | 0 | 0% | 14.07 | 10.5 | 74.63% | 0 | 0%
GNA_1831001_Capacity | South Bay and Central Coast | Los Padres | CABRILLO BANK 1 | 1831001 | Bank | None | None | None | 98.37% | 0 | 0% | 10.4 | 8.8 | 84.62% | 0 | 0% | 10.4 | 10.08 | 96.92% | 0 | 0% | 10.4 | 10.12 | 97.31% | 0 | 0% | 10.4 | 10.16 | 97.69% | 0 | 0% | 10.4 | 10.23 | 98.37% | 0 | 0%
GNA_183101103_Capacity | South Bay and Central Coast | Los Padres | CABRILLO 1103 | 183101103 | Feeder | None | None | None | 53.98% | 0 | 0% | 11.8 | 4.86 | 41.19% | 0 | 0% | 11.8 | 6.37 | 53.98% | 0 | 0% | 11.8 | 6.34 | 53.73% | 0 | 0% | 11.8 | 6.32 | 53.56% | 0 | 0% | 11.8 | 6.33 | 53.64% | 0 | 0%
GNA_183101104_Capacity | South Bay and Central Coast | Los Padres | CABRILLO 1104 | 183101104 | Feeder | None | None | None | 39.41% | 0 | 0% | 11.8 | 4.58 | 38.81% | 0 | 0% | 11.8 | 4.59 | 38.9% | 0 | 0% | 11.8 | 4.61 | 39.07% | 0 | 0% | 11.8 | 4.63 | 39.24% | 0 | 0% | 11.8 | 4.65 | 39.41% | 0 | 0%
GNA_1829702_Capacity | South Bay and Central Coast | Los Padres | PURISIMA BANK 2 | 1829702 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182971101_Capacity | South Bay and Central Coast | Los Padres | PURISIMA SUB 1101 | 182971101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1828001_Capacity | South Bay and Central Coast | Los Padres | BAYWOOD BANK 1 | 1828001 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182801101_Capacity | South Bay and Central Coast | Los Padres | BAYWOOD 1101 | 182801101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1827701_Capacity | South Bay and Central Coast | Los Padres | CAMBRIA BANK 1 | 1827701 | Bank | None | None | None | 8.747% | 0 | 0% | 4.23 | -0.12 | -2.837% | 0 | 0% | 4.23 | 0.01 | 0.2364% | 0 | 0% | 4.23 | 0.1 | 2.364% | 0 | 0% | 4.23 | 0.23 | 5.437% | 0 | 0% | 4.23 | 0.37 | 8.747% | 0 | 0%
GNA_182771101_Capacity | South Bay and Central Coast | Los Padres | CAMBRIA 1101 | 182771101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182771102_Capacity | South Bay and Central Coast | Los Padres | CAMBRIA 1102 | 182771102 | Feeder | None | None | None | 7.882% | 0 | 0% | 6.09 | 0.01 | 0.1642% | 0 | 0% | 6.09 | 0.13 | 2.135% | 0 | 0% | 6.09 | 0.22 | 3.612% | 0 | 0% | 6.09 | 0.35 | 5.747% | 0 | 0% | 6.09 | 0.48 | 7.882% | 0 | 0%
GNA_1825501_Capacity | South Bay and Central Coast | Los Padres | CAYUCOS BANK 1 | 1825501 | Bank | None | None | None | 42.34% | 0 | 0% | 6.59 | 0.94 | 14.26% | 0 | 0% | 6.59 | 1.05 | 15.93% | 0 | 0% | 6.59 | 2.55 | 38.69% | 0 | 0% | 6.59 | 2.67 | 40.52% | 0 | 0% | 6.59 | 2.79 | 42.34% | 0 | 0%
GNA_182551101_Capacity | South Bay and Central Coast | Los Padres | CAYUCOS 1101 | 182551101 | Feeder | None | None | None | 46.17% | 0 | 0% | 6.52 | 1.18 | 18.1% | 0 | 0% | 6.52 | 1.28 | 19.63% | 0 | 0% | 6.52 | 2.78 | 42.64% | 0 | 0% | 6.52 | 2.89 | 44.33% | 0 | 0% | 6.52 | 3.01 | 46.17% | 0 | 0%
GNA_1825502_Capacity | South Bay and Central Coast | Los Padres | CAYUCOS BANK 2 | 1825502 | Bank | None | None | None | 64.78% | 0 | 0% | 7.58 | 4.67 | 61.61% | 0 | 0% | 7.58 | 4.83 | 63.72% | 0 | 0% | 7.58 | 4.91 | 64.78% | 0 | 0% | 7.58 | 4.91 | 64.78% | 0 | 0% | 7.58 | 4.91 | 64.78% | 0 | 0%
GNA_182551102_Capacity | South Bay and Central Coast | Los Padres | CAYUCOS 1102 | 182551102 | Feeder | None | None | None | 65.78% | 0 | 0% | 7.51 | 4.7 | 62.58% | 0 | 0% | 7.51 | 4.86 | 64.71% | 0 | 0% | 7.51 | 4.94 | 65.78% | 0 | 0% | 7.51 | 4.94 | 65.78% | 0 | 0% | 7.51 | 4.94 | 65.78% | 0 | 0%
GNA_1830111_Capacity | South Bay and Central Coast | Los Padres | MORRO BAY BANK 11 | 1830111 | Bank | None | None | None | 99.56% | 0 | 0% | 15.84 | 15.09 | 95.27% | 0 | 0% | 15.84 | 15.47 | 97.66% | 0 | 0% | 15.84 | 14.48 | 91.41% | 0 | 0% | 15.84 | 15.08 | 95.2% | 0 | 0% | 15.84 | 15.77 | 99.56% | 0 | 0%
GNA_183011101_Capacity | South Bay and Central Coast | Los Padres | MORRO BAY 1101 | 183011101 | Feeder | None | None | None | 67.73% | 0 | 0% | 12.83 | 8.62 | 67.19% | 0 | 0% | 12.83 | 8.69 | 67.73% | 0 | 0% | 12.83 | 7.45 | 58.07% | 0 | 0% | 12.83 | 7.69 | 59.94% | 0 | 0% | 12.83 | 7.92 | 61.73% | 0 | 0%
GNA_183011102_Capacity | South Bay and Central Coast | Los Padres | MORRO BAY 1102 | 183011102 | Feeder | None | None | None | 67.6% | 0 | 0% | 12.19 | 6.99 | 57.34% | 0 | 0% | 12.19 | 7.24 | 59.39% | 0 | 0% | 12.19 | 7.47 | 61.28% | 0 | 0% | 12.19 | 7.79 | 63.9% | 0 | 0% | 12.19 | 8.24 | 67.6% | 0 | 0%
GNA_1830702_Capacity | South Bay and Central Coast | Los Padres | PERRY BANK 2 | 1830702 | Bank | None | None | None | 88.87% | 0 | 0% | 4.94 | 3.49 | 70.65% | 0 | 0% | 4.94 | 3.66 | 74.09% | 0 | 0% | 4.94 | 3.87 | 78.34% | 0 | 0% | 4.94 | 4.07 | 82.39% | 0 | 0% | 4.94 | 4.39 | 88.87% | 0 | 0%
GNA_183071101_Capacity | South Bay and Central Coast | Los Padres | PERRY 1101 | 183071101 | Feeder | None | None | None | 63.34% | 0 | 0% | 7.12 | 3.61 | 50.7% | 0 | 0% | 7.12 | 3.78 | 53.09% | 0 | 0% | 7.12 | 4 | 56.18% | 0 | 0% | 7.12 | 4.2 | 58.99% | 0 | 0% | 7.12 | 4.51 | 63.34% | 0 | 0%
GNA_1828204_Capacity | South Bay and Central Coast | Los Padres | MESA BANK 4 | 1828204 | Bank | None | None | None | 76.86% | 0 | 0% | 44.55 | 28.84 | 64.74% | 0 | 0% | 44.55 | 29.38 | 65.95% | 0 | 0% | 44.55 | 31.95 | 71.72% | 0 | 0% | 44.55 | 32.96 | 73.98% | 0 | 0% | 44.55 | 34.24 | 76.86% | 0 | 0%
GNA_182821101_Capacity | South Bay and Central Coast | Los Padres | MESA 1101 | 182821101 | Feeder | None | None | None | 50.66% | 0 | 0% | 12.83 | 5.95 | 46.38% | 0 | 0% | 12.83 | 6.05 | 47.16% | 0 | 0% | 12.83 | 6.17 | 48.09% | 0 | 0% | 12.83 | 6.32 | 49.26% | 0 | 0% | 12.83 | 6.5 | 50.66% | 0 | 0%
GNA_182821102_Capacity | South Bay and Central Coast | Los Padres | MESA 1102 | 182821102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182821103_Capacity | South Bay and Central Coast | Los Padres | MESA 1103 | 182821103 | Feeder | Demand Growth | Capacity | 2026 | 105.1% | 0.66 | 5.144% | 12.83 | 12 | 93.53% | 0 | 0% | 12.83 | 12.24 | 95.4% | 0 | 0% | 12.83 | 12.5 | 97.43% | 0 | 0% | 12.83 | 12.95 | 100.9% | 0.12 | 0.9353% | 12.83 | 13.49 | 105.1% | 0.66 | 5.144%
GNA_182821104_Capacity | South Bay and Central Coast | Los Padres | MESA 1104 | 182821104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1826001_Capacity | South Bay and Central Coast | Los Padres | OCEANO BANK 1 | 1826001 | Bank | None | None | None | 61.64% | 0 | 0% | 44.55 | 22.63 | 50.8% | 0 | 0% | 44.55 | 22.9 | 51.4% | 0 | 0% | 44.55 | 26.08 | 58.54% | 0 | 0% | 44.55 | 26.68 | 59.89% | 0 | 0% | 44.55 | 27.46 | 61.64% | 0 | 0%
GNA_182601104_Capacity | South Bay and Central Coast | Los Padres | OCEANO 1104 | 182601104 | Feeder | None | None | None | 79.08% | 0 | 0% | 12.19 | 8.64 | 70.88% | 0 | 0% | 12.19 | 8.76 | 71.86% | 0 | 0% | 12.19 | 8.78 | 72.03% | 0 | 0% | 12.19 | 9.15 | 75.06% | 0 | 0% | 12.19 | 9.64 | 79.08% | 0 | 0%
GNA_182601106_Capacity | South Bay and Central Coast | Los Padres | OCEANO 1106 | 182601106 | Feeder | None | None | None | 72.72% | 0 | 0% | 14.26 | 7.01 | 49.16% | 0 | 0% | 14.26 | 7.06 | 49.51% | 0 | 0% | 14.26 | 10.12 | 70.97% | 0 | 0% | 14.26 | 10.23 | 71.74% | 0 | 0% | 14.26 | 10.37 | 72.72% | 0 | 0%
GNA_182601108_Capacity | South Bay and Central Coast | Los Padres | OCEANO 1108 | 182601108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1826002_Capacity | South Bay and Central Coast | Los Padres | OCEANO BANK 2 | 1826002 | Bank | None | None | None | 85.62% | 0 | 0% | 29.7 | 21.94 | 73.87% | 0 | 0% | 29.7 | 23.39 | 78.75% | 0 | 0% | 29.7 | 23.92 | 80.54% | 0 | 0% | 29.7 | 24.58 | 82.76% | 0 | 0% | 29.7 | 25.43 | 85.62% | 0 | 0%
GNA_182601102_Capacity | South Bay and Central Coast | Los Padres | OCEANO 1102 | 182601102 | Feeder | None | None | None | 40.69% | 0 | 0% | 12.19 | 4.77 | 39.13% | 0 | 0% | 12.19 | 4.79 | 39.29% | 0 | 0% | 12.19 | 4.81 | 39.46% | 0 | 0% | 12.19 | 4.85 | 39.79% | 0 | 0% | 12.19 | 4.96 | 40.69% | 0 | 0%
GNA_182601103_Capacity | South Bay and Central Coast | Los Padres | OCEANO 1103 | 182601103 | Feeder | None | None | None | 99.15% | 0 | 0% | 11.82 | 9.54 | 80.71% | 0 | 0% | 11.82 | 10.95 | 92.64% | 0 | 0% | 11.82 | 11.24 | 95.09% | 0 | 0% | 11.82 | 11.56 | 97.8% | 0 | 0% | 11.82 | 11.72 | 99.15% | 0 | 0%
GNA_182601105_Capacity | South Bay and Central Coast | Los Padres | OCEANO 1105 | 182601105 | Feeder | None | None | None | 81.67% | 0 | 0% | 12.06 | 8.84 | 73.3% | 0 | 0% | 12.06 | 9.02 | 74.79% | 0 | 0% | 12.06 | 9.18 | 76.12% | 0 | 0% | 12.06 | 9.38 | 77.78% | 0 | 0% | 12.06 | 9.85 | 81.67% | 0 | 0%
GNA_1825401_Capacity | South Bay and Central Coast | Los Padres | ATASCADERO BANK 1 | 1825401 | Bank | Demand Growth | Capacity | 2026 | 106.5% | 1.93 | 6.498% | 29.7 | 29.43 | 99.09% | 0 | 0% | 29.7 | 29.6 | 99.66% | 0 | 0% | 29.7 | 29.66 | 99.87% | 0 | 0% | 29.7 | 30.28 | 102% | 0.58 | 1.953% | 29.7 | 31.63 | 106.5% | 1.93 | 6.498%
GNA_182541101_Capacity | South Bay and Central Coast | Los Padres | ATASCADERO 1101 | 182541101 | Feeder | None | None | None | 96.06% | 0 | 0% | 12.19 | 11.65 | 95.57% | 0 | 0% | 12.19 | 11.59 | 95.08% | 0 | 0% | 12.19 | 11.55 | 94.75% | 0 | 0% | 12.19 | 11.64 | 95.49% | 0 | 0% | 12.19 | 11.71 | 96.06% | 0 | 0%
GNA_182541102_Capacity | South Bay and Central Coast | Los Padres | ATASCADERO 1102 | 182541102 | Feeder | Demand Growth | Capacity | 2027 | 105.9% | 0.72 | 5.906% | 12.19 | 11.42 | 93.68% | 0 | 0% | 12.19 | 11.51 | 94.42% | 0 | 0% | 12.19 | 11.45 | 93.93% | 0 | 0% | 12.19 | 11.84 | 97.13% | 0 | 0% | 12.19 | 12.91 | 105.9% | 0.72 | 5.906%
GNA_182541103_Capacity | South Bay and Central Coast | Los Padres | ATASCADERO 1103 | 182541103 | Feeder | None | None | None | 79.49% | 0 | 0% | 12.19 | 9.21 | 75.55% | 0 | 0% | 12.19 | 9.3 | 76.29% | 0 | 0% | 12.19 | 9.42 | 77.28% | 0 | 0% | 12.19 | 9.54 | 78.26% | 0 | 0% | 12.19 | 9.69 | 79.49% | 0 | 0%
GNA_1826101_Capacity | South Bay and Central Coast | Los Padres | PASO ROBLES BANK 1 | 1826101 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182611101_Capacity | South Bay and Central Coast | Los Padres | PASO ROBLES 1101 | 182611101 | Feeder | None | None | None | 72.99% | 0 | 0% | 11.33 | 8.27 | 72.99% | 0 | 0% | 11.33 | 8.24 | 72.73% | 0 | 0% | 11.33 | 8.21 | 72.46% | 0 | 0% | 11.33 | 8.18 | 72.2% | 0 | 0% | 11.33 | 8.14 | 71.84% | 0 | 0%
GNA_182611102_Capacity | South Bay and Central Coast | Los Padres | PASO ROBLES 1102 | 182611102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182611103_Capacity | South Bay and Central Coast | Los Padres | PASO ROBLES 1103 | 182611103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1826102_Capacity | South Bay and Central Coast | Los Padres | PASO ROBLES BANK 2 | 1826102 | Bank | None | None | None | 97.24% | 0 | 0% | 29.7 | 28.88 | 97.24% | 0 | 0% | 29.7 | 28.11 | 94.65% | 0 | 0% | 29.7 | 27.92 | 94.01% | 0 | 0% | 29.7 | 28.16 | 94.81% | 0 | 0% | 29.7 | 28.4 | 95.62% | 0 | 0%
GNA_182611104_Capacity | South Bay and Central Coast | Los Padres | PASO ROBLES 1104 | 182611104 | Feeder | None | None | None | 92.04% | 0 | 0% | 12.19 | 11.13 | 91.3% | 0 | 0% | 12.19 | 11.12 | 91.22% | 0 | 0% | 12.19 | 11.13 | 91.3% | 0 | 0% | 12.19 | 11.18 | 91.71% | 0 | 0% | 12.19 | 11.22 | 92.04% | 0 | 0%
GNA_182611106_Capacity | South Bay and Central Coast | Los Padres | PASO ROBLES 1106 | 182611106 | Feeder | Demand Growth | Capacity | 2023 | 117.7% | 2.78 | 17.74% | 15.67 | 18.45 | 117.7% | 2.78 | 17.74% | 15.67 | 17.68 | 112.8% | 2.01 | 12.83% | 15.67 | 17.39 | 111% | 1.72 | 10.98% | 15.67 | 17.59 | 112.3% | 1.92 | 12.25% | 15.67 | 17.79 | 113.5% | 2.12 | 13.53%
GNA_1826103_Capacity | South Bay and Central Coast | Los Padres | PASO ROBLES BANK 3 | 1826103 | Bank | Demand Growth | Capacity | 2025 | 120.5% | 6.09 | 20.51% | 29.7 | 23.45 | 78.96% | 0 | 0% | 29.7 | 28.07 | 94.51% | 0 | 0% | 29.7 | 31.52 | 106.1% | 1.82 | 6.128% | 29.7 | 34.15 | 115% | 4.45 | 14.98% | 29.7 | 35.79 | 120.5% | 6.09 | 20.51%
GNA_182611107_Capacity | South Bay and Central Coast | Los Padres | PASO ROBLES 1107 | 182611107 | Feeder | Demand Growth | Capacity | 2024 | 104.8% | 0.65 | 4.779% | 13.6 | 10.88 | 80% | 0 | 0% | 13.6 | 13.78 | 101.3% | 0.18 | 1.324% | 13.6 | 13.94 | 102.5% | 0.34 | 2.5% | 13.6 | 14.08 | 103.5% | 0.48 | 3.529% | 13.6 | 14.25 | 104.8% | 0.65 | 4.779%
GNA_182611108_Capacity | South Bay and Central Coast | Los Padres | PASO ROBLES 1108 | 182611108 | Feeder | Demand Growth | Capacity | 2024 | 149.6% | 7.77 | 49.59% | 15.67 | 14.47 | 92.34% | 0 | 0% | 15.67 | 16.19 | 103.3% | 0.52 | 3.318% | 15.67 | 19.48 | 124.3% | 3.81 | 24.31% | 15.67 | 21.97 | 140.2% | 6.3 | 40.2% | 15.67 | 23.44 | 149.6% | 7.77 | 49.59%
GNA_1826601_Capacity | South Bay and Central Coast | Los Padres | SAN MIGUEL BANK 1 | 1826601 | Bank | Demand Growth | Capacity | 2023 | 118.6% | 2.95 | 18.62% | 15.84 | 18.42 | 116.3% | 2.58 | 16.29% | 15.84 | 18.79 | 118.6% | 2.95 | 18.62% | 15.84 | 18.77 | 118.5% | 2.93 | 18.5% | 15.84 | 18.76 | 118.4% | 2.92 | 18.43% | 15.84 | 18.78 | 118.6% | 2.94 | 18.56%
GNA_182661104_Capacity | South Bay and Central Coast | Los Padres | SAN MIGUEL 1104 | 182661104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182661105_Capacity | South Bay and Central Coast | Los Padres | SAN MIGUEL 1105 | 182661105 | Feeder | None | None | None | 93.83% | 0 | 0% | 5.35 | 5.02 | 93.83% | 0 | 0% | 5.35 | 5.02 | 93.83% | 0 | 0% | 5.35 | 5.02 | 93.83% | 0 | 0% | 5.35 | 5.01 | 93.64% | 0 | 0% | 5.35 | 5.02 | 93.83% | 0 | 0%
GNA_182661106_Capacity | South Bay and Central Coast | Los Padres | SAN MIGUEL 1106 | 182661106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182661107_Capacity | South Bay and Central Coast | Los Padres | SAN MIGUEL 1107 | 182661107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1830502_Capacity | South Bay and Central Coast | Los Padres | TEMPLETON BANK 2 | 1830502 | Bank | None | None | None | 93.31% | 0 | 0% | 44.55 | 35.42 | 79.51% | 0 | 0% | 44.55 | 41.57 | 93.31% | 0 | 0% | 44.55 | 41.08 | 92.21% | 0 | 0% | 44.55 | 41.05 | 92.14% | 0 | 0% | 44.55 | 41.09 | 92.23% | 0 | 0%
GNA_183052108_Capacity | South Bay and Central Coast | Los Padres | TEMPLETON 2108 | 183052108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_183052109_Capacity | South Bay and Central Coast | Los Padres | TEMPLETON 2109 | 183052109 | Feeder | None | None | None | 85.52% | 0 | 0% | 21.41 | 16.3 | 76.13% | 0 | 0% | 21.41 | 17.71 | 82.72% | 0 | 0% | 21.41 | 17.81 | 83.19% | 0 | 0% | 21.41 | 18.05 | 84.31% | 0 | 0% | 21.41 | 18.31 | 85.52% | 0 | 0%
GNA_183052110_Capacity | South Bay and Central Coast | Los Padres | TEMPLETON 2110 | 183052110 | Feeder | None | None | None | 54.19% | 0 | 0% | 21.11 | 11.44 | 54.19% | 0 | 0% | 21.11 | 11.32 | 53.62% | 0 | 0% | 21.11 | 11.2 | 53.06% | 0 | 0% | 21.11 | 11.25 | 53.29% | 0 | 0% | 21.11 | 11.28 | 53.43% | 0 | 0%
GNA_1830503_Capacity | South Bay and Central Coast | Los Padres | TEMPLETON BANK 3 | 1830503 | Bank | None | None | None | 84.78% | 0 | 0% | 44.55 | 37.77 | 84.78% | 0 | 0% | 44.55 | 37.58 | 84.35% | 0 | 0% | 44.55 | 37.43 | 84.02% | 0 | 0% | 44.55 | 37.46 | 84.09% | 0 | 0% | 44.55 | 37.6 | 84.4% | 0 | 0%
GNA_183052111_Capacity | South Bay and Central Coast | Los Padres | TEMPLETON 2111 | 183052111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_183052112_Capacity | South Bay and Central Coast | Los Padres | TEMPLETON 2112 | 183052112 | Feeder | None | None | None | 66.45% | 0 | 0% | 18.63 | 11.64 | 62.48% | 0 | 0% | 18.63 | 11.86 | 63.66% | 0 | 0% | 18.63 | 12.07 | 64.79% | 0 | 0% | 18.63 | 12.22 | 65.59% | 0 | 0% | 18.63 | 12.38 | 66.45% | 0 | 0%
GNA_183052113_Capacity | South Bay and Central Coast | Los Padres | TEMPLETON 2113 | 183052113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1829501_Capacity | South Bay and Central Coast | Los Padres | FOOTHILL BANK 1 | 1829501 | Bank | Demand Growth | Capacity | 2024 | 125.5% | 2.12 | 25.48% | 8.32 | 7.66 | 92.07% | 0 | 0% | 8.32 | 9.7 | 116.6% | 1.38 | 16.59% | 8.32 | 9.9 | 119% | 1.58 | 18.99% | 8.32 | 10.16 | 122.1% | 1.84 | 22.12% | 8.32 | 10.44 | 125.5% | 2.12 | 25.48%
GNA_182951101_Capacity | South Bay and Central Coast | Los Padres | FOOTHILL 1101 | 182951101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182951102_Capacity | South Bay and Central Coast | Los Padres | FOOTHILL 1102 | 182951102 | Feeder | None | None | None | 79.02% | 0 | 0% | 12.06 | 6.75 | 55.97% | 0 | 0% | 12.06 | 8.79 | 72.89% | 0 | 0% | 12.06 | 8.98 | 74.46% | 0 | 0% | 12.06 | 9.24 | 76.62% | 0 | 0% | 12.06 | 9.53 | 79.02% | 0 | 0%
GNA_1825801_Capacity | South Bay and Central Coast | Los Padres | GOLDTREE BANK 1 | 1825801 | Bank | None | None | None | 91.22% | 0 | 0% | 15.84 | 13.47 | 85.04% | 0 | 0% | 15.84 | 14.45 | 91.22% | 0 | 0% | 15.84 | 14.35 | 90.59% | 0 | 0% | 15.84 | 14.26 | 90.03% | 0 | 0% | 15.84 | 14.38 | 90.78% | 0 | 0%
GNA_182581105_Capacity | South Bay and Central Coast | Los Padres | GOLDTREE 1105 | 182581105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182581107_Capacity | South Bay and Central Coast | Los Padres | GOLDTREE 1107 | 182581107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182581108_Capacity | South Bay and Central Coast | Los Padres | GOLDTREE 1108 | 182581108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1826304_Capacity | South Bay and Central Coast | Los Padres | SAN LUIS OBISPO BANK 4 | 1826304 | Bank | None | None | None | 97.73% | 0 | 0% | 44.53 | 40.98 | 92.03% | 0 | 0% | 44.53 | 40.98 | 92.03% | 0 | 0% | 44.53 | 40.18 | 90.23% | 0 | 0% | 44.53 | 41.88 | 94.05% | 0 | 0% | 44.53 | 43.52 | 97.73% | 0 | 0%
GNA_182631101_Capacity | South Bay and Central Coast | Los Padres | SAN LUIS OBISPO 1101 | 182631101 | Feeder | None | None | None | 89.08% | 0 | 0% | 9.71 | 6.48 | 66.74% | 0 | 0% | 9.71 | 6.86 | 70.65% | 0 | 0% | 9.71 | 7.15 | 73.64% | 0 | 0% | 9.71 | 7.81 | 80.43% | 0 | 0% | 9.71 | 8.65 | 89.08% | 0 | 0%
GNA_182631102_Capacity | South Bay and Central Coast | Los Padres | SAN LUIS OBISPO 1102 | 182631102 | Feeder | Demand Growth | Capacity | 2024 | 108% | 0.94 | 7.966% | 11.8 | 11.51 | 97.54% | 0 | 0% | 11.8 | 11.98 | 101.5% | 0.18 | 1.525% | 11.8 | 11.61 | 98.39% | 0 | 0% | 11.8 | 12.36 | 104.7% | 0.56 | 4.746% | 11.8 | 12.74 | 108% | 0.94 | 7.966%
GNA_182631103_Capacity | South Bay and Central Coast | Los Padres | SAN LUIS OBISPO 1103 | 182631103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182631105_Capacity | South Bay and Central Coast | Los Padres | SAN LUIS OBISPO 1105 | 182631105 | Feeder | None | None | None | 98.81% | 0 | 0% | 11.8 | 11.44 | 96.95% | 0 | 0% | 11.8 | 11.44 | 96.95% | 0 | 0% | 11.8 | 11.44 | 96.95% | 0 | 0% | 11.8 | 11.5 | 97.46% | 0 | 0% | 11.8 | 11.66 | 98.81% | 0 | 0%
GNA_1826306_Capacity | South Bay and Central Coast | Los Padres | SAN LUIS OBISPO BANK 6 | 1826306 | Bank | None | None | None | 73.66% | 0 | 0% | 44.53 | 30.93 | 69.46% | 0 | 0% | 44.53 | 30.93 | 69.46% | 0 | 0% | 44.53 | 32.1 | 72.09% | 0 | 0% | 44.53 | 32.46 | 72.89% | 0 | 0% | 44.53 | 32.8 | 73.66% | 0 | 0%
GNA_182631104_Capacity | South Bay and Central Coast | Los Padres | SAN LUIS OBISPO 1104 | 182631104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182631107_Capacity | South Bay and Central Coast | Los Padres | SAN LUIS OBISPO 1107 | 182631107 | Feeder | None | None | None | 93.76% | 0 | 0% | 13.15 | 12.32 | 93.69% | 0 | 0% | 13.15 | 12.32 | 93.69% | 0 | 0% | 13.15 | 12.32 | 93.69% | 0 | 0% | 13.15 | 12.32 | 93.69% | 0 | 0% | 13.15 | 12.33 | 93.76% | 0 | 0%
GNA_182631108_Capacity | South Bay and Central Coast | Los Padres | SAN LUIS OBISPO 1108 | 182631108 | Feeder | Demand Growth | Capacity | 2024 | 116.4% | 2.1 | 16.37% | 12.83 | 12.34 | 96.18% | 0 | 0% | 12.83 | 13.76 | 107.2% | 0.93 | 7.249% | 12.83 | 14.93 | 116.4% | 2.1 | 16.37% | 12.83 | 14.93 | 116.4% | 2.1 | 16.37% | 12.83 | 14.93 | 116.4% | 2.1 | 16.37%
GNA_1825703_Capacity | South Bay and Central Coast | Los Padres | DIVIDE BANK 3 | 1825703 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182571101_Capacity | South Bay and Central Coast | Los Padres | DIVIDE 1101 | 182571101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1825704_Capacity | South Bay and Central Coast | Los Padres | DIVIDE BANK 4 | 1825704 | Bank | None | None | None | 43.13% | 0 | 0% | 29.7 | 11.78 | 39.66% | 0 | 0% | 29.7 | 11.96 | 40.27% | 0 | 0% | 29.7 | 12.15 | 40.91% | 0 | 0% | 29.7 | 12.41 | 41.78% | 0 | 0% | 29.7 | 12.81 | 43.13% | 0 | 0%
GNA_182571102_Capacity | South Bay and Central Coast | Los Padres | DIVIDE 1102 | 182571102 | Feeder | None | None | None | 78.59% | 0 | 0% | 14.48 | 10.52 | 72.65% | 0 | 0% | 14.48 | 10.69 | 73.83% | 0 | 0% | 14.48 | 10.85 | 74.93% | 0 | 0% | 14.48 | 11.05 | 76.31% | 0 | 0% | 14.48 | 11.38 | 78.59% | 0 | 0%
GNA_182571103_Capacity | South Bay and Central Coast | Los Padres | DIVIDE 1103 | 182571103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1820601_Capacity | South Bay and Central Coast | Los Padres | FAIRWAY BANK 1 | 1820601 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182061103_Capacity | South Bay and Central Coast | Los Padres | FAIRWAY 1103 | 182061103 | Feeder | None | None | None | 86.47% | 0 | 0% | 14.41 | 11.7 | 81.19% | 0 | 0% | 14.41 | 12.09 | 83.9% | 0 | 0% | 14.41 | 12.22 | 84.8% | 0 | 0% | 14.41 | 12.33 | 85.57% | 0 | 0% | 14.41 | 12.46 | 86.47% | 0 | 0%
GNA_182061104_Capacity | South Bay and Central Coast | Los Padres | FAIRWAY 1104 | 182061104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1820602_Capacity | South Bay and Central Coast | Los Padres | FAIRWAY BANK 2 | 1820602 | Bank | None | None | None | 92.66% | 0 | 0% | 29.7 | 26.09 | 87.85% | 0 | 0% | 29.7 | 27.26 | 91.78% | 0 | 0% | 29.7 | 26.97 | 90.81% | 0 | 0% | 29.7 | 27.09 | 91.21% | 0 | 0% | 29.7 | 27.52 | 92.66% | 0 | 0%
GNA_182061106_Capacity | South Bay and Central Coast | Los Padres | FAIRWAY 1106 | 182061106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182061107_Capacity | South Bay and Central Coast | Los Padres | FAIRWAY 1107 | 182061107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182061108_Capacity | South Bay and Central Coast | Los Padres | FAIRWAY 1108 | 182061108 | Feeder | None | None | None | 88.94% | 0 | 0% | 11.57 | 9.66 | 83.49% | 0 | 0% | 11.57 | 9.76 | 84.36% | 0 | 0% | 11.57 | 9.88 | 85.39% | 0 | 0% | 11.57 | 10.05 | 86.86% | 0 | 0% | 11.57 | 10.29 | 88.94% | 0 | 0%
GNA_1826702_Capacity | South Bay and Central Coast | Los Padres | SANTA MARIA BANK 2 | 1826702 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182671105_Capacity | South Bay and Central Coast | Los Padres | SANTA MARIA 1105 | 182671105 | Feeder | None | None | None | 78.81% | 0 | 0% | 14.63 | 11.34 | 77.51% | 0 | 0% | 14.63 | 11.36 | 77.65% | 0 | 0% | 14.63 | 11.37 | 77.72% | 0 | 0% | 14.63 | 11.43 | 78.13% | 0 | 0% | 14.63 | 11.53 | 78.81% | 0 | 0%
GNA_182671106_Capacity | South Bay and Central Coast | Los Padres | SANTA MARIA 1106 | 182671106 | Feeder | None | None | None | 71.56% | 0 | 0% | 12.06 | 7.58 | 62.85% | 0 | 0% | 12.06 | 8.03 | 66.58% | 0 | 0% | 12.06 | 8.14 | 67.5% | 0 | 0% | 12.06 | 8.41 | 69.73% | 0 | 0% | 12.06 | 8.63 | 71.56% | 0 | 0%
GNA_182671107_Capacity | South Bay and Central Coast | Los Padres | SANTA MARIA 1107 | 182671107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182671108_Capacity | South Bay and Central Coast | Los Padres | SANTA MARIA 1108 | 182671108 | Feeder | None | None | None | 95.33% | 0 | 0% | 11.57 | 10.77 | 93.09% | 0 | 0% | 11.57 | 10.8 | 93.34% | 0 | 0% | 11.57 | 10.84 | 93.69% | 0 | 0% | 11.57 | 10.94 | 94.55% | 0 | 0% | 11.57 | 11.03 | 95.33% | 0 | 0%
GNA_1826703_Capacity | South Bay and Central Coast | Los Padres | SANTA MARIA BANK 3 | 1826703 | Bank | None | None | None | 65.84% | 0 | 0% | 44.55 | 27.62 | 62% | 0 | 0% | 44.55 | 28.7 | 64.42% | 0 | 0% | 44.55 | 29.12 | 65.36% | 0 | 0% | 44.55 | 29.19 | 65.52% | 0 | 0% | 44.55 | 29.33 | 65.84% | 0 | 0%
GNA_182671109_Capacity | South Bay and Central Coast | Los Padres | SANTA MARIA 1109 | 182671109 | Feeder | None | None | None | 44.74% | 0 | 0% | 12.83 | 5.67 | 44.19% | 0 | 0% | 12.83 | 5.73 | 44.66% | 0 | 0% | 12.83 | 5.72 | 44.58% | 0 | 0% | 12.83 | 5.73 | 44.66% | 0 | 0% | 12.83 | 5.74 | 44.74% | 0 | 0%
GNA_182671110_Capacity | South Bay and Central Coast | Los Padres | SANTA MARIA 1110 | 182671110 | Feeder | None | None | None | 89.79% | 0 | 0% | 12.83 | 10.2 | 79.5% | 0 | 0% | 12.83 | 11.01 | 85.81% | 0 | 0% | 12.83 | 11.33 | 88.31% | 0 | 0% | 12.83 | 11.42 | 89.01% | 0 | 0% | 12.83 | 11.52 | 89.79% | 0 | 0%
GNA_182671111_Capacity | South Bay and Central Coast | Los Padres | SANTA MARIA 1111 | 182671111 | Feeder | None | None | None | 85.32% | 0 | 0% | 12.06 | 9.67 | 80.18% | 0 | 0% | 12.06 | 9.99 | 82.84% | 0 | 0% | 12.06 | 10.2 | 84.58% | 0 | 0% | 12.06 | 10.24 | 84.91% | 0 | 0% | 12.06 | 10.29 | 85.32% | 0 | 0%
GNA_182671112_Capacity | South Bay and Central Coast | Los Padres | SANTA MARIA 1112 | 182671112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1830401_Capacity | South Bay and Central Coast | Los Padres | BUELLTON BANK 1 | 1830401 | Bank | Demand Growth | Capacity | 2023 | 135% | 3.64 | 35% | 10.4 | 11.1 | 106.7% | 0.7 | 6.731% | 10.4 | 11.92 | 114.6% | 1.52 | 14.62% | 10.4 | 12.59 | 121.1% | 2.19 | 21.06% | 10.4 | 13.16 | 126.5% | 2.76 | 26.54% | 10.4 | 14.04 | 135% | 3.64 | 35%
GNA_183041101_Capacity | South Bay and Central Coast | Los Padres | BUELLTON 1101 | 183041101 | Feeder | Demand Growth | Capacity | 2025 | 114.6% | 1.78 | 14.6% | 12.19 | 11.02 | 90.4% | 0 | 0% | 12.19 | 11.84 | 97.13% | 0 | 0% | 12.19 | 12.51 | 102.6% | 0.32 | 2.625% | 12.19 | 13.08 | 107.3% | 0.89 | 7.301% | 12.19 | 13.97 | 114.6% | 1.78 | 14.6%
GNA_1830402_Capacity | South Bay and Central Coast | Los Padres | BUELLTON BANK 2 | 1830402 | Bank | None | None | None | 70% | 0 | 0% | 10.4 | 7.28 | 70% | 0 | 0% | 10.4 | 7.06 | 67.88% | 0 | 0% | 10.4 | 7.13 | 68.56% | 0 | 0% | 10.4 | 7.15 | 68.75% | 0 | 0% | 10.4 | 7.2 | 69.23% | 0 | 0%
GNA_183041102_Capacity | South Bay and Central Coast | Los Padres | BUELLTON 1102 | 183041102 | Feeder | None | None | None | 54.88% | 0 | 0% | 12.19 | 6.69 | 54.88% | 0 | 0% | 12.19 | 6.49 | 53.24% | 0 | 0% | 12.19 | 6.56 | 53.81% | 0 | 0% | 12.19 | 6.58 | 53.98% | 0 | 0% | 12.19 | 6.63 | 54.39% | 0 | 0%
GNA_1827201_Capacity | South Bay and Central Coast | Los Padres | SANTA YNEZ BANK 1 | 1827201 | Bank | None | None | None | 94.42% | 0 | 0% | 10.4 | 9.23 | 88.75% | 0 | 0% | 10.4 | 9.35 | 89.9% | 0 | 0% | 10.4 | 9.48 | 91.15% | 0 | 0% | 10.4 | 9.64 | 92.69% | 0 | 0% | 10.4 | 9.82 | 94.42% | 0 | 0%
GNA_182721101_Capacity | South Bay and Central Coast | Los Padres | SANTA YNEZ 1101 | 182721101 | Feeder | None | None | None | 74.44% | 0 | 0% | 12.44 | 8.67 | 69.69% | 0 | 0% | 12.44 | 8.79 | 70.66% | 0 | 0% | 12.44 | 8.92 | 71.7% | 0 | 0% | 12.44 | 9.08 | 72.99% | 0 | 0% | 12.44 | 9.26 | 74.44% | 0 | 0%
GNA_1827202_Capacity | South Bay and Central Coast | Los Padres | SANTA YNEZ BANK 2 | 1827202 | Bank | None | None | None | 67.68% | 0 | 0% | 29.7 | 17.42 | 58.65% | 0 | 0% | 29.7 | 19.48 | 65.59% | 0 | 0% | 29.7 | 19.68 | 66.26% | 0 | 0% | 29.7 | 19.82 | 66.73% | 0 | 0% | 29.7 | 20.1 | 67.68% | 0 | 0%
GNA_182721102_Capacity | South Bay and Central Coast | Los Padres | SANTA YNEZ 1102 | 182721102 | Feeder | None | None | None | 96.18% | 0 | 0% | 12.83 | 9.99 | 77.86% | 0 | 0% | 12.83 | 11.73 | 91.43% | 0 | 0% | 12.83 | 11.9 | 92.75% | 0 | 0% | 12.83 | 12.1 | 94.31% | 0 | 0% | 12.83 | 12.34 | 96.18% | 0 | 0%
GNA_182721104_Capacity | South Bay and Central Coast | Los Padres | SANTA YNEZ 1104 | 182721104 | Feeder | None | None | None | 76.46% | 0 | 0% | 12.83 | 9.34 | 72.8% | 0 | 0% | 12.83 | 9.62 | 74.98% | 0 | 0% | 12.83 | 9.68 | 75.45% | 0 | 0% | 12.83 | 9.7 | 75.6% | 0 | 0% | 12.83 | 9.81 | 76.46% | 0 | 0%
GNA_1826801_Capacity | South Bay and Central Coast | Los Padres | ZACA BANK 1 | 1826801 | Bank | None | None | None | 88.37% | 0 | 0% | 10.4 | 9.19 | 88.37% | 0 | 0% | 10.4 | 9.18 | 88.27% | 0 | 0% | 10.4 | 9.15 | 87.98% | 0 | 0% | 10.4 | 9.04 | 86.92% | 0 | 0% | 10.4 | 9.02 | 86.73% | 0 | 0%
GNA_182681101_Capacity | South Bay and Central Coast | Los Padres | ZACA 1101 | 182681101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182681102_Capacity | South Bay and Central Coast | Los Padres | ZACA 1102 | 182681102 | Feeder | None | None | None | 53.51% | 0 | 0% | 10.69 | 5.72 | 53.51% | 0 | 0% | 10.69 | 5.7 | 53.32% | 0 | 0% | 10.69 | 5.67 | 53.04% | 0 | 0% | 10.69 | 5.56 | 52.01% | 0 | 0% | 10.69 | 5.5 | 51.45% | 0 | 0%
GNA_1830301_Capacity | South Bay and Central Coast | Los Padres | PALMER BANK 1 | 1830301 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_183031101_Capacity | South Bay and Central Coast | Los Padres | PALMER 1101 | 183031101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1828102_Capacity | South Bay and Central Coast | Los Padres | SISQUOC BANK 2 | 1828102 | Bank | None | None | None | 95.83% | 0 | 0% | 15.84 | 15.18 | 95.83% | 0 | 0% | 15.84 | 15.12 | 95.45% | 0 | 0% | 15.84 | 15.06 | 95.08% | 0 | 0% | 15.84 | 15.02 | 94.82% | 0 | 0% | 15.84 | 15 | 94.7% | 0 | 0%
GNA_182811101_Capacity | South Bay and Central Coast | Los Padres | SISQUOC 1101 | 182811101 | Feeder | None | None | None | 37.7% | 0 | 0% | 10.69 | 4.03 | 37.7% | 0 | 0% | 10.69 | 4.01 | 37.51% | 0 | 0% | 10.69 | 3.98 | 37.23% | 0 | 0% | 10.69 | 3.95 | 36.95% | 0 | 0% | 10.69 | 3.96 | 37.04% | 0 | 0%
GNA_182811102_Capacity | South Bay and Central Coast | Los Padres | SISQUOC 1102 | 182811102 | Feeder | Demand Growth | Capacity | 2023 | 125.5% | 2.95 | 25.5% | 11.57 | 14.52 | 125.5% | 2.95 | 25.5% | 11.57 | 14.48 | 125.2% | 2.91 | 25.15% | 11.57 | 14.45 | 124.9% | 2.88 | 24.89% | 11.57 | 14.45 | 124.9% | 2.88 | 24.89% | 11.57 | 14.42 | 124.6% | 2.85 | 24.63%
GNA_1828103_Capacity | South Bay and Central Coast | Los Padres | SISQUOC BANK 3 | 1828103 | Bank | None | None | None | 78.85% | 0 | 0% | 15.84 | 12.49 | 78.85% | 0 | 0% | 15.84 | 12.46 | 78.66% | 0 | 0% | 15.84 | 12.41 | 78.35% | 0 | 0% | 15.84 | 12.36 | 78.03% | 0 | 0% | 15.84 | 12.33 | 77.84% | 0 | 0%
GNA_182811103_Capacity | South Bay and Central Coast | Los Padres | SISQUOC 1103 | 182811103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_182811104_Capacity | South Bay and Central Coast | Los Padres | SISQUOC 1104 | 182811104 | Feeder | None | None | None | 76.15% | 0 | 0% | 10.69 | 8.14 | 76.15% | 0 | 0% | 10.69 | 8.12 | 75.96% | 0 | 0% | 10.69 | 8.09 | 75.68% | 0 | 0% | 10.69 | 8.07 | 75.49% | 0 | 0% | 10.69 | 8.05 | 75.3% | 0 | 0%
GNA_0144701_Capacity | Bay Area | Mission | DUMBARTON BANK 1 | 144701 | Bank | Demand Growth | Capacity | 2026 | 107.1% | 2.1 | 7.075% | 29.68 | 25.68 | 86.52% | 0 | 0% | 29.68 | 27.81 | 93.7% | 0 | 0% | 29.68 | 29.33 | 98.82% | 0 | 0% | 29.68 | 30.98 | 104.4% | 1.3 | 4.38% | 29.68 | 31.78 | 107.1% | 2.1 | 7.075%
GNA_014471102_Capacity | Bay Area | Mission | DUMBARTON SUB 1102 | 14471102 | Feeder | Demand Growth | Capacity | 2023 | 148.5% | 5.61 | 48.49% | 11.57 | 12.96 | 112% | 1.39 | 12.01% | 11.57 | 14.45 | 124.9% | 2.88 | 24.89% | 11.57 | 15.63 | 135.1% | 4.06 | 35.09% | 11.57 | 16.9 | 146.1% | 5.33 | 46.07% | 11.57 | 17.18 | 148.5% | 5.61 | 48.49%
GNA_014471103_Capacity | Bay Area | Mission | DUMBARTON SUB 1103 | 14471103 | Feeder | None | None | None | 60.07% | 0 | 0% | 10.97 | 5.83 | 53.14% | 0 | 0% | 10.97 | 5.97 | 54.42% | 0 | 0% | 10.97 | 6.11 | 55.7% | 0 | 0% | 10.97 | 6.31 | 57.52% | 0 | 0% | 10.97 | 6.59 | 60.07% | 0 | 0%
GNA_014471104_Capacity | Bay Area | Mission | DUMBARTON SUB 1104 | 14471104 | Feeder | None | None | None | 59.55% | 0 | 0% | 11.57 | 6.03 | 52.12% | 0 | 0% | 11.57 | 6.51 | 56.27% | 0 | 0% | 11.57 | 6.61 | 57.13% | 0 | 0% | 11.57 | 6.73 | 58.17% | 0 | 0% | 11.57 | 6.89 | 59.55% | 0 | 0%
GNA_0144702_Capacity | Bay Area | Mission | DUMBARTON BANK 2 | 144702 | Bank | Demand Growth | Capacity | 2023 | 132.6% | 9.69 | 32.65% | 29.68 | 37.72 | 127.1% | 8.04 | 27.09% | 29.68 | 38.05 | 128.2% | 8.37 | 28.2% | 29.68 | 38.41 | 129.4% | 8.73 | 29.41% | 29.68 | 38.78 | 130.7% | 9.1 | 30.66% | 29.68 | 39.37 | 132.6% | 9.69 | 32.65%
GNA_014471105_Capacity | Bay Area | Mission | DUMBARTON SUB 1105 | 14471105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014471106_Capacity | Bay Area | Mission | DUMBARTON SUB 1106 | 14471106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014471107_Capacity | Bay Area | Mission | DUMBARTON SUB 1107 | 14471107 | Feeder | None | None | None | 74.16% | 0 | 0% | 11.57 | 8.16 | 70.53% | 0 | 0% | 11.57 | 8.18 | 70.7% | 0 | 0% | 11.57 | 8.29 | 71.65% | 0 | 0% | 11.57 | 8.4 | 72.6% | 0 | 0% | 11.57 | 8.58 | 74.16% | 0 | 0%
GNA_014471108_Capacity | Bay Area | Mission | DUMBARTON SUB 1108 | 14471108 | Feeder | None | None | None | 84.18% | 0 | 0% | 11.57 | 9.33 | 80.64% | 0 | 0% | 11.57 | 9.38 | 81.07% | 0 | 0% | 11.57 | 9.42 | 81.42% | 0 | 0% | 11.57 | 9.54 | 82.45% | 0 | 0% | 11.57 | 9.74 | 84.18% | 0 | 0%
GNA_0144703_Capacity | Bay Area | Mission | DUMBARTON BANK 3 | 144703 | Bank | Demand Growth | Capacity | 2024 | 105.8% | 2.57 | 5.77% | 44.54 | 43.9 | 98.56% | 0 | 0% | 44.54 | 46.16 | 103.6% | 1.62 | 3.637% | 44.54 | 46.55 | 104.5% | 2.01 | 4.513% | 44.54 | 46.77 | 105% | 2.23 | 5.007% | 44.54 | 47.11 | 105.8% | 2.57 | 5.77%
GNA_014471109_Capacity | Bay Area | Mission | DUMBARTON SUB 1109 | 14471109 | Feeder | None | None | None | 87.21% | 0 | 0% | 11.57 | 9.89 | 85.48% | 0 | 0% | 11.57 | 9.91 | 85.65% | 0 | 0% | 11.57 | 9.93 | 85.83% | 0 | 0% | 11.57 | 10 | 86.43% | 0 | 0% | 11.57 | 10.09 | 87.21% | 0 | 0%
GNA_014471110_Capacity | Bay Area | Mission | DUMBARTON SUB 1110 | 14471110 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014471112_Capacity | Bay Area | Mission | DUMBARTON SUB 1112 | 14471112 | Feeder | None | None | None | 97.97% | 0 | 0% | 12.83 | 10.72 | 83.55% | 0 | 0% | 12.83 | 11.95 | 93.14% | 0 | 0% | 12.83 | 12.38 | 96.49% | 0 | 0% | 12.83 | 12.48 | 97.27% | 0 | 0% | 12.83 | 12.57 | 97.97% | 0 | 0%
GNA_014472111_Capacity | Bay Area | Mission | DUMBARTON SUB 2111(CB 1111) | 14472111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0143501_Capacity | Bay Area | Mission | FREMONT BANK 1 | 143501 | Bank | None | None | None | 86.62% | 0 | 0% | 29.68 | 24.6 | 82.88% | 0 | 0% | 29.68 | 24.8 | 83.56% | 0 | 0% | 29.68 | 25.01 | 84.27% | 0 | 0% | 29.68 | 25.36 | 85.44% | 0 | 0% | 29.68 | 25.71 | 86.62% | 0 | 0%
GNA_014351103_Capacity | Bay Area | Mission | FREMONT 1103 | 14351103 | Feeder | None | None | None | 80.12% | 0 | 0% | 12.83 | 10.15 | 79.11% | 0 | 0% | 12.83 | 10.17 | 79.27% | 0 | 0% | 12.83 | 10.19 | 79.42% | 0 | 0% | 12.83 | 10.23 | 79.73% | 0 | 0% | 12.83 | 10.28 | 80.12% | 0 | 0%
GNA_014351104_Capacity | Bay Area | Mission | FREMONT 1104 | 14351104 | Feeder | None | None | None | 95.85% | 0 | 0% | 11.57 | 10.42 | 90.06% | 0 | 0% | 11.57 | 10.47 | 90.49% | 0 | 0% | 11.57 | 10.57 | 91.36% | 0 | 0% | 11.57 | 10.82 | 93.52% | 0 | 0% | 11.57 | 11.09 | 95.85% | 0 | 0%
GNA_014351105_Capacity | Bay Area | Mission | FREMONT 1105 | 14351105 | Feeder | None | None | None | 32.65% | 0 | 0% | 9.71 | 3.17 | 32.65% | 0 | 0% | 9.71 | 3.16 | 32.54% | 0 | 0% | 9.71 | 3.15 | 32.44% | 0 | 0% | 9.71 | 3.15 | 32.44% | 0 | 0% | 9.71 | 3.15 | 32.44% | 0 | 0%
GNA_0143502_Capacity | Bay Area | Mission | FREMONT BANK 2 | 143502 | Bank | None | None | None | 74.26% | 0 | 0% | 42.77 | 29.75 | 69.56% | 0 | 0% | 42.77 | 30.5 | 71.31% | 0 | 0% | 42.77 | 30.78 | 71.97% | 0 | 0% | 42.77 | 31.2 | 72.95% | 0 | 0% | 42.77 | 31.76 | 74.26% | 0 | 0%
GNA_014351107_Capacity | Bay Area | Mission | FREMONT 1107 | 14351107 | Feeder | None | None | None | 98.44% | 0 | 0% | 11.57 | 11.39 | 98.44% | 0 | 0% | 11.57 | 11.32 | 97.84% | 0 | 0% | 11.57 | 11.27 | 97.41% | 0 | 0% | 11.57 | 11.3 | 97.67% | 0 | 0% | 11.57 | 11.37 | 98.27% | 0 | 0%
GNA_014351108_Capacity | Bay Area | Mission | FREMONT 1108 | 14351108 | Feeder | None | None | None | 97.58% | 0 | 0% | 11.57 | 10.72 | 92.65% | 0 | 0% | 11.57 | 11.26 | 97.32% | 0 | 0% | 11.57 | 11.26 | 97.32% | 0 | 0% | 11.57 | 11.27 | 97.41% | 0 | 0% | 11.57 | 11.29 | 97.58% | 0 | 0%
GNA_014351109_Capacity | Bay Area | Mission | FREMONT 1109 | 14351109 | Feeder | None | None | None | 94.85% | 0 | 0% | 12.42 | 10.86 | 87.44% | 0 | 0% | 12.42 | 11.01 | 88.65% | 0 | 0% | 12.42 | 11.21 | 90.26% | 0 | 0% | 12.42 | 11.46 | 92.27% | 0 | 0% | 12.42 | 11.78 | 94.85% | 0 | 0%
GNA_0143503_Capacity | Bay Area | Mission | FREMONT BANK 3 | 143503 | Bank | None | None | None | 91.91% | 0 | 0% | 29.68 | 27.13 | 91.41% | 0 | 0% | 29.68 | 27.28 | 91.91% | 0 | 0% | 29.68 | 27.14 | 91.44% | 0 | 0% | 29.68 | 27.07 | 91.21% | 0 | 0% | 29.68 | 27.09 | 91.27% | 0 | 0%
GNA_014351110_Capacity | Bay Area | Mission | FREMONT 1110 | 14351110 | Feeder | None | None | None | 92.48% | 0 | 0% | 11.57 | 10.42 | 90.06% | 0 | 0% | 11.57 | 10.62 | 91.79% | 0 | 0% | 11.57 | 10.51 | 90.84% | 0 | 0% | 11.57 | 10.58 | 91.44% | 0 | 0% | 11.57 | 10.7 | 92.48% | 0 | 0%
GNA_014351111_Capacity | Bay Area | Mission | FREMONT 1111 | 14351111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014351112_Capacity | Bay Area | Mission | FREMONT 1112 | 14351112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0135001_Capacity | Bay Area | Mission | JARVIS BANK 1 | 135001 | Bank | None | None | None | 67.15% | 0 | 0% | 44.54 | 29.49 | 66.21% | 0 | 0% | 44.54 | 29.64 | 66.55% | 0 | 0% | 44.54 | 29.81 | 66.93% | 0 | 0% | 44.54 | 29.9 | 67.13% | 0 | 0% | 44.54 | 29.91 | 67.15% | 0 | 0%
GNA_013501101_Capacity | Bay Area | Mission | JARVIS 1101 | 13501101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013501103_Capacity | Bay Area | Mission | JARVIS 1103 | 13501103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013501104_Capacity | Bay Area | Mission | JARVIS 1104 | 13501104 | Feeder | None | None | None | 71.94% | 0 | 0% | 12.19 | 8.77 | 71.94% | 0 | 0% | 12.19 | 8.76 | 71.86% | 0 | 0% | 12.19 | 8.75 | 71.78% | 0 | 0% | 12.19 | 8.77 | 71.94% | 0 | 0% | 12.19 | 8.75 | 71.78% | 0 | 0%
GNA_0135002_Capacity | Bay Area | Mission | JARVIS BANK 2 | 135002 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013501105_Capacity | Bay Area | Mission | JARVIS 1105 | 13501105 | Feeder | Demand Growth | Capacity | 2025 | 104.1% | 0.48 | 4.149% | 11.57 | 11.4 | 98.53% | 0 | 0% | 11.57 | 11.52 | 99.57% | 0 | 0% | 11.57 | 11.64 | 100.6% | 0.07 | 0.605% | 11.57 | 11.83 | 102.2% | 0.26 | 2.247% | 11.57 | 12.05 | 104.1% | 0.48 | 4.149%
GNA_013501106_Capacity | Bay Area | Mission | JARVIS 1106 | 13501106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013501108_Capacity | Bay Area | Mission | JARVIS 1108 | 13501108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0135003_Capacity | Bay Area | Mission | JARVIS BANK 3 | 135003 | Bank | None | None | None | 99.1% | 0 | 0% | 44.54 | 41.17 | 92.43% | 0 | 0% | 44.54 | 42.73 | 95.94% | 0 | 0% | 44.54 | 42.93 | 96.39% | 0 | 0% | 44.54 | 43.44 | 97.53% | 0 | 0% | 44.54 | 44.14 | 99.1% | 0 | 0%
GNA_013501109_Capacity | Bay Area | Mission | JARVIS 1109 | 13501109 | Feeder | None | None | None | 95.57% | 0 | 0% | 12.19 | 10.33 | 84.74% | 0 | 0% | 12.19 | 11.65 | 95.57% | 0 | 0% | 12.19 | 11.59 | 95.08% | 0 | 0% | 12.19 | 11.6 | 95.16% | 0 | 0% | 12.19 | 11.6 | 95.16% | 0 | 0%
GNA_013501110_Capacity | Bay Area | Mission | JARVIS 1110 | 13501110 | Feeder | None | None | None | 95.67% | 0 | 0% | 10.16 | 9.12 | 89.76% | 0 | 0% | 10.16 | 9.22 | 90.75% | 0 | 0% | 10.16 | 9.33 | 91.83% | 0 | 0% | 10.16 | 9.52 | 93.7% | 0 | 0% | 10.16 | 9.72 | 95.67% | 0 | 0%
GNA_013501111_Capacity | Bay Area | Mission | JARVIS 1111 | 13501111 | Feeder | Demand Growth | Capacity | 2027 | 100.8% | 0.1 | 0.7605% | 13.15 | 12.72 | 96.73% | 0 | 0% | 13.15 | 12.89 | 98.02% | 0 | 0% | 13.15 | 12.92 | 98.25% | 0 | 0% | 13.15 | 13.05 | 99.24% | 0 | 0% | 13.15 | 13.25 | 100.8% | 0.1 | 0.7605%
GNA_013501112_Capacity | Bay Area | Mission | JARVIS 1112 | 13501112 | Feeder | None | None | None | 98.01% | 0 | 0% | 11.57 | 10.89 | 94.12% | 0 | 0% | 11.57 | 10.93 | 94.47% | 0 | 0% | 11.57 | 10.98 | 94.9% | 0 | 0% | 11.57 | 11.11 | 96.02% | 0 | 0% | 11.57 | 11.34 | 98.01% | 0 | 0%
GNA_0122203_Capacity | Bay Area | Mission | NEWARK BANK 3 | 122203 | Bank | None | None | None | 72.34% | 0 | 0% | 44.54 | 29.71 | 66.7% | 0 | 0% | 44.54 | 31.89 | 71.6% | 0 | 0% | 44.54 | 31.81 | 71.42% | 0 | 0% | 44.54 | 31.94 | 71.71% | 0 | 0% | 44.54 | 32.22 | 72.34% | 0 | 0%
GNA_012221101_Capacity | Bay Area | Mission | NEWARK 1101 | 12221101 | Feeder | None | None | None | 83.1% | 0 | 0% | 12.19 | 8.17 | 67.02% | 0 | 0% | 12.19 | 10.13 | 83.1% | 0 | 0% | 12.19 | 10.1 | 82.85% | 0 | 0% | 12.19 | 10.08 | 82.69% | 0 | 0% | 12.19 | 10.07 | 82.61% | 0 | 0%
GNA_012221102_Capacity | Bay Area | Mission | NEWARK 1102 | 12221102 | Feeder | None | None | None | 87.55% | 0 | 0% | 11.57 | 9.43 | 81.5% | 0 | 0% | 11.57 | 9.9 | 85.57% | 0 | 0% | 11.57 | 9.94 | 85.91% | 0 | 0% | 11.57 | 10.01 | 86.52% | 0 | 0% | 11.57 | 10.13 | 87.55% | 0 | 0%
GNA_012221103_Capacity | Bay Area | Mission | NEWARK 1103 | 12221103 | Feeder | None | None | None | 91.62% | 0 | 0% | 11.57 | 10.17 | 87.9% | 0 | 0% | 11.57 | 10.18 | 87.99% | 0 | 0% | 11.57 | 10.22 | 88.33% | 0 | 0% | 11.57 | 10.38 | 89.71% | 0 | 0% | 11.57 | 10.6 | 91.62% | 0 | 0%
GNA_012221104_Capacity | Bay Area | Mission | NEWARK 1104 | 12221104 | Feeder | None | None | None | 29.21% | 0 | 0% | 11.57 | 3.38 | 29.21% | 0 | 0% | 11.57 | 3.37 | 29.13% | 0 | 0% | 11.57 | 3.36 | 29.04% | 0 | 0% | 11.57 | 3.36 | 29.04% | 0 | 0% | 11.57 | 3.36 | 29.04% | 0 | 0%
GNA_0122204_Capacity | Bay Area | Mission | NEWARK BANK 4 | 122204 | Bank | None | None | None | 90.57% | 0 | 0% | 44.54 | 40.34 | 90.57% | 0 | 0% | 44.54 | 39.96 | 89.72% | 0 | 0% | 44.54 | 39.63 | 88.98% | 0 | 0% | 44.54 | 39.53 | 88.75% | 0 | 0% | 44.54 | 39.58 | 88.86% | 0 | 0%
GNA_012221105_Capacity | Bay Area | Mission | NEWARK 1105 | 12221105 | Feeder | None | None | None | 74.08% | 0 | 0% | 12.19 | 8.62 | 70.71% | 0 | 0% | 12.19 | 8.72 | 71.53% | 0 | 0% | 12.19 | 8.82 | 72.35% | 0 | 0% | 12.19 | 8.92 | 73.17% | 0 | 0% | 12.19 | 9.03 | 74.08% | 0 | 0%
GNA_012221106_Capacity | Bay Area | Mission | NEWARK 1106 | 12221106 | Feeder | None | None | None | 97.7% | 0 | 0% | 12.19 | 11.91 | 97.7% | 0 | 0% | 12.19 | 11.83 | 97.05% | 0 | 0% | 12.19 | 11.75 | 96.39% | 0 | 0% | 12.19 | 11.77 | 96.55% | 0 | 0% | 12.19 | 11.86 | 97.29% | 0 | 0%
GNA_012221107_Capacity | Bay Area | Mission | NEWARK 1107 | 12221107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012221108_Capacity | Bay Area | Mission | NEWARK 1108 | 12221108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0147202_Capacity | Bay Area | Mission | DIXON LANDING BANK 2 | 147202 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014722106_Capacity | Bay Area | Mission | DIXON LANDING 2106 | 14722106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014722107_Capacity | Bay Area | Mission | DIXON LANDING 2107 | 14722107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0147203_Capacity | Bay Area | Mission | DIXON LANDING BANK 3 | 147203 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014722109_Capacity | Bay Area | Mission | DIXON LANDING 2109 | 14722109 | Feeder | None | None | None | 95.01% | 0 | 0% | 20.04 | 18.43 | 91.97% | 0 | 0% | 20.04 | 19.04 | 95.01% | 0 | 0% | 20.04 | 18.71 | 93.36% | 0 | 0% | 20.04 | 18.6 | 92.81% | 0 | 0% | 20.04 | 18.64 | 93.01% | 0 | 0%
GNA_014722111_Capacity | Bay Area | Mission | DIXON LANDING 2111 | 14722111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0122321_Capacity | Bay Area | Mission | NEWARK BANK 21 | 122321 | Bank | None | None | None | 100% | 0 | 0% | 74.22 | 62.92 | 84.77% | 0 | 0% | 74.22 | 70.94 | 95.58% | 0 | 0% | 74.22 | 73.57 | 99.12% | 0 | 0% | 74.22 | 73.89 | 99.56% | 0 | 0% | 74.22 | 74.22 | 100% | 0 | 0%
GNA_012232102_Capacity | Bay Area | Mission | NEWARK 2102 | 12232102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012232103_Capacity | Bay Area | Mission | NEWARK 2103 | 12232103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012232104_Capacity | Bay Area | Mission | NEWARK 2104 | 12232104 | Feeder | None | None | None | 92.07% | 0 | 0% | 20.04 | 18.06 | 90.12% | 0 | 0% | 20.04 | 18.15 | 90.57% | 0 | 0% | 20.04 | 18.25 | 91.07% | 0 | 0% | 20.04 | 18.34 | 91.52% | 0 | 0% | 20.04 | 18.45 | 92.07% | 0 | 0%
GNA_012232105_Capacity | Bay Area | Mission | NEWARK 2105 | 12232105 | Feeder | None | None | None | 99.8% | 0 | 0% | 20.04 | 11.21 | 55.94% | 0 | 0% | 20.04 | 18.17 | 90.67% | 0 | 0% | 20.04 | 19.76 | 98.6% | 0 | 0% | 20.04 | 19.88 | 99.2% | 0 | 0% | 20.04 | 20 | 99.8% | 0 | 0%
GNA_0122322_Capacity | Bay Area | Mission | NEWARK BANK 22 | 122322 | Bank | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012232107_Capacity | Bay Area | Mission | NEWARK 2107 | 12232107 | Feeder | None | None | None | 86.75% | 0 | 0% | 20.15 | 17.03 | 84.52% | 0 | 0% | 20.15 | 17.14 | 85.06% | 0 | 0% | 20.15 | 17.25 | 85.61% | 0 | 0% | 20.15 | 17.37 | 86.2% | 0 | 0% | 20.15 | 17.48 | 86.75% | 0 | 0%
GNA_012232108_Capacity | Bay Area | Mission | NEWARK 2108 | 12232108 | Feeder | None | None | None | 96.21% | 0 | 0% | 20.04 | 18.42 | 91.92% | 0 | 0% | 20.04 | 18.72 | 93.41% | 0 | 0% | 20.04 | 18.94 | 94.51% | 0 | 0% | 20.04 | 19.17 | 95.66% | 0 | 0% | 20.04 | 19.28 | 96.21% | 0 | 0%
GNA_012232109_Capacity | Bay Area | Mission | NEWARK 2109 | 12232109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012232110_Capacity | Bay Area | Mission | NEWARK 2110 | 12232110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_012232111_Capacity | Bay Area | Mission | NEWARK 2111 | 12232111 | Feeder | None | None | None | 99.64% | 0 | 0% | 22.22 | 19.68 | 88.57% | 0 | 0% | 22.22 | 18.85 | 84.83% | 0 | 0% | 22.22 | 22.14 | 99.64% | 0 | 0% | 22.22 | 22.14 | 99.64% | 0 | 0% | 22.22 | 22.14 | 99.64% | 0 | 0%
GNA_0140901_Capacity | Bay Area | Mission | CASTRO VALLEY BANK 1 | 140901 | Bank | None | None | None | 90.46% | 0 | 0% | 44.54 | 38.78 | 87.07% | 0 | 0% | 44.54 | 39.45 | 88.57% | 0 | 0% | 44.54 | 39.62 | 88.95% | 0 | 0% | 44.54 | 39.93 | 89.65% | 0 | 0% | 44.54 | 40.29 | 90.46% | 0 | 0%
GNA_014091102_Capacity | Bay Area | Mission | CASTRO VALLEY 1102 (Formerly 1101) | 14091102 | Feeder | None | None | None | 98.69% | 0 | 0% | 12.19 | 11.69 | 95.9% | 0 | 0% | 12.19 | 11.87 | 97.37% | 0 | 0% | 12.19 | 11.9 | 97.62% | 0 | 0% | 12.19 | 11.96 | 98.11% | 0 | 0% | 12.19 | 12.03 | 98.69% | 0 | 0%
GNA_014091103_Capacity | Bay Area | Mission | CASTRO VALLEY 1103 (Formerly 1102) | 14091103 | Feeder | None | None | None | 66.8% | 0 | 0% | 12.83 | 7.78 | 60.64% | 0 | 0% | 12.83 | 8.46 | 65.94% | 0 | 0% | 12.83 | 8.4 | 65.47% | 0 | 0% | 12.83 | 8.45 | 65.86% | 0 | 0% | 12.83 | 8.57 | 66.8% | 0 | 0%
GNA_014091104_Capacity | Bay Area | Mission | CASTRO VALLEY 1104 (Formerly 1103) | 14091104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014091105_Capacity | Bay Area | Mission | CASTRO VALLEY 1105 (Formerly 1104) | 14091105 | Feeder | None | None | None | 98.11% | 0 | 0% | 12.19 | 11.58 | 95% | 0 | 0% | 12.19 | 11.67 | 95.73% | 0 | 0% | 12.19 | 11.78 | 96.64% | 0 | 0% | 12.19 | 11.88 | 97.46% | 0 | 0% | 12.19 | 11.96 | 98.11% | 0 | 0%
GNA_0136601_Capacity | Bay Area | Mission | PARSONS BANK 1 | 136601 | Bank | None | None | None | 6.061% | 0 | 0% | 1.98 | -0.12 | -6.061% | 0 | 0% | 1.98 | -0.11 | -5.556% | 0 | 0% | 1.98 | -0.12 | -6.061% | 0 | 0% | 1.98 | -0.11 | -5.556% | 0 | 0% | 1.98 | -0.1 | -5.051% | 0 | 0%
GNA_013660401_Capacity | Bay Area | Mission | PARSONS 0401 | 13660401 | Feeder | None | None | None | 4.211% | 0 | 0% | 2.85 | -0.12 | -4.211% | 0 | 0% | 2.85 | -0.12 | -4.211% | 0 | 0% | 2.85 | -0.12 | -4.211% | 0 | 0% | 2.85 | -0.11 | -3.86% | 0 | 0% | 2.85 | -0.11 | -3.86% | 0 | 0%
GNA_0136602_Capacity | Bay Area | Mission | PARSONS BANK 2 | 136602 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013660402_Capacity | Bay Area | Mission | PARSONS 0402 | 13660402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0140902_Capacity | Bay Area | Mission | CASTRO VALLEY BANK 2 | 140902 | Bank | Demand Growth | Capacity | 2023 | 109.3% | 4.13 | 9.273% | 44.54 | 44.8 | 100.6% | 0.26 | 0.5837% | 44.54 | 45.28 | 101.7% | 0.74 | 1.661% | 44.54 | 45.88 | 103% | 1.34 | 3.009% | 44.54 | 47.34 | 106.3% | 2.8 | 6.286% | 44.54 | 48.67 | 109.3% | 4.13 | 9.273%
GNA_014091107_Capacity | Bay Area | Mission | CASTRO VALLEY 1107 (Formerly 1105) | 14091107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014091108_Capacity | Bay Area | Mission | CASTRO VALLEY 1108 (Formerly 1106) | 14091108 | Feeder | None | None | None | 90.81% | 0 | 0% | 12.19 | 10.26 | 84.17% | 0 | 0% | 12.19 | 10.35 | 84.91% | 0 | 0% | 12.19 | 10.49 | 86.05% | 0 | 0% | 12.19 | 10.72 | 87.94% | 0 | 0% | 12.19 | 11.07 | 90.81% | 0 | 0%
GNA_014091109_Capacity | Bay Area | Mission | CASTRO VALLEY 1109 (Formerly 1107) | 14091109 | Feeder | None | None | None | 88.16% | 0 | 0% | 11.57 | 10.13 | 87.55% | 0 | 0% | 11.57 | 10.1 | 87.29% | 0 | 0% | 11.57 | 10.08 | 87.12% | 0 | 0% | 11.57 | 10.11 | 87.38% | 0 | 0% | 11.57 | 10.2 | 88.16% | 0 | 0%
GNA_0132602_Capacity | Bay Area | Mission | SOTO BANK 2 | 132602 | Bank | None | None | None | 67.17% | 0 | 0% | 1.98 | 1.32 | 66.67% | 0 | 0% | 1.98 | 1.31 | 66.16% | 0 | 0% | 1.98 | 1.31 | 66.16% | 0 | 0% | 1.98 | 1.33 | 67.17% | 0 | 0% | 1.98 | 1.33 | 67.17% | 0 | 0%
GNA_013260402_Capacity | Bay Area | Mission | SOTO 0402 | 13260402 | Feeder | None | None | None | 46.67% | 0 | 0% | 2.85 | 1.31 | 45.96% | 0 | 0% | 2.85 | 1.3 | 45.61% | 0 | 0% | 2.85 | 1.31 | 45.96% | 0 | 0% | 2.85 | 1.32 | 46.32% | 0 | 0% | 2.85 | 1.33 | 46.67% | 0 | 0%
GNA_014091110_Capacity | Bay Area | Mission | CASTRO VALLEY 1110 (Formerly 1108) | 14091110 | Feeder | None | None | None | 90.32% | 0 | 0% | 11.57 | 9.07 | 78.39% | 0 | 0% | 11.57 | 9.21 | 79.6% | 0 | 0% | 11.57 | 9.39 | 81.16% | 0 | 0% | 11.57 | 10.16 | 87.81% | 0 | 0% | 11.57 | 10.45 | 90.32% | 0 | 0%
GNA_014091111_Capacity | Bay Area | Mission | CASTRO VALLEY 1111 (Formerly 1109) | 14091111 | Feeder | None | None | None | 70.54% | 0 | 0% | 12.83 | 8.32 | 64.85% | 0 | 0% | 12.83 | 8.46 | 65.94% | 0 | 0% | 12.83 | 8.61 | 67.11% | 0 | 0% | 12.83 | 8.83 | 68.82% | 0 | 0% | 12.83 | 9.05 | 70.54% | 0 | 0%
GNA_0143801_Capacity | Bay Area | Mission | GRANT BANK 1 | 143801 | Bank | None | None | None | 63.47% | 0 | 0% | 44.54 | 27.82 | 62.46% | 0 | 0% | 44.54 | 27.56 | 61.88% | 0 | 0% | 44.54 | 27.34 | 61.38% | 0 | 0% | 44.54 | 28.27 | 63.47% | 0 | 0% | 44.54 | 28.22 | 63.36% | 0 | 0%
GNA_014381102_Capacity | Bay Area | Mission | GRANT 1102 | 14381102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014381103_Capacity | Bay Area | Mission | GRANT 1103 | 14381103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014381104_Capacity | Bay Area | Mission | GRANT 1104 | 14381104 | Feeder | None | None | None | 87.25% | 0 | 0% | 10.82 | 8.49 | 78.47% | 0 | 0% | 10.82 | 8.51 | 78.65% | 0 | 0% | 10.82 | 8.55 | 79.02% | 0 | 0% | 10.82 | 9.3 | 85.95% | 0 | 0% | 10.82 | 9.44 | 87.25% | 0 | 0%
GNA_0134601_Capacity | Bay Area | Mission | SAN LORENZO BANK 1 | 134601 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013460401_Capacity | Bay Area | Mission | SAN LORENZO 0401 | 13460401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0143802_Capacity | Bay Area | Mission | GRANT BANK 2 | 143802 | Bank | None | None | None | 86.89% | 0 | 0% | 44.54 | 37.31 | 83.77% | 0 | 0% | 44.54 | 38 | 85.32% | 0 | 0% | 44.54 | 38.11 | 85.56% | 0 | 0% | 44.54 | 38.27 | 85.92% | 0 | 0% | 44.54 | 38.7 | 86.89% | 0 | 0%
GNA_014381105_Capacity | Bay Area | Mission | GRANT 1105 | 14381105 | Feeder | None | None | None | 72.69% | 0 | 0% | 11.57 | 8.09 | 69.92% | 0 | 0% | 11.57 | 8.12 | 70.18% | 0 | 0% | 11.57 | 8.17 | 70.61% | 0 | 0% | 11.57 | 8.27 | 71.48% | 0 | 0% | 11.57 | 8.41 | 72.69% | 0 | 0%
GNA_014381106_Capacity | Bay Area | Mission | GRANT 1106 | 14381106 | Feeder | None | None | None | 99.75% | 0 | 0% | 12.19 | 11.43 | 93.77% | 0 | 0% | 12.19 | 12.07 | 99.02% | 0 | 0% | 12.19 | 12.09 | 99.18% | 0 | 0% | 12.19 | 12.05 | 98.85% | 0 | 0% | 12.19 | 12.16 | 99.75% | 0 | 0%
GNA_014381107_Capacity | Bay Area | Mission | GRANT 1107 | 14381107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014381108_Capacity | Bay Area | Mission | GRANT 1108 | 14381108 | Feeder | None | None | None | 96.02% | 0 | 0% | 11.57 | 10.88 | 94.04% | 0 | 0% | 11.57 | 10.89 | 94.12% | 0 | 0% | 11.57 | 10.91 | 94.3% | 0 | 0% | 11.57 | 10.98 | 94.9% | 0 | 0% | 11.57 | 11.11 | 96.02% | 0 | 0%
GNA_0137601_Capacity | Bay Area | Mission | MT EDEN BANK 1 | 137601 | Bank | None | None | None | 88.57% | 0 | 0% | 44.54 | 36.73 | 82.47% | 0 | 0% | 44.54 | 38.64 | 86.75% | 0 | 0% | 44.54 | 38.67 | 86.82% | 0 | 0% | 44.54 | 39 | 87.56% | 0 | 0% | 44.54 | 39.45 | 88.57% | 0 | 0%
GNA_013761101_Capacity | Bay Area | Mission | MT EDEN 1101 | 13761101 | Feeder | None | None | None | 93.77% | 0 | 0% | 12.19 | 11.43 | 93.77% | 0 | 0% | 12.19 | 11.35 | 93.11% | 0 | 0% | 12.19 | 11.29 | 92.62% | 0 | 0% | 12.19 | 11.32 | 92.86% | 0 | 0% | 12.19 | 11.38 | 93.36% | 0 | 0%
GNA_013761103_Capacity | Bay Area | Mission | MT EDEN 1103 | 13761103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013761105_Capacity | Bay Area | Mission | MT EDEN 1105 | 13761105 | Feeder | None | None | None | 50.04% | 0 | 0% | 11.57 | 5.7 | 49.27% | 0 | 0% | 11.57 | 5.71 | 49.35% | 0 | 0% | 11.57 | 5.71 | 49.35% | 0 | 0% | 11.57 | 5.76 | 49.78% | 0 | 0% | 11.57 | 5.79 | 50.04% | 0 | 0%
GNA_013761109_Capacity | Bay Area | Mission | MT EDEN 1109 | 13761109 | Feeder | None | None | None | 67.84% | 0 | 0% | 12.19 | 7.97 | 65.38% | 0 | 0% | 12.19 | 8.01 | 65.71% | 0 | 0% | 12.19 | 8.02 | 65.79% | 0 | 0% | 12.19 | 8.09 | 66.37% | 0 | 0% | 12.19 | 8.27 | 67.84% | 0 | 0%
GNA_013761114_Capacity | Bay Area | Mission | MT EDEN 1114 | 13761114 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0137602_Capacity | Bay Area | Mission | MT EDEN BANK 2 | 137602 | Bank | None | None | None | 93.98% | 0 | 0% | 44.54 | 41.86 | 93.98% | 0 | 0% | 44.54 | 41.44 | 93.04% | 0 | 0% | 44.54 | 41.11 | 92.3% | 0 | 0% | 44.54 | 41.27 | 92.66% | 0 | 0% | 44.54 | 41.69 | 93.6% | 0 | 0%
GNA_013761102_Capacity | Bay Area | Mission | MT EDEN 1102 | 13761102 | Feeder | None | None | None | 78.22% | 0 | 0% | 11.57 | 8.3 | 71.74% | 0 | 0% | 11.57 | 9.03 | 78.05% | 0 | 0% | 11.57 | 9.01 | 77.87% | 0 | 0% | 11.57 | 9.03 | 78.05% | 0 | 0% | 11.57 | 9.05 | 78.22% | 0 | 0%
GNA_013761104_Capacity | Bay Area | Mission | MT EDEN 1104 | 13761104 | Feeder | None | None | None | 93.68% | 0 | 0% | 12.19 | 11.42 | 93.68% | 0 | 0% | 12.19 | 11.2 | 91.88% | 0 | 0% | 12.19 | 11.04 | 90.57% | 0 | 0% | 12.19 | 10.98 | 90.07% | 0 | 0% | 12.19 | 10.96 | 89.91% | 0 | 0%
GNA_013761106_Capacity | Bay Area | Mission | MT EDEN 1106 | 13761106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013761107_Capacity | Bay Area | Mission | MT EDEN 1107 | 13761107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013761108_Capacity | Bay Area | Mission | MT EDEN 1108 | 13761108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0137603_Capacity | Bay Area | Mission | MT EDEN BANK 3 | 137603 | Bank | None | None | None | 95.04% | 0 | 0% | 44.54 | 42.33 | 95.04% | 0 | 0% | 44.54 | 38.1 | 85.54% | 0 | 0% | 44.54 | 37.95 | 85.2% | 0 | 0% | 44.54 | 41.47 | 93.11% | 0 | 0% | 44.54 | 41.58 | 93.35% | 0 | 0%
GNA_013761110_Capacity | Bay Area | Mission | MT EDEN 1110 | 13761110 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013761111_Capacity | Bay Area | Mission | MT EDEN 1111 | 13761111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013761112_Capacity | Bay Area | Mission | MT EDEN 1112 | 13761112 | Feeder | None | None | None | 90.32% | 0 | 0% | 12.19 | 8.54 | 70.06% | 0 | 0% | 12.19 | 9.87 | 80.97% | 0 | 0% | 12.19 | 9.9 | 81.21% | 0 | 0% | 12.19 | 10.93 | 89.66% | 0 | 0% | 12.19 | 11.01 | 90.32% | 0 | 0%
GNA_013761113_Capacity | Bay Area | Mission | MT EDEN 1113 | 13761113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0131101_Capacity | Bay Area | Mission | SAN LEANDRO BANK 1 | 131101 | Bank | None | None | None | 92.46% | 0 | 0% | 44.54 | 40.39 | 90.68% | 0 | 0% | 44.54 | 39.83 | 89.43% | 0 | 0% | 44.54 | 39.41 | 88.48% | 0 | 0% | 44.54 | 41.09 | 92.25% | 0 | 0% | 44.54 | 41.18 | 92.46% | 0 | 0%
GNA_013111101_Capacity | Bay Area | Mission | SAN LEANDRO U 1101 | 13111101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013111102_Capacity | Bay Area | Mission | SAN LEANDRO U 1102 | 13111102 | Feeder | None | None | None | 87.12% | 0 | 0% | 11.57 | 9.44 | 81.59% | 0 | 0% | 11.57 | 9.51 | 82.2% | 0 | 0% | 11.57 | 9.58 | 82.8% | 0 | 0% | 11.57 | 9.78 | 84.53% | 0 | 0% | 11.57 | 10.08 | 87.12% | 0 | 0%
GNA_0130301_Capacity | Bay Area | Mission | BANCROFT BANK 1 | 130301 | Bank | None | None | None | 88.38% | 0 | 0% | 1.98 | 1.62 | 81.82% | 0 | 0% | 1.98 | 1.64 | 82.83% | 0 | 0% | 1.98 | 1.65 | 83.33% | 0 | 0% | 1.98 | 1.68 | 84.85% | 0 | 0% | 1.98 | 1.75 | 88.38% | 0 | 0%
GNA_013030401_Capacity | Bay Area | Mission | BANCROFT 0401 | 13030401 | Feeder | None | None | None | 63.47% | 0 | 0% | 2.71 | 1.6 | 59.04% | 0 | 0% | 2.71 | 1.61 | 59.41% | 0 | 0% | 2.71 | 1.63 | 60.15% | 0 | 0% | 2.71 | 1.65 | 60.89% | 0 | 0% | 2.71 | 1.72 | 63.47% | 0 | 0%
GNA_0134801_Capacity | Bay Area | Mission | ESTUDILLO BANK 1 | 134801 | Bank | None | None | None | 75.25% | 0 | 0% | 1.98 | 1.37 | 69.19% | 0 | 0% | 1.98 | 1.38 | 69.7% | 0 | 0% | 1.98 | 1.39 | 70.2% | 0 | 0% | 1.98 | 1.43 | 72.22% | 0 | 0% | 1.98 | 1.49 | 75.25% | 0 | 0%
GNA_013480401_Capacity | Bay Area | Mission | ESTUDILLO 0401 | 13480401 | Feeder | None | None | None | 51.93% | 0 | 0% | 2.85 | 1.35 | 47.37% | 0 | 0% | 2.85 | 1.37 | 48.07% | 0 | 0% | 2.85 | 1.38 | 48.42% | 0 | 0% | 2.85 | 1.42 | 49.82% | 0 | 0% | 2.85 | 1.48 | 51.93% | 0 | 0%
GNA_013111103_Capacity | Bay Area | Mission | SAN LEANDRO U 1103 | 13111103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013111104_Capacity | Bay Area | Mission | SAN LEANDRO U 1104 | 13111104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013111110_Capacity | Bay Area | Mission | SAN LEANDRO U 1110 | 13111110 | Feeder | None | None | None | 64.64% | 0 | 0% | 12.19 | 7.36 | 60.38% | 0 | 0% | 12.19 | 7.4 | 60.71% | 0 | 0% | 12.19 | 7.47 | 61.28% | 0 | 0% | 12.19 | 7.65 | 62.76% | 0 | 0% | 12.19 | 7.88 | 64.64% | 0 | 0%
GNA_013111151_Capacity | Bay Area | Mission | SAN LEANDRO U 1151 | 13111151 | Feeder | None | None | None | 38.27% | 0 | 0% | 12.83 | 4.81 | 37.49% | 0 | 0% | 12.83 | 4.82 | 37.57% | 0 | 0% | 12.83 | 4.81 | 37.49% | 0 | 0% | 12.83 | 4.86 | 37.88% | 0 | 0% | 12.83 | 4.91 | 38.27% | 0 | 0%
GNA_0122401_Capacity | Bay Area | Mission | HAYWARD O BANK 1 | 122401 | Bank | None | None | None | 75.25% | 0 | 0% | 1.98 | 1.48 | 74.75% | 0 | 0% | 1.98 | 1.48 | 74.75% | 0 | 0% | 1.98 | 1.47 | 74.24% | 0 | 0% | 1.98 | 1.48 | 74.75% | 0 | 0% | 1.98 | 1.49 | 75.25% | 0 | 0%
GNA_012240401_Capacity | Bay Area | Mission | MISSION STATION O 0401 | 12240401 | Feeder | None | None | None | 51.58% | 0 | 0% | 2.85 | 1.47 | 51.58% | 0 | 0% | 2.85 | 1.47 | 51.58% | 0 | 0% | 2.85 | 1.46 | 51.23% | 0 | 0% | 2.85 | 1.47 | 51.58% | 0 | 0% | 2.85 | 1.47 | 51.58% | 0 | 0%
GNA_0122402_Capacity | Bay Area | Mission | HAYWARD O BANK 2 | 122402 | Bank | None | None | None | 79.29% | 0 | 0% | 1.98 | 1.53 | 77.27% | 0 | 0% | 1.98 | 1.53 | 77.27% | 0 | 0% | 1.98 | 1.53 | 77.27% | 0 | 0% | 1.98 | 1.55 | 78.28% | 0 | 0% | 1.98 | 1.57 | 79.29% | 0 | 0%
GNA_012240402_Capacity | Bay Area | Mission | MISSION STATION O 0402 | 12240402 | Feeder | None | None | None | 54.39% | 0 | 0% | 2.85 | 1.51 | 52.98% | 0 | 0% | 2.85 | 1.51 | 52.98% | 0 | 0% | 2.85 | 1.51 | 52.98% | 0 | 0% | 2.85 | 1.53 | 53.68% | 0 | 0% | 2.85 | 1.55 | 54.39% | 0 | 0%
GNA_0131102_Capacity | Bay Area | Mission | SAN LEANDRO BANK 2 | 131102 | Bank | None | None | None | 90.39% | 0 | 0% | 44.54 | 37.84 | 84.96% | 0 | 0% | 44.54 | 37.84 | 84.96% | 0 | 0% | 44.54 | 38.6 | 86.66% | 0 | 0% | 44.54 | 39.61 | 88.93% | 0 | 0% | 44.54 | 40.26 | 90.39% | 0 | 0%
GNA_013111105_Capacity | Bay Area | Mission | SAN LEANDRO U 1105 | 13111105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013111106_Capacity | Bay Area | Mission | SAN LEANDRO U 1106 | 13111106 | Feeder | None | None | None | 52.38% | 0 | 0% | 11.57 | 6.06 | 52.38% | 0 | 0% | 11.57 | 5.91 | 51.08% | 0 | 0% | 11.57 | 5.82 | 50.3% | 0 | 0% | 11.57 | 5.86 | 50.65% | 0 | 0% | 11.57 | 5.91 | 51.08% | 0 | 0%
GNA_013111107_Capacity | Bay Area | Mission | SAN LEANDRO U 1107 | 13111107 | Feeder | None | None | None | 70.88% | 0 | 0% | 12.19 | 8.5 | 69.73% | 0 | 0% | 12.19 | 8.52 | 69.89% | 0 | 0% | 12.19 | 8.54 | 70.06% | 0 | 0% | 12.19 | 8.58 | 70.39% | 0 | 0% | 12.19 | 8.64 | 70.88% | 0 | 0%
GNA_013111108_Capacity | Bay Area | Mission | SAN LEANDRO U 1108 | 13111108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013111109_Capacity | Bay Area | Mission | SAN LEANDRO U 1109 | 13111109 | Feeder | None | None | None | 78.74% | 0 | 0% | 11.57 | 6.64 | 57.39% | 0 | 0% | 11.57 | 6.9 | 59.64% | 0 | 0% | 11.57 | 7.79 | 67.33% | 0 | 0% | 11.57 | 8.78 | 75.89% | 0 | 0% | 11.57 | 9.11 | 78.74% | 0 | 0%
GNA_013111111_Capacity | Bay Area | Mission | SAN LEANDRO U 1111 | 13111111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0131103_Capacity | Bay Area | Mission | SAN LEANDRO BANK 3 | 131103 | Bank | None | None | None | 89.32% | 0 | 0% | 29.68 | 25.59 | 86.22% | 0 | 0% | 29.68 | 25.4 | 85.58% | 0 | 0% | 29.68 | 25.46 | 85.78% | 0 | 0% | 29.68 | 25.95 | 87.43% | 0 | 0% | 29.68 | 26.51 | 89.32% | 0 | 0%
GNA_013111112_Capacity | Bay Area | Mission | SAN LEANDRO U 1112 | 13111112 | Feeder | None | None | None | 16.25% | 0 | 0% | 11.57 | 1.88 | 16.25% | 0 | 0% | 11.57 | 1.86 | 16.08% | 0 | 0% | 11.57 | 1.86 | 16.08% | 0 | 0% | 11.57 | 1.86 | 16.08% | 0 | 0% | 11.57 | 1.84 | 15.9% | 0 | 0%
GNA_013111113_Capacity | Bay Area | Mission | SAN LEANDRO U 1113 | 13111113 | Feeder | None | None | None | 66.72% | 0 | 0% | 11.57 | 7.59 | 65.6% | 0 | 0% | 11.57 | 7.6 | 65.69% | 0 | 0% | 11.57 | 7.63 | 65.95% | 0 | 0% | 11.57 | 7.67 | 66.29% | 0 | 0% | 11.57 | 7.72 | 66.72% | 0 | 0%
GNA_013111114_Capacity | Bay Area | Mission | SAN LEANDRO U 1114 | 13111114 | Feeder | None | None | None | 96.97% | 0 | 0% | 11.57 | 10.56 | 91.27% | 0 | 0% | 11.57 | 10.63 | 91.88% | 0 | 0% | 11.57 | 10.74 | 92.83% | 0 | 0% | 11.57 | 10.97 | 94.81% | 0 | 0% | 11.57 | 11.22 | 96.97% | 0 | 0%
GNA_013111115_Capacity | Bay Area | Mission | SAN LEANDRO U 1115 | 13111115 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_013111116_Capacity | Bay Area | Mission | SAN LEANDRO U 1116 | 13111116 | Feeder | None | None | None | 58.16% | 0 | 0% | 9.99 | 5.54 | 55.46% | 0 | 0% | 9.99 | 5.54 | 55.46% | 0 | 0% | 9.99 | 5.58 | 55.86% | 0 | 0% | 9.99 | 5.68 | 56.86% | 0 | 0% | 9.99 | 5.81 | 58.16% | 0 | 0%
GNA_0129801_Capacity | Bay Area | Mission | WARD BANK 1 | 129801 | Bank | None | None | None | 83.47% | 0 | 0% | 2.48 | 1.98 | 79.84% | 0 | 0% | 2.48 | 1.98 | 79.84% | 0 | 0% | 2.48 | 2 | 80.65% | 0 | 0% | 2.48 | 2.04 | 82.26% | 0 | 0% | 2.48 | 2.07 | 83.47% | 0 | 0%
GNA_012980401_Capacity | Bay Area | Mission | WARD 0401 | 12980401 | Feeder | None | None | None | 68.07% | 0 | 0% | 2.85 | 1.84 | 64.56% | 0 | 0% | 2.85 | 1.85 | 64.91% | 0 | 0% | 2.85 | 1.87 | 65.61% | 0 | 0% | 2.85 | 1.9 | 66.67% | 0 | 0% | 2.85 | 1.94 | 68.07% | 0 | 0%
GNA_0144203_Capacity | Bay Area | Mission | CAYETANO BANK 3 | 144203 | Bank | None | None | None | 66.13% | 0 | 0% | 44.52 | 21.7 | 48.74% | 0 | 0% | 44.52 | 25.76 | 57.86% | 0 | 0% | 44.52 | 25.93 | 58.24% | 0 | 0% | 44.52 | 29.1 | 65.36% | 0 | 0% | 44.52 | 29.44 | 66.13% | 0 | 0%
GNA_014422109_Capacity | Bay Area | Mission | CAYETANO 2109 | 14422109 | Feeder | None | None | None | 82% | 0 | 0% | 21.11 | 13.5 | 63.95% | 0 | 0% | 21.11 | 16.95 | 80.29% | 0 | 0% | 21.11 | 17.02 | 80.63% | 0 | 0% | 21.11 | 17.14 | 81.19% | 0 | 0% | 21.11 | 17.31 | 82% | 0 | 0%
GNA_014422111_Capacity | Bay Area | Mission | CAYETANO 2111 | 14422111 | Feeder | None | None | None | 81.19% | 0 | 0% | 21.11 | 13.43 | 63.62% | 0 | 0% | 21.11 | 14.08 | 66.7% | 0 | 0% | 21.11 | 14.04 | 66.51% | 0 | 0% | 21.11 | 17.09 | 80.96% | 0 | 0% | 21.11 | 17.14 | 81.19% | 0 | 0%
GNA_0144001_Capacity | Bay Area | Mission | LAS POSITAS BANK 1 | 144001 | Bank | None | None | None | 71.24% | 0 | 0% | 44.44 | 29.18 | 65.66% | 0 | 0% | 44.44 | 31.3 | 70.43% | 0 | 0% | 44.44 | 31.35 | 70.54% | 0 | 0% | 44.44 | 31.5 | 70.88% | 0 | 0% | 44.44 | 31.66 | 71.24% | 0 | 0%
GNA_014402103_Capacity | Bay Area | Mission | LAS POSITAS 2103 | 14402103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014402104_Capacity | Bay Area | Mission | LAS POSITAS 2104 | 14402104 | Feeder | None | None | None | 92.13% | 0 | 0% | 21.22 | 19.5 | 91.89% | 0 | 0% | 21.22 | 19.49 | 91.85% | 0 | 0% | 21.22 | 19.46 | 91.71% | 0 | 0% | 21.22 | 19.5 | 91.89% | 0 | 0% | 21.22 | 19.55 | 92.13% | 0 | 0%
GNA_0144002_Capacity | Bay Area | Mission | LAS POSITAS BANK 2 | 144002 | Bank | None | None | None | 93.3% | 0 | 0% | 72.22 | 64.32 | 89.06% | 0 | 0% | 72.22 | 67.38 | 93.3% | 0 | 0% | 72.22 | 66.75 | 92.43% | 0 | 0% | 72.22 | 66.8 | 92.5% | 0 | 0% | 72.22 | 67.13 | 92.95% | 0 | 0%
GNA_014402105_Capacity | Bay Area | Mission | LAS POSITAS 2105 | 14402105 | Feeder | None | None | None | 97.29% | 0 | 0% | 21.41 | 16.49 | 77.02% | 0 | 0% | 21.41 | 20.74 | 96.87% | 0 | 0% | 21.41 | 20.72 | 96.78% | 0 | 0% | 21.41 | 20.78 | 97.06% | 0 | 0% | 21.41 | 20.83 | 97.29% | 0 | 0%
GNA_014402106_Capacity | Bay Area | Mission | LAS POSITAS 2106 | 14402106 | Feeder | None | None | None | 94.58% | 0 | 0% | 21.41 | 20.11 | 93.93% | 0 | 0% | 21.41 | 20.12 | 93.97% | 0 | 0% | 21.41 | 20.12 | 93.97% | 0 | 0% | 21.41 | 20.16 | 94.16% | 0 | 0% | 21.41 | 20.25 | 94.58% | 0 | 0%
GNA_014402107_Capacity | Bay Area | Mission | LAS POSITAS 2107 | 14402107 | Feeder | None | None | None | 88.7% | 0 | 0% | 21.41 | 18.99 | 88.7% | 0 | 0% | 21.41 | 18.78 | 87.72% | 0 | 0% | 21.41 | 18.58 | 86.78% | 0 | 0% | 21.41 | 18.39 | 85.89% | 0 | 0% | 21.41 | 18.26 | 85.29% | 0 | 0%
GNA_014402108_Capacity | Bay Area | Mission | LAS POSITAS 2108 | 14402108 | Feeder | None | None | None | 81.72% | 0 | 0% | 21.22 | 16.86 | 79.45% | 0 | 0% | 21.22 | 16.84 | 79.36% | 0 | 0% | 21.22 | 16.93 | 79.78% | 0 | 0% | 21.22 | 17.14 | 80.77% | 0 | 0% | 21.22 | 17.34 | 81.72% | 0 | 0%
GNA_0144003_Capacity | Bay Area | Mission | LAS POSITAS BANK 3 | 144003 | Bank | None | None | None | 73.94% | 0 | 0% | 44.52 | 30.62 | 68.78% | 0 | 0% | 44.52 | 31.7 | 71.2% | 0 | 0% | 44.52 | 31.67 | 71.14% | 0 | 0% | 44.52 | 32.7 | 73.45% | 0 | 0% | 44.52 | 32.92 | 73.94% | 0 | 0%
GNA_014402109_Capacity | Bay Area | Mission | LAS POSITAS 2109 | 14402109 | Feeder | None | None | None | 98.93% | 0 | 0% | 21.41 | 19.59 | 91.5% | 0 | 0% | 21.41 | 20.39 | 95.24% | 0 | 0% | 21.41 | 20.35 | 95.05% | 0 | 0% | 21.41 | 21.08 | 98.46% | 0 | 0% | 21.41 | 21.18 | 98.93% | 0 | 0%
GNA_014402110_Capacity | Bay Area | Mission | LAS POSITAS 2110 | 14402110 | Feeder | None | None | None | 72.43% | 0 | 0% | 21.22 | 14.86 | 70.03% | 0 | 0% | 21.22 | 15.19 | 71.58% | 0 | 0% | 21.22 | 15.24 | 71.82% | 0 | 0% | 21.22 | 15.3 | 72.1% | 0 | 0% | 21.22 | 15.37 | 72.43% | 0 | 0%
GNA_0140501_Capacity | Bay Area | Mission | NORTH DUBLIN BANK 1 | 140501 | Bank | None | None | None | 94.61% | 0 | 0% | 44.52 | 38.7 | 86.93% | 0 | 0% | 44.52 | 39.82 | 89.44% | 0 | 0% | 44.52 | 39.84 | 89.49% | 0 | 0% | 44.52 | 41.7 | 93.67% | 0 | 0% | 44.52 | 42.12 | 94.61% | 0 | 0%
GNA_014052101_Capacity | Bay Area | Mission | NORTH DUBLIN 2101 | 14052101 | Feeder | None | None | None | 99.07% | 0 | 0% | 21.41 | 18.35 | 85.71% | 0 | 0% | 21.41 | 19.49 | 91.03% | 0 | 0% | 21.41 | 19.47 | 90.94% | 0 | 0% | 21.41 | 21.07 | 98.41% | 0 | 0% | 21.41 | 21.21 | 99.07% | 0 | 0%
GNA_014052103_Capacity | Bay Area | Mission | NORTH DUBLIN 2103 | 14052103 | Feeder | None | None | None | 95.8% | 0 | 0% | 21.41 | 20.1 | 93.88% | 0 | 0% | 21.41 | 20.08 | 93.79% | 0 | 0% | 21.41 | 20.08 | 93.79% | 0 | 0% | 21.41 | 20.26 | 94.63% | 0 | 0% | 21.41 | 20.51 | 95.8% | 0 | 0%
GNA_0142303_Capacity | Bay Area | Mission | SAN RAMON BANK 3 | 142303 | Bank | None | None | None | 91.85% | 0 | 0% | 74.22 | 68.17 | 91.85% | 0 | 0% | 74.22 | 68.17 | 91.85% | 0 | 0% | 74.22 | 67.65 | 91.15% | 0 | 0% | 74.22 | 67.54 | 91% | 0 | 0% | 74.22 | 67.63 | 91.12% | 0 | 0%
GNA_014232101_Capacity | Bay Area | Mission | SAN RAMON 2101 | 14232101 | Feeder | None | None | None | 92.94% | 0 | 0% | 21.11 | 19.62 | 92.94% | 0 | 0% | 21.11 | 19.35 | 91.66% | 0 | 0% | 21.11 | 19.21 | 91% | 0 | 0% | 21.11 | 19.28 | 91.33% | 0 | 0% | 21.11 | 19.42 | 91.99% | 0 | 0%
GNA_014232102_Capacity | Bay Area | Mission | SAN RAMON 2102 | 14232102 | Feeder | None | None | None | 91.66% | 0 | 0% | 21.11 | 18.59 | 88.06% | 0 | 0% | 21.11 | 19.25 | 91.19% | 0 | 0% | 21.11 | 19.17 | 90.81% | 0 | 0% | 21.11 | 19.24 | 91.14% | 0 | 0% | 21.11 | 19.35 | 91.66% | 0 | 0%
GNA_014232103_Capacity | Bay Area | Mission | SAN RAMON 2103 | 14232103 | Feeder | None | None | None | 80.84% | 0 | 0% | 18.63 | 15.06 | 80.84% | 0 | 0% | 18.63 | 15.02 | 80.62% | 0 | 0% | 18.63 | 14.99 | 80.46% | 0 | 0% | 18.63 | 14.97 | 80.35% | 0 | 0% | 18.63 | 14.98 | 80.41% | 0 | 0%
GNA_014232104_Capacity | Bay Area | Mission | SAN RAMON 2104 | 14232104 | Feeder | None | None | None | 89.64% | 0 | 0% | 18.63 | 16.7 | 89.64% | 0 | 0% | 18.63 | 16.22 | 87.06% | 0 | 0% | 18.63 | 15.87 | 85.19% | 0 | 0% | 18.63 | 15.6 | 83.74% | 0 | 0% | 18.63 | 15.58 | 83.63% | 0 | 0%
GNA_0142304_Capacity | Bay Area | Mission | SAN RAMON BANK 4 | 142304 | Bank | None | None | None | 96.13% | 0 | 0% | 74.22 | 64.92 | 87.47% | 0 | 0% | 74.22 | 69.12 | 93.13% | 0 | 0% | 74.22 | 68.88 | 92.81% | 0 | 0% | 74.22 | 71.16 | 95.88% | 0 | 0% | 74.22 | 71.35 | 96.13% | 0 | 0%
GNA_014232105_Capacity | Bay Area | Mission | SAN RAMON 2105 | 14232105 | Feeder | None | None | None | 88.44% | 0 | 0% | 21.11 | 14.15 | 67.03% | 0 | 0% | 21.11 | 18.67 | 88.44% | 0 | 0% | 21.11 | 18.62 | 88.2% | 0 | 0% | 21.11 | 18.59 | 88.06% | 0 | 0% | 21.11 | 18.56 | 87.92% | 0 | 0%
GNA_014232106_Capacity | Bay Area | Mission | SAN RAMON 2106 | 14232106 | Feeder | None | None | None | 97.48% | 0 | 0% | 21.41 | 18.89 | 88.23% | 0 | 0% | 21.41 | 18.76 | 87.62% | 0 | 0% | 21.41 | 18.64 | 87.06% | 0 | 0% | 21.41 | 20.87 | 97.48% | 0 | 0% | 21.41 | 20.85 | 97.38% | 0 | 0%
GNA_014232107_Capacity | Bay Area | Mission | SAN RAMON 2107 | 14232107 | Feeder | None | None | None | 90.48% | 0 | 0% | 21.11 | 18.72 | 88.68% | 0 | 0% | 21.11 | 18.7 | 88.58% | 0 | 0% | 21.11 | 18.7 | 88.58% | 0 | 0% | 21.11 | 18.87 | 89.39% | 0 | 0% | 21.11 | 19.1 | 90.48% | 0 | 0%
GNA_014232108_Capacity | Bay Area | Mission | SAN RAMON 2108 | 14232108 | Feeder | None | None | None | 89.53% | 0 | 0% | 18.63 | 16.68 | 89.53% | 0 | 0% | 18.63 | 16.64 | 89.32% | 0 | 0% | 18.63 | 16.61 | 89.16% | 0 | 0% | 18.63 | 16.63 | 89.26% | 0 | 0% | 18.63 | 16.68 | 89.53% | 0 | 0%
GNA_0142305_Capacity | Bay Area | Mission | SAN RAMON BANK 5 | 142305 | Bank | None | None | None | 57.34% | 0 | 0% | 74.22 | 42.13 | 56.76% | 0 | 0% | 74.22 | 41.92 | 56.48% | 0 | 0% | 74.22 | 41.75 | 56.25% | 0 | 0% | 74.22 | 42.52 | 57.29% | 0 | 0% | 74.22 | 42.56 | 57.34% | 0 | 0%
GNA_014232110_Capacity | Bay Area | Mission | SAN RAMON 2110 | 14232110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014232111_Capacity | Bay Area | Mission | SAN RAMON 2111 | 14232111 | Feeder | None | None | None | 95.26% | 0 | 0% | 21.11 | 19.55 | 92.61% | 0 | 0% | 21.11 | 19.4 | 91.9% | 0 | 0% | 21.11 | 19.31 | 91.47% | 0 | 0% | 21.11 | 20.11 | 95.26% | 0 | 0% | 21.11 | 20.05 | 94.98% | 0 | 0%
GNA_014232114_Capacity | Bay Area | Mission | SAN RAMON 2114 | 14232114 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0142306_Capacity | Bay Area | Mission | SAN RAMON BANK 6 | 142306 | Bank | None | None | None | 87.09% | 0 | 0% | 74.22 | 61.36 | 82.67% | 0 | 0% | 74.22 | 63.99 | 86.22% | 0 | 0% | 74.22 | 64.14 | 86.42% | 0 | 0% | 74.22 | 64.37 | 86.73% | 0 | 0% | 74.22 | 64.64 | 87.09% | 0 | 0%
GNA_014232116_Capacity | Bay Area | Mission | SAN RAMON 2116 | 14232116 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014232117_Capacity | Bay Area | Mission | SAN RAMON 2117 | 14232117 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_014232118_Capacity | Bay Area | Mission | SAN RAMON 2118 | 14232118 | Feeder | None | None | None | 99.14% | 0 | 0% | 18.63 | 18.25 | 97.96% | 0 | 0% | 18.63 | 18.29 | 98.17% | 0 | 0% | 18.63 | 18.33 | 98.39% | 0 | 0% | 18.63 | 18.39 | 98.71% | 0 | 0% | 18.63 | 18.47 | 99.14% | 0 | 0%
GNA_014232119_Capacity | Bay Area | Mission | SAN RAMON 2119 | 14232119 | Feeder | None | None | None | 82.95% | 0 | 0% | 21.11 | 16.52 | 78.26% | 0 | 0% | 21.11 | 17.46 | 82.71% | 0 | 0% | 21.11 | 17.43 | 82.57% | 0 | 0% | 21.11 | 17.47 | 82.76% | 0 | 0% | 21.11 | 17.51 | 82.95% | 0 | 0%
GNA_0145001_Capacity | Bay Area | Mission | VINEYARD BANK 1 | 145001 | Bank | None | None | None | 71.98% | 0 | 0% | 74.22 | 51.95 | 69.99% | 0 | 0% | 74.22 | 53.42 | 71.98% | 0 | 0% | 74.22 | 52.86 | 71.22% | 0 | 0% | 74.22 | 51.43 | 69.29% | 0 | 0% | 74.22 | 51.61 | 69.54% | 0 | 0%
GNA_014502104_Capacity | Bay Area | Mission | VINEYARD 2104 | 14502104 | Feeder | None | None | None | 83.31% | 0 | 0% | 18.63 | 13.92 | 74.72% | 0 | 0% | 18.63 | 15.12 | 81.16% | 0 | 0% | 18.63 | 15.19 | 81.54% | 0 | 0% | 18.63 | 15.35 | 82.39% | 0 | 0% | 18.63 | 15.52 | 83.31% | 0 | 0%
GNA_014502105_Capacity | Bay Area | Mission | VINEYARD 2105 | 14502105 | Feeder | None | None | None | 96.64% | 0 | 0% | 21.11 | 20.4 | 96.64% | 0 | 0% | 21.11 | 20.04 | 94.93% | 0 | 0% | 21.11 | 19.81 | 93.84% | 0 | 0% | 21.11 | 18.04 | 85.46% | 0 | 0% | 21.11 | 18.01 | 85.32% | 0 | 0%
GNA_014502106_Capacity | Bay Area | Mission | VINEYARD 2106 | 14502106 | Feeder | None | None | None | 99.19% | 0 | 0% | 18.63 | 17.56 | 94.26% | 0 | 0% | 18.63 | 18.48 | 99.19% | 0 | 0% | 18.63 | 18.17 | 97.53% | 0 | 0% | 18.63 | 18.03 | 96.78% | 0 | 0% | 18.63 | 17.96 | 96.4% | 0 | 0%
GNA_0145002_Capacity | Bay Area | Mission | VINEYARD BANK 2 | 145002 | Bank | None | None | None | 97.87% | 0 | 0% | 74.22 | 68.82 | 92.72% | 0 | 0% | 74.22 | 67.83 | 91.39% | 0 | 0% | 74.22 | 67.23 | 90.58% | 0 | 0% | 74.22 | 72.17 | 97.24% | 0 | 0% | 74.22 | 72.64 | 97.87% | 0 | 0%
GNA_014502107_Capacity | Bay Area | Mission | VINEYARD 2107 | 14502107 | Feeder | None | None | None | 97.25% | 0 | 0% | 22.22 | 20.24 | 91.09% | 0 | 0% | 22.22 | 20.23 | 91.04% | 0 | 0% | 22.22 | 20.25 | 91.13% | 0 | 0% | 22.22 | 21.45 | 96.53% | 0 | 0% | 22.22 | 21.61 | 97.25% | 0 | 0%
GNA_014502108_Capacity | Bay Area | Mission | VINEYARD 2108 | 14502108 | Feeder | None | None | None | 94.98% | 0 | 0% | 21.11 | 19.84 | 93.98% | 0 | 0% | 21.11 | 19.76 | 93.6% | 0 | 0% | 21.11 | 19.75 | 93.56% | 0 | 0% | 21.11 | 19.92 | 94.36% | 0 | 0% | 21.11 | 20.05 | 94.98% | 0 | 0%
GNA_014502109_Capacity | Bay Area | Mission | VINEYARD 2109 | 14502109 | Feeder | None | None | None | 95.76% | 0 | 0% | 18.63 | 14.82 | 79.55% | 0 | 0% | 18.63 | 14.51 | 77.89% | 0 | 0% | 18.63 | 14.26 | 76.54% | 0 | 0% | 18.63 | 17.84 | 95.76% | 0 | 0% | 18.63 | 17.8 | 95.54% | 0 | 0%
GNA_014502110_Capacity | Bay Area | Mission | VINEYARD 2110 | 14502110 | Feeder | None | None | None | 93.23% | 0 | 0% | 21.11 | 19.68 | 93.23% | 0 | 0% | 21.11 | 19.3 | 91.43% | 0 | 0% | 21.11 | 19.2 | 90.95% | 0 | 0% | 21.11 | 19.37 | 91.76% | 0 | 0% | 21.11 | 19.62 | 92.94% | 0 | 0%
GNA_0121401_Capacity | Bay Area | Mission | LIVERMORE BANK 1 | 121401 | Bank | None | None | None | 85.02% | 0 | 0% | 15.82 | 10.12 | 63.97% | 0 | 0% | 15.82 | 13.45 | 85.02% | 0 | 0% | 15.82 | 13.37 | 84.51% | 0 | 0% | 15.82 | 13.31 | 84.13% | 0 | 0% | 15.82 | 13.25 | 83.75% | 0 | 0%
GNA_012141101_Capacity | Bay Area | Mission | LIVERMORE 1101 | 12141101 | Feeder | None | None | None | 85.18% | 0 | 0% | 10.46 | 6 | 57.36% | 0 | 0% | 10.46 | 8.91 | 85.18% | 0 | 0% | 10.46 | 8.85 | 84.61% | 0 | 0% | 10.46 | 8.82 | 84.32% | 0 | 0% | 10.46 | 8.78 | 83.94% | 0 | 0%
GNA_012141103_Capacity | Bay Area | Mission | LIVERMORE 1103 | 12141103 | Feeder | None | None | None | 53.69% | 0 | 0% | 9.22 | 4.59 | 49.78% | 0 | 0% | 9.22 | 4.95 | 53.69% | 0 | 0% | 9.22 | 4.93 | 53.47% | 0 | 0% | 9.22 | 4.92 | 53.36% | 0 | 0% | 9.22 | 4.92 | 53.36% | 0 | 0%
GNA_0121402_Capacity | Bay Area | Mission | LIVERMORE BANK 2 | 121402 | Bank | None | None | None | 86.89% | 0 | 0% | 11.82 | 10.27 | 86.89% | 0 | 0% | 11.82 | 10.23 | 86.55% | 0 | 0% | 11.82 | 10.17 | 86.04% | 0 | 0% | 11.82 | 10.13 | 85.7% | 0 | 0% | 11.82 | 10.12 | 85.62% | 0 | 0%
GNA_012141102_Capacity | Bay Area | Mission | LIVERMORE 1102 | 12141102 | Feeder | None | None | None | 38.84% | 0 | 0% | 9.45 | 3.67 | 38.84% | 0 | 0% | 9.45 | 3.65 | 38.62% | 0 | 0% | 9.45 | 3.64 | 38.52% | 0 | 0% | 9.45 | 3.61 | 38.2% | 0 | 0% | 9.45 | 3.61 | 38.2% | 0 | 0%
GNA_012141104_Capacity | Bay Area | Mission | LIVERMORE 1104 | 12141104 | Feeder | None | None | None | 58.82% | 0 | 0% | 12.19 | 7.17 | 58.82% | 0 | 0% | 12.19 | 7.13 | 58.49% | 0 | 0% | 12.19 | 7.08 | 58.08% | 0 | 0% | 12.19 | 7.06 | 57.92% | 0 | 0% | 12.19 | 7.04 | 57.75% | 0 | 0%
GNA_0131501_Capacity | Bay Area | Mission | RADUM BANK 1 | 131501 | Bank | None | None | None | 90.02% | 0 | 0% | 11.82 | 10.64 | 90.02% | 0 | 0% | 11.82 | 10.58 | 89.51% | 0 | 0% | 11.82 | 10.5 | 88.83% | 0 | 0% | 11.82 | 10.48 | 88.66% | 0 | 0% | 11.82 | 10.55 | 89.26% | 0 | 0%
GNA_013151101_Capacity | Bay Area | Mission | RADUM 1101 | 13151101 | Feeder | None | None | None | 64.68% | 0 | 0% | 10.76 | 6.96 | 64.68% | 0 | 0% | 10.76 | 6.92 | 64.31% | 0 | 0% | 10.76 | 6.87 | 63.85% | 0 | 0% | 10.76 | 6.86 | 63.75% | 0 | 0% | 10.76 | 6.92 | 64.31% | 0 | 0%
GNA_013151102_Capacity | Bay Area | Mission | RADUM 1102 | 13151102 | Feeder | None | None | None | 29.37% | 0 | 0% | 10.76 | 3.16 | 29.37% | 0 | 0% | 10.76 | 3.14 | 29.18% | 0 | 0% | 10.76 | 3.11 | 28.9% | 0 | 0% | 10.76 | 3.1 | 28.81% | 0 | 0% | 10.76 | 3.12 | 29% | 0 | 0%
GNA_0131502_Capacity | Bay Area | Mission | RADUM BANK 2 | 131502 | Bank | None | None | None | 82.49% | 0 | 0% | 11.82 | 9.75 | 82.49% | 0 | 0% | 11.82 | 9.69 | 81.98% | 0 | 0% | 11.82 | 9.62 | 81.39% | 0 | 0% | 11.82 | 9.62 | 81.39% | 0 | 0% | 11.82 | 9.64 | 81.56% | 0 | 0%
GNA_013151105_Capacity | Bay Area | Mission | RADUM 1105 | 13151105 | Feeder | None | None | None | 80.39% | 0 | 0% | 12.19 | 9.8 | 80.39% | 0 | 0% | 12.19 | 9.74 | 79.9% | 0 | 0% | 12.19 | 9.66 | 79.25% | 0 | 0% | 12.19 | 9.66 | 79.25% | 0 | 0% | 12.19 | 9.69 | 79.49% | 0 | 0%
GNA_0142401_Capacity | Bay Area | Mission | SUNOL BANK 1 | 142401 | Bank | None | None | None | 68.61% | 0 | 0% | 12.36 | 8.48 | 68.61% | 0 | 0% | 12.36 | 8.46 | 68.45% | 0 | 0% | 12.36 | 8.45 | 68.37% | 0 | 0% | 12.36 | 8.45 | 68.37% | 0 | 0% | 12.36 | 8.44 | 68.28% | 0 | 0%
GNA_014241101_Capacity | Bay Area | Mission | SUNOL 1101 | 14241101 | Feeder | None | None | None | 84.51% | 0 | 0% | 10.46 | 8.84 | 84.51% | 0 | 0% | 10.46 | 8.83 | 84.42% | 0 | 0% | 10.46 | 8.82 | 84.32% | 0 | 0% | 10.46 | 8.81 | 84.23% | 0 | 0% | 10.46 | 8.81 | 84.23% | 0 | 0%
GNA_0137501_Capacity | Bay Area | Mission | VASCO BANK 1 | 137501 | Bank | None | None | None | 96.54% | 0 | 0% | 8.1 | 7.45 | 91.98% | 0 | 0% | 8.1 | 7.52 | 92.84% | 0 | 0% | 8.1 | 7.59 | 93.7% | 0 | 0% | 8.1 | 7.69 | 94.94% | 0 | 0% | 8.1 | 7.82 | 96.54% | 0 | 0%
GNA_013751102_Capacity | Bay Area | Mission | VASCO 1102 | 13751102 | Feeder | None | None | None | 70.56% | 0 | 0% | 11.55 | 7.79 | 67.45% | 0 | 0% | 11.55 | 7.85 | 67.97% | 0 | 0% | 11.55 | 7.92 | 68.57% | 0 | 0% | 11.55 | 8.02 | 69.44% | 0 | 0% | 11.55 | 8.15 | 70.56% | 0 | 0%
GNA_0137502_Capacity | Bay Area | Mission | VASCO BANK 2 | 137502 | Bank | None | None | None | 77.5% | 0 | 0% | 8.8 | 6.82 | 77.5% | 0 | 0% | 8.8 | 6.8 | 77.27% | 0 | 0% | 8.8 | 6.77 | 76.93% | 0 | 0% | 8.8 | 6.75 | 76.7% | 0 | 0% | 8.8 | 6.75 | 76.7% | 0 | 0%
GNA_013751101_Capacity | Bay Area | Mission | VASCO 1101 | 13751101 | Feeder | None | None | None | 60.43% | 0 | 0% | 10.69 | 6.46 | 60.43% | 0 | 0% | 10.69 | 6.44 | 60.24% | 0 | 0% | 10.69 | 6.41 | 59.96% | 0 | 0% | 10.69 | 6.39 | 59.78% | 0 | 0% | 10.69 | 6.38 | 59.68% | 0 | 0%
GNA_013751103_Capacity | Bay Area | Mission | VASCO 1103 | 13751103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0432501_Capacity | North Valley and Sierra | North Bay | BAHIA BANK 1 | 432501 | Bank | None | None | None | 54.4% | 0 | 0% | 55.4 | 28.01 | 50.56% | 0 | 0% | 55.4 | 28.33 | 51.14% | 0 | 0% | 55.4 | 28.72 | 51.84% | 0 | 0% | 55.4 | 29.38 | 53.03% | 0 | 0% | 55.4 | 30.14 | 54.4% | 0 | 0%
GNA_043251101_Capacity | North Valley and Sierra | North Bay | BAHIA 1101 | 43251101 | Feeder | None | None | None | 100.3% | 0.04 | 0.3037% | 13.17 | 12.36 | 93.85% | 0 | 0% | 13.17 | 12.46 | 94.61% | 0 | 0% | 13.17 | 12.59 | 95.6% | 0 | 0% | 13.17 | 12.84 | 97.49% | 0 | 0% | 13.17 | 13.21 | 100.3% | 0.04 | 0.3037%
GNA_043251104_Capacity | North Valley and Sierra | North Bay | BAHIA 1104 | 43251104 | Feeder | None | None | None | 72.26% | 0 | 0% | 11.57 | 7.56 | 65.34% | 0 | 0% | 11.57 | 7.69 | 66.46% | 0 | 0% | 11.57 | 7.85 | 67.85% | 0 | 0% | 11.57 | 8.13 | 70.27% | 0 | 0% | 11.57 | 8.36 | 72.26% | 0 | 0%
GNA_043251105_Capacity | North Valley and Sierra | North Bay | BAHIA 1105 | 43251105 | Feeder | None | None | None | 83.41% | 0 | 0% | 11.57 | 9.13 | 78.91% | 0 | 0% | 11.57 | 9.24 | 79.86% | 0 | 0% | 11.57 | 9.34 | 80.73% | 0 | 0% | 11.57 | 9.48 | 81.94% | 0 | 0% | 11.57 | 9.65 | 83.41% | 0 | 0%
GNA_0432502_Capacity | North Valley and Sierra | North Bay | BAHIA BANK 2 | 432502 | Bank | None | None | None | 32.18% | 0 | 0% | 55.4 | 17.79 | 32.11% | 0 | 0% | 55.4 | 17.76 | 32.06% | 0 | 0% | 55.4 | 17.75 | 32.04% | 0 | 0% | 55.4 | 17.75 | 32.04% | 0 | 0% | 55.4 | 17.83 | 32.18% | 0 | 0%
GNA_043251102_Capacity | North Valley and Sierra | North Bay | BAHIA 1102 | 43251102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043251103_Capacity | North Valley and Sierra | North Bay | BAHIA 1103 | 43251103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0429901_Capacity | North Valley and Sierra | North Bay | LAS GALLINAS A BANK 1 | 429901 | Bank | None | None | None | 76.08% | 0 | 0% | 15.8 | 11.89 | 75.25% | 0 | 0% | 15.8 | 11.81 | 74.75% | 0 | 0% | 15.8 | 11.8 | 74.68% | 0 | 0% | 15.8 | 11.9 | 75.32% | 0 | 0% | 15.8 | 12.02 | 76.08% | 0 | 0%
GNA_042991103_Capacity | North Valley and Sierra | North Bay | LAS GALLINAS A 1103 | 42991103 | Feeder | None | None | None | 40.11% | 0 | 0% | 12.19 | 4.89 | 40.11% | 0 | 0% | 12.19 | 4.86 | 39.87% | 0 | 0% | 12.19 | 4.82 | 39.54% | 0 | 0% | 12.19 | 4.85 | 39.79% | 0 | 0% | 12.19 | 4.85 | 39.79% | 0 | 0%
GNA_042991104_Capacity | North Valley and Sierra | North Bay | LAS GALLINAS A 1104 | 42991104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0429902_Capacity | North Valley and Sierra | North Bay | LAS GALLINAS A BANK 2 | 429902 | Bank | None | None | None | 51.25% | 0 | 0% | 29.7 | 13.72 | 46.2% | 0 | 0% | 29.7 | 14.02 | 47.21% | 0 | 0% | 29.7 | 14.25 | 47.98% | 0 | 0% | 29.7 | 14.71 | 49.53% | 0 | 0% | 29.7 | 15.22 | 51.25% | 0 | 0%
GNA_042991105_Capacity | North Valley and Sierra | North Bay | LAS GALLINAS A 1105 | 42991105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042991106_Capacity | North Valley and Sierra | North Bay | LAS GALLINAS A 1106 | 42991106 | Feeder | None | None | None | 74.76% | 0 | 0% | 11.57 | 7.97 | 68.89% | 0 | 0% | 11.57 | 8.11 | 70.1% | 0 | 0% | 11.57 | 8.22 | 71.05% | 0 | 0% | 11.57 | 8.43 | 72.86% | 0 | 0% | 11.57 | 8.65 | 74.76% | 0 | 0%
GNA_0429903_Capacity | North Valley and Sierra | North Bay | LAS GALLINAS A BANK 3 | 429903 | Bank | None | None | None | 29.66% | 0 | 0% | 29.7 | 8.81 | 29.66% | 0 | 0% | 29.7 | 8.71 | 29.33% | 0 | 0% | 29.7 | 8.67 | 29.19% | 0 | 0% | 29.7 | 8.68 | 29.23% | 0 | 0% | 29.7 | 8.7 | 29.29% | 0 | 0%
GNA_042991107_Capacity | North Valley and Sierra | North Bay | LAS GALLINAS A 1107 | 42991107 | Feeder | None | None | None | 97.62% | 0 | 0% | 12.19 | 11.9 | 97.62% | 0 | 0% | 12.19 | 11.8 | 96.8% | 0 | 0% | 12.19 | 11.72 | 96.14% | 0 | 0% | 12.19 | 11.73 | 96.23% | 0 | 0% | 12.19 | 11.75 | 96.39% | 0 | 0%
GNA_0420101_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL BANK 1 | 420101 | Bank | None | None | None | 55.54% | 0 | 0% | 44.6 | 23.83 | 53.43% | 0 | 0% | 44.6 | 23.93 | 53.65% | 0 | 0% | 44.6 | 24 | 53.81% | 0 | 0% | 44.6 | 24.29 | 54.46% | 0 | 0% | 44.6 | 24.77 | 55.54% | 0 | 0%
GNA_042011103_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL 1103 | 42011103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042011104_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL 1104 | 42011104 | Feeder | None | None | None | 79.6% | 0 | 0% | 11.57 | 8.3 | 71.74% | 0 | 0% | 11.57 | 8.5 | 73.47% | 0 | 0% | 11.57 | 8.67 | 74.94% | 0 | 0% | 11.57 | 8.96 | 77.44% | 0 | 0% | 11.57 | 9.21 | 79.6% | 0 | 0%
GNA_042011106_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL 1106 | 42011106 | Feeder | None | None | None | 88.07% | 0 | 0% | 11.65 | 9.97 | 85.58% | 0 | 0% | 11.65 | 9.94 | 85.32% | 0 | 0% | 11.65 | 9.96 | 85.49% | 0 | 0% | 11.65 | 10.05 | 86.27% | 0 | 0% | 11.65 | 10.26 | 88.07% | 0 | 0%
GNA_0420102_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL BANK 2 | 420102 | Bank | None | None | None | 47.33% | 0 | 0% | 44.6 | 19.32 | 43.32% | 0 | 0% | 44.6 | 19.67 | 44.1% | 0 | 0% | 44.6 | 20 | 44.84% | 0 | 0% | 44.6 | 20.48 | 45.92% | 0 | 0% | 44.6 | 21.11 | 47.33% | 0 | 0%
GNA_042011102_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL 1102 | 42011102 | Feeder | None | None | None | 66.98% | 0 | 0% | 11.57 | 7.25 | 62.66% | 0 | 0% | 11.57 | 7.36 | 63.61% | 0 | 0% | 11.57 | 7.47 | 64.56% | 0 | 0% | 11.57 | 7.61 | 65.77% | 0 | 0% | 11.57 | 7.75 | 66.98% | 0 | 0%
GNA_042011107_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL 1107 | 42011107 | Feeder | None | None | None | 93.89% | 0 | 0% | 10.63 | 9.34 | 87.86% | 0 | 0% | 10.63 | 9.45 | 88.9% | 0 | 0% | 10.63 | 9.54 | 89.75% | 0 | 0% | 10.63 | 9.72 | 91.44% | 0 | 0% | 10.63 | 9.98 | 93.89% | 0 | 0%
GNA_042011108_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL 1108 | 42011108 | Feeder | None | None | None | 58.71% | 0 | 0% | 11.65 | 6.35 | 54.51% | 0 | 0% | 11.65 | 6.43 | 55.19% | 0 | 0% | 11.65 | 6.52 | 55.97% | 0 | 0% | 11.65 | 6.65 | 57.08% | 0 | 0% | 11.65 | 6.84 | 58.71% | 0 | 0%
GNA_0420103_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL BANK 3 | 420103 | Bank | None | None | None | 64.8% | 0 | 0% | 44.55 | 28.21 | 63.32% | 0 | 0% | 44.55 | 27.87 | 62.56% | 0 | 0% | 44.55 | 27.82 | 62.45% | 0 | 0% | 44.55 | 28.31 | 63.55% | 0 | 0% | 44.55 | 28.87 | 64.8% | 0 | 0%
GNA_042011101_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL 1101 | 42011101 | Feeder | None | None | None | 79.74% | 0 | 0% | 11.65 | 8.79 | 75.45% | 0 | 0% | 11.65 | 8.86 | 76.05% | 0 | 0% | 11.65 | 8.92 | 76.57% | 0 | 0% | 11.65 | 9.08 | 77.94% | 0 | 0% | 11.65 | 9.29 | 79.74% | 0 | 0%
GNA_042011105_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL 1105 | 42011105 | Feeder | None | None | None | 81.38% | 0 | 0% | 12.19 | 9.58 | 78.59% | 0 | 0% | 12.19 | 9.42 | 77.28% | 0 | 0% | 12.19 | 9.41 | 77.19% | 0 | 0% | 12.19 | 9.66 | 79.25% | 0 | 0% | 12.19 | 9.92 | 81.38% | 0 | 0%
GNA_042011109_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL 1109 | 42011109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042011110_Capacity | North Valley and Sierra | North Bay | SAN RAFAEL 1110 | 42011110 | Feeder | None | None | None | 55.87% | 0 | 0% | 12.19 | 6.81 | 55.87% | 0 | 0% | 12.19 | 6.75 | 55.37% | 0 | 0% | 12.19 | 6.7 | 54.96% | 0 | 0% | 12.19 | 6.72 | 55.13% | 0 | 0% | 12.19 | 6.76 | 55.46% | 0 | 0%
GNA_0430201_Capacity | North Valley and Sierra | North Bay | WOODACRE BANK 1 | 430201 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043021101_Capacity | North Valley and Sierra | North Bay | WOODACRE 1101 | 43021101 | Feeder | None | None | None | 21.19% | 0 | 0% | 11.8 | 2.35 | 19.92% | 0 | 0% | 11.8 | 2.38 | 20.17% | 0 | 0% | 11.8 | 2.41 | 20.42% | 0 | 0% | 11.8 | 2.45 | 20.76% | 0 | 0% | 11.8 | 2.5 | 21.19% | 0 | 0%
GNA_043021102_Capacity | North Valley and Sierra | North Bay | WOODACRE 1102 | 43021102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0422601_Capacity | North Valley and Sierra | North Bay | BOLINAS BANK 1 | 422601 | Bank | None | None | None | 23.56% | 0 | 0% | 10.4 | 2.45 | 23.56% | 0 | 0% | 10.4 | 2.44 | 23.46% | 0 | 0% | 10.4 | 2.43 | 23.37% | 0 | 0% | 10.4 | 2.43 | 23.37% | 0 | 0% | 10.4 | 2.4 | 23.08% | 0 | 0%
GNA_042261101_Capacity | North Valley and Sierra | North Bay | BOLINAS 1101 | 42261101 | Feeder | None | None | None | 22.73% | 0 | 0% | 10.69 | 2.43 | 22.73% | 0 | 0% | 10.69 | 2.42 | 22.64% | 0 | 0% | 10.69 | 2.41 | 22.54% | 0 | 0% | 10.69 | 2.4 | 22.45% | 0 | 0% | 10.69 | 2.37 | 22.17% | 0 | 0%
GNA_0422901_Capacity | North Valley and Sierra | North Bay | OLEMA BANK 1 | 422901 | Bank | None | None | None | 57.32% | 0 | 0% | 5.67 | 3.1 | 54.67% | 0 | 0% | 5.67 | 3.12 | 55.03% | 0 | 0% | 5.67 | 3.14 | 55.38% | 0 | 0% | 5.67 | 3.18 | 56.08% | 0 | 0% | 5.67 | 3.25 | 57.32% | 0 | 0%
GNA_042291101_Capacity | North Valley and Sierra | North Bay | OLEMA 1101 | 42291101 | Feeder | None | None | None | 38.25% | 0 | 0% | 8.55 | 3.12 | 36.49% | 0 | 0% | 8.55 | 3.14 | 36.73% | 0 | 0% | 8.55 | 3.16 | 36.96% | 0 | 0% | 8.55 | 3.2 | 37.43% | 0 | 0% | 8.55 | 3.27 | 38.25% | 0 | 0%
GNA_0424802_Capacity | North Valley and Sierra | North Bay | IGNACIO BANK 2 | 424802 | Bank | None | None | None | 96.5% | 0 | 0% | 29.7 | 28.66 | 96.5% | 0 | 0% | 29.7 | 28.1 | 94.61% | 0 | 0% | 29.7 | 27.43 | 92.36% | 0 | 0% | 29.7 | 26.92 | 90.64% | 0 | 0% | 29.7 | 26.73 | 90% | 0 | 0%
GNA_042481101_Capacity | North Valley and Sierra | North Bay | IGNACIO 1101 | 42481101 | Feeder | None | None | None | 71.27% | 0 | 0% | 11.8 | 8.41 | 71.27% | 0 | 0% | 11.8 | 8.27 | 70.08% | 0 | 0% | 11.8 | 8.1 | 68.64% | 0 | 0% | 11.8 | 8.04 | 68.14% | 0 | 0% | 11.8 | 8.05 | 68.22% | 0 | 0%
GNA_042481102_Capacity | North Valley and Sierra | North Bay | IGNACIO 1102 | 42481102 | Feeder | None | None | None | 77.2% | 0 | 0% | 11.8 | 9.11 | 77.2% | 0 | 0% | 11.8 | 9.06 | 76.78% | 0 | 0% | 11.8 | 9.01 | 76.36% | 0 | 0% | 11.8 | 9 | 76.27% | 0 | 0% | 11.8 | 9.01 | 76.36% | 0 | 0%
GNA_042481105_Capacity | North Valley and Sierra | North Bay | IGNACIO 1105 | 42481105 | Feeder | None | None | None | 88.22% | 0 | 0% | 11.8 | 10.41 | 88.22% | 0 | 0% | 11.8 | 10.18 | 86.27% | 0 | 0% | 11.8 | 9.89 | 83.81% | 0 | 0% | 11.8 | 9.59 | 81.27% | 0 | 0% | 11.8 | 9.42 | 79.83% | 0 | 0%
GNA_0424805_Capacity | North Valley and Sierra | North Bay | IGNACIO BANK 5 | 424805 | Bank | None | None | None | 96.28% | 0 | 0% | 15.84 | 14.93 | 94.26% | 0 | 0% | 15.84 | 14.96 | 94.44% | 0 | 0% | 15.84 | 15.01 | 94.76% | 0 | 0% | 15.84 | 15.11 | 95.39% | 0 | 0% | 15.84 | 15.25 | 96.28% | 0 | 0%
GNA_042481103_Capacity | North Valley and Sierra | North Bay | IGNACIO 1103 | 42481103 | Feeder | None | None | None | 90.48% | 0 | 0% | 12.19 | 10.67 | 87.53% | 0 | 0% | 12.19 | 10.72 | 87.94% | 0 | 0% | 12.19 | 10.79 | 88.52% | 0 | 0% | 12.19 | 10.9 | 89.42% | 0 | 0% | 12.19 | 11.03 | 90.48% | 0 | 0%
GNA_042481104_Capacity | North Valley and Sierra | North Bay | IGNACIO 1104 | 42481104 | Feeder | None | None | None | 35.7% | 0 | 0% | 12.83 | 4.58 | 35.7% | 0 | 0% | 12.83 | 4.55 | 35.46% | 0 | 0% | 12.83 | 4.54 | 35.39% | 0 | 0% | 12.83 | 4.53 | 35.31% | 0 | 0% | 12.83 | 4.53 | 35.31% | 0 | 0%
GNA_0422101_Capacity | North Valley and Sierra | North Bay | NOVATO BANK 1 | 422101 | Bank | None | None | None | 98.79% | 0 | 0% | 6.6 | 6.52 | 98.79% | 0 | 0% | 6.6 | 6.46 | 97.88% | 0 | 0% | 6.6 | 6.4 | 96.97% | 0 | 0% | 6.6 | 6.38 | 96.67% | 0 | 0% | 6.6 | 6.38 | 96.67% | 0 | 0%
GNA_042211101_Capacity | North Valley and Sierra | North Bay | NOVATO 1101 | 42211101 | Feeder | None | None | None | 29.52% | 0 | 0% | 8.13 | 2.4 | 29.52% | 0 | 0% | 8.13 | 2.36 | 29.03% | 0 | 0% | 8.13 | 2.31 | 28.41% | 0 | 0% | 8.13 | 2.29 | 28.17% | 0 | 0% | 8.13 | 2.29 | 28.17% | 0 | 0%
GNA_042211102_Capacity | North Valley and Sierra | North Bay | NOVATO 1102 | 42211102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0422102_Capacity | North Valley and Sierra | North Bay | NOVATO BANK 2 | 422102 | Bank | Demand Growth | Capacity | 2023 | 115.8% | 2.51 | 15.85% | 15.84 | 18.1 | 114.3% | 2.26 | 14.27% | 15.84 | 18.06 | 114% | 2.22 | 14.02% | 15.84 | 18.07 | 114.1% | 2.23 | 14.08% | 15.84 | 18.2 | 114.9% | 2.36 | 14.9% | 15.84 | 18.35 | 115.8% | 2.51 | 15.85%
GNA_042211103_Capacity | North Valley and Sierra | North Bay | NOVATO 1103 | 42211103 | Feeder | None | None | None | 83.9% | 0 | 0% | 11.8 | 9.9 | 83.9% | 0 | 0% | 11.8 | 9.88 | 83.73% | 0 | 0% | 11.8 | 9.87 | 83.64% | 0 | 0% | 11.8 | 9.86 | 83.56% | 0 | 0% | 11.8 | 9.87 | 83.64% | 0 | 0%
GNA_042211104_Capacity | North Valley and Sierra | North Bay | NOVATO 1104 | 42211104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0432001_Capacity | North Valley and Sierra | North Bay | STAFFORD BANK 1 | 432001 | Bank | None | None | None | 89.58% | 0 | 0% | 12.38 | 11.09 | 89.58% | 0 | 0% | 12.38 | 10.92 | 88.21% | 0 | 0% | 12.38 | 10.78 | 87.08% | 0 | 0% | 12.38 | 10.75 | 86.83% | 0 | 0% | 12.38 | 10.74 | 86.75% | 0 | 0%
GNA_043201101_Capacity | North Valley and Sierra | North Bay | STAFFORD 1101 | 43201101 | Feeder | None | None | None | 92.31% | 0 | 0% | 12.23 | 11.29 | 92.31% | 0 | 0% | 12.23 | 11.11 | 90.84% | 0 | 0% | 12.23 | 10.98 | 89.78% | 0 | 0% | 12.23 | 10.95 | 89.53% | 0 | 0% | 12.23 | 10.94 | 89.45% | 0 | 0%
GNA_0432002_Capacity | North Valley and Sierra | North Bay | STAFFORD BANK 2 | 432002 | Bank | None | None | None | 76.9% | 0 | 0% | 12.38 | 9.52 | 76.9% | 0 | 0% | 12.38 | 9.39 | 75.85% | 0 | 0% | 12.38 | 9.28 | 74.96% | 0 | 0% | 12.38 | 9.29 | 75.04% | 0 | 0% | 12.38 | 9.39 | 75.85% | 0 | 0%
GNA_043201102_Capacity | North Valley and Sierra | North Bay | STAFFORD 1102 | 43201102 | Feeder | None | None | None | 80.7% | 0 | 0% | 12.23 | 9.87 | 80.7% | 0 | 0% | 12.23 | 9.74 | 79.64% | 0 | 0% | 12.23 | 9.63 | 78.74% | 0 | 0% | 12.23 | 9.62 | 78.66% | 0 | 0% | 12.23 | 9.73 | 79.56% | 0 | 0%
GNA_0420301_Capacity | North Valley and Sierra | North Bay | ALTO BANK 1 | 420301 | Bank | None | None | None | 96.14% | 0 | 0% | 17.63 | 15.45 | 87.63% | 0 | 0% | 17.63 | 15.7 | 89.05% | 0 | 0% | 17.63 | 15.94 | 90.41% | 0 | 0% | 17.63 | 16.42 | 93.14% | 0 | 0% | 17.63 | 16.95 | 96.14% | 0 | 0%
GNA_042031122_Capacity | North Valley and Sierra | North Bay | ALTO 1122 | 42031122 | Feeder | None | None | None | 71.85% | 0 | 0% | 9.52 | 6.68 | 70.17% | 0 | 0% | 9.52 | 6.68 | 70.17% | 0 | 0% | 9.52 | 6.69 | 70.27% | 0 | 0% | 9.52 | 6.77 | 71.11% | 0 | 0% | 9.52 | 6.84 | 71.85% | 0 | 0%
GNA_042031123_Capacity | North Valley and Sierra | North Bay | ALTO 1123 | 42031123 | Feeder | None | None | None | 46.32% | 0 | 0% | 9.52 | 3.82 | 40.13% | 0 | 0% | 9.52 | 3.95 | 41.49% | 0 | 0% | 9.52 | 4.07 | 42.75% | 0 | 0% | 9.52 | 4.23 | 44.43% | 0 | 0% | 9.52 | 4.41 | 46.32% | 0 | 0%
GNA_042031124_Capacity | North Valley and Sierra | North Bay | ALTO 1124 | 42031124 | Feeder | None | None | None | 66.07% | 0 | 0% | 9.52 | 5.67 | 59.56% | 0 | 0% | 9.52 | 5.76 | 60.5% | 0 | 0% | 9.52 | 5.84 | 61.34% | 0 | 0% | 9.52 | 6.05 | 63.55% | 0 | 0% | 9.52 | 6.29 | 66.07% | 0 | 0%
GNA_0420303_Capacity | North Valley and Sierra | North Bay | ALTO BANK 3 | 420303 | Bank | None | None | None | 73.36% | 0 | 0% | 29.69 | 20.51 | 69.08% | 0 | 0% | 29.69 | 20.7 | 69.72% | 0 | 0% | 29.69 | 20.86 | 70.26% | 0 | 0% | 29.69 | 21.23 | 71.51% | 0 | 0% | 29.69 | 21.78 | 73.36% | 0 | 0%
GNA_042031120_Capacity | North Valley and Sierra | North Bay | ALTO 1120 | 42031120 | Feeder | None | None | None | 63.22% | 0 | 0% | 11.8 | 6.95 | 58.9% | 0 | 0% | 11.8 | 7.02 | 59.49% | 0 | 0% | 11.8 | 7.07 | 59.92% | 0 | 0% | 11.8 | 7.21 | 61.1% | 0 | 0% | 11.8 | 7.46 | 63.22% | 0 | 0%
GNA_042031121_Capacity | North Valley and Sierra | North Bay | ALTO 1121 | 42031121 | Feeder | None | None | None | 87.92% | 0 | 0% | 9.52 | 8.26 | 86.76% | 0 | 0% | 9.52 | 8.28 | 86.97% | 0 | 0% | 9.52 | 8.29 | 87.08% | 0 | 0% | 9.52 | 8.34 | 87.61% | 0 | 0% | 9.52 | 8.37 | 87.92% | 0 | 0%
GNA_042031125_Capacity | North Valley and Sierra | North Bay | ALTO 1125 | 42031125 | Feeder | None | None | None | 66.74% | 0 | 0% | 8.81 | 5.24 | 59.48% | 0 | 0% | 8.81 | 5.33 | 60.5% | 0 | 0% | 8.81 | 5.43 | 61.63% | 0 | 0% | 8.81 | 5.62 | 63.79% | 0 | 0% | 8.81 | 5.88 | 66.74% | 0 | 0%
GNA_0430901_Capacity | North Valley and Sierra | North Bay | GREENBRAE BANK 1 | 430901 | Bank | None | None | None | 84.34% | 0 | 0% | 15.84 | 13.19 | 83.27% | 0 | 0% | 15.84 | 13.16 | 83.08% | 0 | 0% | 15.84 | 13.09 | 82.64% | 0 | 0% | 15.84 | 13.14 | 82.95% | 0 | 0% | 15.84 | 13.36 | 84.34% | 0 | 0%
GNA_043091101_Capacity | North Valley and Sierra | North Bay | GREENBRAE 1101 | 43091101 | Feeder | None | None | None | 44.24% | 0 | 0% | 11.8 | 5.22 | 44.24% | 0 | 0% | 11.8 | 5.21 | 44.15% | 0 | 0% | 11.8 | 5.19 | 43.98% | 0 | 0% | 11.8 | 5.18 | 43.9% | 0 | 0% | 11.8 | 5.17 | 43.81% | 0 | 0%
GNA_043091102_Capacity | North Valley and Sierra | North Bay | GREENBRAE 1102 | 43091102 | Feeder | None | None | None | 91.69% | 0 | 0% | 11.8 | 10.17 | 86.19% | 0 | 0% | 11.8 | 10.3 | 87.29% | 0 | 0% | 11.8 | 10.4 | 88.14% | 0 | 0% | 11.8 | 10.53 | 89.24% | 0 | 0% | 11.8 | 10.82 | 91.69% | 0 | 0%
GNA_0430902_Capacity | North Valley and Sierra | North Bay | GREENBRAE BANK 2 | 430902 | Bank | None | None | None | 84.97% | 0 | 0% | 15.84 | 12.74 | 80.43% | 0 | 0% | 15.84 | 12.92 | 81.57% | 0 | 0% | 15.84 | 13.05 | 82.39% | 0 | 0% | 15.84 | 13.24 | 83.59% | 0 | 0% | 15.84 | 13.46 | 84.97% | 0 | 0%
GNA_043091103_Capacity | North Valley and Sierra | North Bay | GREENBRAE 1103 | 43091103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043091104_Capacity | North Valley and Sierra | North Bay | GREENBRAE 1104 | 43091104 | Feeder | None | None | None | 87.37% | 0 | 0% | 11.8 | 9.77 | 82.8% | 0 | 0% | 11.8 | 9.91 | 83.98% | 0 | 0% | 11.8 | 10.03 | 85% | 0 | 0% | 11.8 | 10.16 | 86.1% | 0 | 0% | 11.8 | 10.31 | 87.37% | 0 | 0%
GNA_0424901_Capacity | North Valley and Sierra | North Bay | SAUSALITO BANK 1 | 424901 | Bank | None | None | None | 27.66% | 0 | 0% | 4.23 | 0.99 | 23.4% | 0 | 0% | 4.23 | 1.04 | 24.59% | 0 | 0% | 4.23 | 1.06 | 25.06% | 0 | 0% | 4.23 | 1.12 | 26.48% | 0 | 0% | 4.23 | 1.17 | 27.66% | 0 | 0%
GNA_042490401_Capacity | North Valley and Sierra | North Bay | SAUSALITO 0401 | 42490401 | Feeder | None | None | None | 30.54% | 0 | 0% | 2.03 | 0.55 | 27.09% | 0 | 0% | 2.03 | 0.56 | 27.59% | 0 | 0% | 2.03 | 0.57 | 28.08% | 0 | 0% | 2.03 | 0.59 | 29.06% | 0 | 0% | 2.03 | 0.62 | 30.54% | 0 | 0%
GNA_042490402_Capacity | North Valley and Sierra | North Bay | SAUSALITO 0402 | 42490402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0424902_Capacity | North Valley and Sierra | North Bay | SAUSALITO BANK 2 | 424902 | Bank | None | None | None | 67.24% | 0 | 0% | 14.99 | 9.27 | 61.84% | 0 | 0% | 14.99 | 9.41 | 62.78% | 0 | 0% | 14.99 | 9.53 | 63.58% | 0 | 0% | 14.99 | 9.75 | 65.04% | 0 | 0% | 14.99 | 10.08 | 67.24% | 0 | 0%
GNA_042491101_Capacity | North Valley and Sierra | North Bay | SAUSALITO 1101 | 42491101 | Feeder | None | None | None | 31.36% | 0 | 0% | 11.8 | 3.67 | 31.1% | 0 | 0% | 11.8 | 3.64 | 30.85% | 0 | 0% | 11.8 | 3.58 | 30.34% | 0 | 0% | 11.8 | 3.62 | 30.68% | 0 | 0% | 11.8 | 3.7 | 31.36% | 0 | 0%
GNA_042491102_Capacity | North Valley and Sierra | North Bay | SAUSALITO 1102 | 42491102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0430501_Capacity | North Valley and Sierra | North Bay | MONTICELLO BANK 1 | 430501 | Bank | None | None | None | 79.59% | 0 | 0% | 6.91 | 4.88 | 70.62% | 0 | 0% | 6.91 | 4.98 | 72.07% | 0 | 0% | 6.91 | 5.06 | 73.23% | 0 | 0% | 6.91 | 5.25 | 75.98% | 0 | 0% | 6.91 | 5.5 | 79.59% | 0 | 0%
GNA_043051101_Capacity | North Valley and Sierra | North Bay | MONTICELLO 1101 | 43051101 | Feeder | None | None | None | 80% | 0 | 0% | 7.85 | 5.65 | 71.97% | 0 | 0% | 7.85 | 5.75 | 73.25% | 0 | 0% | 7.85 | 5.84 | 74.39% | 0 | 0% | 7.85 | 6.03 | 76.82% | 0 | 0% | 7.85 | 6.28 | 80% | 0 | 0%
GNA_0424601_Capacity | North Valley and Sierra | North Bay | BASALT BANK 1 | 424601 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042461101_Capacity | North Valley and Sierra | North Bay | BASALT 1101 | 42461101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0424602_Capacity | North Valley and Sierra | North Bay | BASALT BANK 2 | 424602 | Bank | None | None | None | 98.86% | 0 | 0% | 29.7 | 23.02 | 77.51% | 0 | 0% | 29.7 | 29.04 | 97.78% | 0 | 0% | 29.7 | 29.1 | 97.98% | 0 | 0% | 29.7 | 29.2 | 98.32% | 0 | 0% | 29.7 | 29.36 | 98.86% | 0 | 0%
GNA_042461105_Capacity | North Valley and Sierra | North Bay | BASALT 1105 | 42461105 | Feeder | Demand Growth | Capacity | 2026 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042461106_Capacity | North Valley and Sierra | North Bay | BASALT 1106 | 42461106 | Feeder | Demand Growth | Capacity | 2023 | 151% | 6.03 | 51.02% | 11.82 | 14.87 | 125.8% | 3.05 | 25.8% | 11.82 | 17.85 | 151% | 6.03 | 51.02% | 11.82 | 17.81 | 150.7% | 5.99 | 50.68% | 11.82 | 17.78 | 150.4% | 5.96 | 50.42% | 11.82 | 17.84 | 150.9% | 6.02 | 50.93%
GNA_0420201_Capacity | North Valley and Sierra | North Bay | NAPA BANK 1 | 420201 | Bank | None | None | None | 68.74% | 0 | 0% | 29.69 | 20.41 | 68.74% | 0 | 0% | 29.69 | 17.1 | 57.6% | 0 | 0% | 29.69 | 17.02 | 57.33% | 0 | 0% | 29.69 | 16.98 | 57.19% | 0 | 0% | 29.69 | 17.12 | 57.66% | 0 | 0%
GNA_042021102_Capacity | North Valley and Sierra | North Bay | NAPA 1102 | 42021102 | Feeder | None | None | None | 72.1% | 0 | 0% | 12.83 | 9.25 | 72.1% | 0 | 0% | 12.83 | 9.07 | 70.69% | 0 | 0% | 12.83 | 8.88 | 69.21% | 0 | 0% | 12.83 | 8.71 | 67.89% | 0 | 0% | 12.83 | 8.65 | 67.42% | 0 | 0%
GNA_042021103_Capacity | North Valley and Sierra | North Bay | NAPA 1103 | 42021103 | Feeder | Demand Growth | Capacity | 2023 | 117.1% | 1.79 | 17.11% | 10.46 | 12.25 | 117.1% | 1.79 | 17.11% | 10.46 | 9.18 | 87.76% | 0 | 0% | 10.46 | 9.18 | 87.76% | 0 | 0% | 10.46 | 9.21 | 88.05% | 0 | 0% | 10.46 | 9.28 | 88.72% | 0 | 0%
GNA_0420202_Capacity | North Valley and Sierra | North Bay | NAPA BANK 2 | 420202 | Bank | None | None | None | 95.59% | 0 | 0% | 18.6 | 17.78 | 95.59% | 0 | 0% | 18.6 | 17.68 | 95.05% | 0 | 0% | 18.6 | 17.55 | 94.35% | 0 | 0% | 18.6 | 17.51 | 94.14% | 0 | 0% | 18.6 | 17.47 | 93.92% | 0 | 0%
GNA_042021105_Capacity | North Valley and Sierra | North Bay | NAPA 1105 | 42021105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042021106_Capacity | North Valley and Sierra | North Bay | NAPA 1106 | 42021106 | Feeder | None | None | None | 79.92% | 0 | 0% | 10.61 | 8.48 | 79.92% | 0 | 0% | 10.61 | 8.48 | 79.92% | 0 | 0% | 10.61 | 8.45 | 79.64% | 0 | 0% | 10.61 | 8.45 | 79.64% | 0 | 0% | 10.61 | 8.44 | 79.55% | 0 | 0%
GNA_0420203_Capacity | North Valley and Sierra | North Bay | NAPA BANK 3 | 420203 | Bank | Demand Growth | Capacity | 2023 | 103.4% | 1.01 | 3.401% | 29.7 | 30.71 | 103.4% | 1.01 | 3.401% | 29.7 | 30.19 | 101.6% | 0.49 | 1.65% | 29.7 | 29.78 | 100.3% | 0.08 | 0.2694% | 29.7 | 29.78 | 100.3% | 0.08 | 0.2694% | 29.7 | 29.96 | 100.9% | 0.26 | 0.8754%
GNA_042021109_Capacity | North Valley and Sierra | North Bay | NAPA 1109 | 42021109 | Feeder | None | None | None | 89.89% | 0 | 0% | 12.36 | 11.11 | 89.89% | 0 | 0% | 12.36 | 11.02 | 89.16% | 0 | 0% | 12.36 | 10.88 | 88.03% | 0 | 0% | 12.36 | 10.81 | 87.46% | 0 | 0% | 12.36 | 10.75 | 86.97% | 0 | 0%
GNA_042021110_Capacity | North Valley and Sierra | North Bay | NAPA 1110 | 42021110 | Feeder | Demand Growth | Capacity | 2023 | 108.9% | 0.93 | 8.891% | 10.46 | 11.39 | 108.9% | 0.93 | 8.891% | 10.46 | 11.26 | 107.6% | 0.8 | 7.648% | 10.46 | 11.17 | 106.8% | 0.71 | 6.788% | 10.46 | 11.12 | 106.3% | 0.66 | 6.31% | 10.46 | 11.13 | 106.4% | 0.67 | 6.405%
GNA_042021112_Capacity | North Valley and Sierra | North Bay | NAPA 1112 | 42021112 | Feeder | None | None | None | 99.71% | 0 | 0% | 10.46 | 10.33 | 98.76% | 0 | 0% | 10.46 | 10.13 | 96.85% | 0 | 0% | 10.46 | 10.02 | 95.79% | 0 | 0% | 10.46 | 10.21 | 97.61% | 0 | 0% | 10.46 | 10.43 | 99.71% | 0 | 0%
GNA_0432901_Capacity | North Valley and Sierra | North Bay | PUEBLO BANK 1 | 432901 | Bank | Demand Growth | Capacity | 2023 | 124.2% | 10.78 | 24.22% | 44.5 | 51.89 | 116.6% | 7.39 | 16.61% | 44.5 | 53.94 | 121.2% | 9.44 | 21.21% | 44.5 | 54.11 | 121.6% | 9.61 | 21.6% | 44.5 | 54.6 | 122.7% | 10.1 | 22.7% | 44.5 | 55.28 | 124.2% | 10.78 | 24.22%
GNA_043292101_Capacity | North Valley and Sierra | North Bay | PUEBLO 2101 | 43292101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043292102_Capacity | North Valley and Sierra | North Bay | PUEBLO 2102 | 43292102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043292103_Capacity | North Valley and Sierra | North Bay | PUEBLO 2103 | 43292103 | Feeder | Demand Growth | Capacity | 2023 | 114.8% | 2.75 | 14.76% | 18.63 | 21.38 | 114.8% | 2.75 | 14.76% | 18.63 | 20.87 | 112% | 2.24 | 12.02% | 18.63 | 20.36 | 109.3% | 1.73 | 9.286% | 18.63 | 20.36 | 109.3% | 1.73 | 9.286% | 18.63 | 20.75 | 111.4% | 2.12 | 11.38%
GNA_0432902_Capacity | North Valley and Sierra | North Bay | PUEBLO BANK 2 | 432902 | Bank | None | None | None | 75.93% | 0 | 0% | 44.5 | 33.79 | 75.93% | 0 | 0% | 44.5 | 33.25 | 74.72% | 0 | 0% | 44.5 | 32.86 | 73.84% | 0 | 0% | 44.5 | 32.55 | 73.15% | 0 | 0% | 44.5 | 32.51 | 73.06% | 0 | 0%
GNA_043291102_Capacity | North Valley and Sierra | North Bay | PUEBLO 1102 | 43291102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043291103_Capacity | North Valley and Sierra | North Bay | PUEBLO 1103 | 43291103 | Feeder | None | None | None | 91.08% | 0 | 0% | 10.76 | 9.8 | 91.08% | 0 | 0% | 10.76 | 9.76 | 90.71% | 0 | 0% | 10.76 | 9.72 | 90.33% | 0 | 0% | 10.76 | 9.76 | 90.71% | 0 | 0% | 10.76 | 9.76 | 90.71% | 0 | 0%
GNA_043291104_Capacity | North Valley and Sierra | North Bay | PUEBLO 1104 | 43291104 | Feeder | None | None | None | 63.84% | 0 | 0% | 12.25 | 7.82 | 63.84% | 0 | 0% | 12.25 | 7.7 | 62.86% | 0 | 0% | 12.25 | 7.61 | 62.12% | 0 | 0% | 12.25 | 7.62 | 62.2% | 0 | 0% | 12.25 | 7.81 | 63.76% | 0 | 0%
GNA_043291105_Capacity | North Valley and Sierra | North Bay | PUEBLO 1105 | 43291105 | Feeder | None | None | None | 67.84% | 0 | 0% | 12.25 | 8.31 | 67.84% | 0 | 0% | 12.25 | 8.17 | 66.69% | 0 | 0% | 12.25 | 8.13 | 66.37% | 0 | 0% | 12.25 | 8.11 | 66.2% | 0 | 0% | 12.25 | 8.13 | 66.37% | 0 | 0%
GNA_0432903_Capacity | North Valley and Sierra | North Bay | PUEBLO BANK 3 | 432903 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043292104_Capacity | North Valley and Sierra | North Bay | PUEBLO 2104 | 43292104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0423002_Capacity | North Valley and Sierra | North Bay | TULUCAY BANK 2 | 423002 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042301101_Capacity | North Valley and Sierra | North Bay | TULUCAY 1101 | 42301101 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0427101_Capacity | North Valley and Sierra | North Bay | CALISTOGA BANK 1 | 427101 | Bank | Demand Growth | Capacity | 2025 | 103.3% | 0.66 | 3.333% | 19.8 | 17.5 | 88.38% | 0 | 0% | 19.8 | 17.66 | 89.19% | 0 | 0% | 19.8 | 19.97 | 100.9% | 0.17 | 0.8586% | 19.8 | 20.16 | 101.8% | 0.36 | 1.818% | 19.8 | 20.46 | 103.3% | 0.66 | 3.333%
GNA_042711101_Capacity | North Valley and Sierra | North Bay | CALISTOGA 1101 | 42711101 | Feeder | None | None | None | 58.07% | 0 | 0% | 12.83 | 6.94 | 54.09% | 0 | 0% | 12.83 | 7.05 | 54.95% | 0 | 0% | 12.83 | 7.16 | 55.81% | 0 | 0% | 12.83 | 7.29 | 56.82% | 0 | 0% | 12.83 | 7.45 | 58.07% | 0 | 0%
GNA_042711102_Capacity | North Valley and Sierra | North Bay | CALISTOGA 1102 | 42711102 | Feeder | Demand Growth | Capacity | 2023 | 123.5% | 3.02 | 23.54% | 12.83 | 13.35 | 104.1% | 0.52 | 4.053% | 12.83 | 13.41 | 104.5% | 0.58 | 4.521% | 12.83 | 15.63 | 121.8% | 2.8 | 21.82% | 12.83 | 15.7 | 122.4% | 2.87 | 22.37% | 12.83 | 15.85 | 123.5% | 3.02 | 23.54%
GNA_0434301_Capacity | North Valley and Sierra | North Bay | SILVERADO BANK 1 | 434301 | Bank | None | None | None | 93.06% | 0 | 0% | 29.7 | 26.68 | 89.83% | 0 | 0% | 29.7 | 27.07 | 91.14% | 0 | 0% | 29.7 | 27.21 | 91.62% | 0 | 0% | 29.7 | 27.41 | 92.29% | 0 | 0% | 29.7 | 27.64 | 93.06% | 0 | 0%
GNA_043432102_Capacity | North Valley and Sierra | North Bay | SILVERADO 2102 | 43432102 | Feeder | None | None | None | 52.82% | 0 | 0% | 21.11 | 10.61 | 50.26% | 0 | 0% | 21.11 | 10.92 | 51.73% | 0 | 0% | 21.11 | 10.97 | 51.97% | 0 | 0% | 21.11 | 11.05 | 52.34% | 0 | 0% | 21.11 | 11.15 | 52.82% | 0 | 0%
GNA_043432103_Capacity | North Valley and Sierra | North Bay | SILVERADO 2103 | 43432103 | Feeder | None | None | None | 98.39% | 0 | 0% | 18.63 | 18.04 | 96.83% | 0 | 0% | 18.63 | 18.08 | 97.05% | 0 | 0% | 18.63 | 18.12 | 97.26% | 0 | 0% | 18.63 | 18.21 | 97.75% | 0 | 0% | 18.63 | 18.33 | 98.39% | 0 | 0%
GNA_0434302_Capacity | North Valley and Sierra | North Bay | SILVERADO BANK 2 | 434302 | Bank | Demand Growth | Capacity | 2023 | 109.9% | 2.94 | 9.899% | 29.7 | 32.64 | 109.9% | 2.94 | 9.899% | 29.7 | 30.33 | 102.1% | 0.63 | 2.121% | 29.7 | 28.28 | 95.22% | 0 | 0% | 29.7 | 28.51 | 95.99% | 0 | 0% | 29.7 | 28.78 | 96.9% | 0 | 0%
GNA_043432104_Capacity | North Valley and Sierra | North Bay | SILVERADO 2104 | 43432104 | Feeder | None | None | None | 90.5% | 0 | 0% | 18.52 | 16.76 | 90.5% | 0 | 0% | 18.52 | 14.26 | 77% | 0 | 0% | 18.52 | 14.18 | 76.57% | 0 | 0% | 18.52 | 14.13 | 76.3% | 0 | 0% | 18.52 | 14.1 | 76.13% | 0 | 0%
GNA_043432105_Capacity | North Valley and Sierra | North Bay | SILVERADO 2105 | 43432105 | Feeder | None | None | None | 86.37% | 0 | 0% | 18.63 | 16.05 | 86.15% | 0 | 0% | 18.63 | 16.09 | 86.37% | 0 | 0% | 18.63 | 13.98 | 75.04% | 0 | 0% | 18.63 | 14.11 | 75.74% | 0 | 0% | 18.63 | 14.27 | 76.6% | 0 | 0%
GNA_0432801_Capacity | North Valley and Sierra | North Bay | CARQUINEZ BANK 1 | 432801 | Bank | None | None | None | 63.87% | 0 | 0% | 12.4 | 7.92 | 63.87% | 0 | 0% | 12.4 | 7.85 | 63.31% | 0 | 0% | 12.4 | 7.77 | 62.66% | 0 | 0% | 12.4 | 7.68 | 61.94% | 0 | 0% | 12.4 | 7.67 | 61.85% | 0 | 0%
GNA_043281103_Capacity | North Valley and Sierra | North Bay | CARQUINEZ 1103 | 43281103 | Feeder | None | None | None | 77.44% | 0 | 0% | 11.57 | 8.96 | 77.44% | 0 | 0% | 11.57 | 8.88 | 76.75% | 0 | 0% | 11.57 | 8.81 | 76.15% | 0 | 0% | 11.57 | 8.73 | 75.45% | 0 | 0% | 11.57 | 8.71 | 75.28% | 0 | 0%
GNA_043281104_Capacity | North Valley and Sierra | North Bay | CARQUINEZ 1104 | 43281104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0432802_Capacity | North Valley and Sierra | North Bay | CARQUINEZ BANK 2 | 432802 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043281105_Capacity | North Valley and Sierra | North Bay | CARQUINEZ 1105 | 43281105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0425501_Capacity | North Valley and Sierra | North Bay | VALLEJO C BANK 1 | 425501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042550401_Capacity | North Valley and Sierra | North Bay | VALLEJO C 0401 | 42550401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0426501_Capacity | North Valley and Sierra | North Bay | HIGHWAY BANK 1 | 426501 | Bank | None | None | None | 72.85% | 0 | 0% | 44.53 | 31.73 | 71.26% | 0 | 0% | 44.53 | 31.96 | 71.77% | 0 | 0% | 44.53 | 32.21 | 72.33% | 0 | 0% | 44.53 | 32.38 | 72.72% | 0 | 0% | 44.53 | 32.44 | 72.85% | 0 | 0%
GNA_042651102_Capacity | North Valley and Sierra | North Bay | HIGHWAY 1102 | 42651102 | Feeder | Demand Growth | Capacity | 2023 | 149.1% | 6.01 | 49.14% | 12.23 | 16.49 | 134.8% | 4.26 | 34.83% | 12.23 | 17.12 | 140% | 4.89 | 39.98% | 12.23 | 17.77 | 145.3% | 5.54 | 45.3% | 12.23 | 18.1 | 148% | 5.87 | 48% | 12.23 | 18.24 | 149.1% | 6.01 | 49.14%
GNA_042651104_Capacity | North Valley and Sierra | North Bay | HIGHWAY 1104 | 42651104 | Feeder | None | None | None | 68.98% | 0 | 0% | 12.83 | 8.72 | 67.97% | 0 | 0% | 12.83 | 8.57 | 66.8% | 0 | 0% | 12.83 | 8.53 | 66.48% | 0 | 0% | 12.83 | 8.65 | 67.42% | 0 | 0% | 12.83 | 8.85 | 68.98% | 0 | 0%
GNA_042651106_Capacity | North Valley and Sierra | North Bay | HIGHWAY 1106 | 42651106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0426502_Capacity | North Valley and Sierra | North Bay | HIGHWAY BANK 2 | 426502 | Bank | None | None | None | 56.35% | 0 | 0% | 44.6 | 23.71 | 53.16% | 0 | 0% | 44.6 | 24.39 | 54.69% | 0 | 0% | 44.6 | 24.4 | 54.71% | 0 | 0% | 44.6 | 24.71 | 55.4% | 0 | 0% | 44.6 | 25.13 | 56.35% | 0 | 0%
GNA_042651101_Capacity | North Valley and Sierra | North Bay | HIGHWAY 1101 | 42651101 | Feeder | None | None | None | 99.38% | 0 | 0% | 12.83 | 11.54 | 89.95% | 0 | 0% | 12.83 | 12.31 | 95.95% | 0 | 0% | 12.83 | 12.3 | 95.87% | 0 | 0% | 12.83 | 12.48 | 97.27% | 0 | 0% | 12.83 | 12.75 | 99.38% | 0 | 0%
GNA_042651103_Capacity | North Valley and Sierra | North Bay | HIGHWAY 1103 | 42651103 | Feeder | None | None | None | 44.35% | 0 | 0% | 12.83 | 5.34 | 41.62% | 0 | 0% | 12.83 | 5.4 | 42.09% | 0 | 0% | 12.83 | 5.49 | 42.79% | 0 | 0% | 12.83 | 5.58 | 43.49% | 0 | 0% | 12.83 | 5.69 | 44.35% | 0 | 0%
GNA_042651105_Capacity | North Valley and Sierra | North Bay | HIGHWAY 1105 | 42651105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042651107_Capacity | North Valley and Sierra | North Bay | HIGHWAY 1107 | 42651107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0420401_Capacity | North Valley and Sierra | North Bay | NORTH TOWER BANK 1 | 420401 | Bank | None | None | None | 75.4% | 0 | 0% | 44.55 | 33.59 | 75.4% | 0 | 0% | 44.55 | 32.73 | 73.47% | 0 | 0% | 44.55 | 31.99 | 71.81% | 0 | 0% | 44.55 | 31.66 | 71.07% | 0 | 0% | 44.55 | 31.82 | 71.43% | 0 | 0%
GNA_042041102_Capacity | North Valley and Sierra | North Bay | NORTH TOWER 1102 | 42041102 | Feeder | None | None | None | 77.32% | 0 | 0% | 12.83 | 9.92 | 77.32% | 0 | 0% | 12.83 | 9.67 | 75.37% | 0 | 0% | 12.83 | 9.62 | 74.98% | 0 | 0% | 12.83 | 9.65 | 75.21% | 0 | 0% | 12.83 | 9.84 | 76.7% | 0 | 0%
GNA_042041103_Capacity | North Valley and Sierra | North Bay | NORTH TOWER 1103 | 42041103 | Feeder | None | None | None | 78.17% | 0 | 0% | 9.71 | 7.59 | 78.17% | 0 | 0% | 9.71 | 7.44 | 76.62% | 0 | 0% | 9.71 | 7.34 | 75.59% | 0 | 0% | 9.71 | 7.38 | 76% | 0 | 0% | 9.71 | 7.45 | 76.73% | 0 | 0%
GNA_042041104_Capacity | North Valley and Sierra | North Bay | NORTH TOWER 1104 | 42041104 | Feeder | None | None | None | 94.93% | 0 | 0% | 12.83 | 12.18 | 94.93% | 0 | 0% | 12.83 | 12 | 93.53% | 0 | 0% | 12.83 | 11.82 | 92.13% | 0 | 0% | 12.83 | 11.74 | 91.5% | 0 | 0% | 12.83 | 11.67 | 90.96% | 0 | 0%
GNA_0424504_Capacity | North Valley and Sierra | North Bay | VALLEJO B BANK 4 | 424504 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042451101_Capacity | North Valley and Sierra | North Bay | VALLEJO B 1101 | 42451101 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0420404_Capacity | North Valley and Sierra | North Bay | NORTH TOWER BANK 4 | 420404 | Bank | None | None | None | 44.73% | 0 | 0% | 44.53 | 19.92 | 44.73% | 0 | 0% | 44.53 | 19.3 | 43.34% | 0 | 0% | 44.53 | 19.03 | 42.74% | 0 | 0% | 44.53 | 19.11 | 42.91% | 0 | 0% | 44.53 | 19.32 | 43.39% | 0 | 0%
GNA_0420406_Capacity | North Valley and Sierra | North Bay | NORTH TOWER BANK 6 | 420406 | Bank | None | None | None | 44.95% | 0 | 0% | 15.84 | 7.12 | 44.95% | 0 | 0% | 15.84 | 6.85 | 43.24% | 0 | 0% | 15.84 | 6.77 | 42.74% | 0 | 0% | 15.84 | 6.8 | 42.93% | 0 | 0% | 15.84 | 6.92 | 43.69% | 0 | 0%
GNA_0424501_Capacity | North Valley and Sierra | North Bay | VALLEJO B BANK 1 | 424501 | Bank | None | None | None | 86.86% | 0 | 0% | 10.58 | 9.19 | 86.86% | 0 | 0% | 10.58 | 8.87 | 83.84% | 0 | 0% | 10.58 | 8.74 | 82.61% | 0 | 0% | 10.58 | 8.76 | 82.8% | 0 | 0% | 10.58 | 8.85 | 83.65% | 0 | 0%
GNA_042450411_Capacity | North Valley and Sierra | North Bay | VALLEJO B 0411 | 42450411 | Feeder | None | None | None | 72.9% | 0 | 0% | 3.69 | 2.69 | 72.9% | 0 | 0% | 3.69 | 2.63 | 71.27% | 0 | 0% | 3.69 | 2.59 | 70.19% | 0 | 0% | 3.69 | 2.57 | 69.65% | 0 | 0% | 3.69 | 2.58 | 69.92% | 0 | 0%
GNA_042450413_Capacity | North Valley and Sierra | North Bay | VALLEJO B 0413 | 42450413 | Feeder | None | None | None | 57.06% | 0 | 0% | 3.33 | 1.9 | 57.06% | 0 | 0% | 3.33 | 1.84 | 55.26% | 0 | 0% | 3.33 | 1.82 | 54.65% | 0 | 0% | 3.33 | 1.81 | 54.35% | 0 | 0% | 3.33 | 1.82 | 54.65% | 0 | 0%
GNA_042450414_Capacity | North Valley and Sierra | North Bay | VALLEJO B 0414 | 42450414 | Feeder | None | None | None | 71.34% | 0 | 0% | 3.21 | 2.29 | 71.34% | 0 | 0% | 3.21 | 2.21 | 68.85% | 0 | 0% | 3.21 | 2.18 | 67.91% | 0 | 0% | 3.21 | 2.2 | 68.54% | 0 | 0% | 3.21 | 2.25 | 70.09% | 0 | 0%
GNA_042450415_Capacity | North Valley and Sierra | North Bay | VALLEJO B 0415 | 42450415 | Feeder | None | None | None | 71.17% | 0 | 0% | 3.33 | 2.37 | 71.17% | 0 | 0% | 3.33 | 2.28 | 68.47% | 0 | 0% | 3.33 | 2.25 | 67.57% | 0 | 0% | 3.33 | 2.26 | 67.87% | 0 | 0% | 3.33 | 2.28 | 68.47% | 0 | 0%
GNA_0424505_Capacity | North Valley and Sierra | North Bay | VALLEJO B BANK 5 | 424505 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042451102_Capacity | North Valley and Sierra | North Bay | VALLEJO B 1102 | 42451102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042041108_Capacity | North Valley and Sierra | North Bay | NORTH TOWER 1108 (formerly 1101) | 42041108 | Feeder | None | None | None | 89.73% | 0 | 0% | 13.15 | 11.8 | 89.73% | 0 | 0% | 13.15 | 11.49 | 87.38% | 0 | 0% | 13.15 | 11.36 | 86.39% | 0 | 0% | 13.15 | 11.38 | 86.54% | 0 | 0% | 13.15 | 11.5 | 87.45% | 0 | 0%
GNA_0420501_Capacity | North Valley and Sierra | North Bay | PARKWAY BANK 1 | 420501 | Bank | None | None | None | 99.73% | 0 | 0% | 29.7 | 29.62 | 99.73% | 0 | 0% | 29.7 | 29.25 | 98.48% | 0 | 0% | 29.7 | 28.98 | 97.58% | 0 | 0% | 29.7 | 29.18 | 98.25% | 0 | 0% | 29.7 | 29.56 | 99.53% | 0 | 0%
GNA_042051101_Capacity | North Valley and Sierra | North Bay | PARKWAY 1101 | 42051101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042051102_Capacity | North Valley and Sierra | North Bay | PARKWAY 1102 | 42051102 | Feeder | None | None | None | 83.78% | 0 | 0% | 11.65 | 9.76 | 83.78% | 0 | 0% | 11.65 | 9.61 | 82.49% | 0 | 0% | 11.65 | 9.49 | 81.46% | 0 | 0% | 11.65 | 9.59 | 82.32% | 0 | 0% | 11.65 | 9.69 | 83.18% | 0 | 0%
GNA_042051103_Capacity | North Valley and Sierra | North Bay | PARKWAY 1103 | 42051103 | Feeder | None | None | None | 92.45% | 0 | 0% | 11.65 | 10.77 | 92.45% | 0 | 0% | 11.65 | 10.68 | 91.67% | 0 | 0% | 11.65 | 10.64 | 91.33% | 0 | 0% | 11.65 | 10.63 | 91.24% | 0 | 0% | 11.65 | 10.72 | 92.02% | 0 | 0%
GNA_1032701_Capacity | North Valley and Sierra | North Valley | ANTLER BANK 1 | 1032701 | Bank | None | None | None | 29.85% | 0 | 0% | 9.85 | 2.93 | 29.75% | 0 | 0% | 9.85 | 2.93 | 29.75% | 0 | 0% | 9.85 | 2.94 | 29.85% | 0 | 0% | 9.85 | 2.93 | 29.75% | 0 | 0% | 9.85 | 2.94 | 29.85% | 0 | 0%
GNA_103271101_Capacity | North Valley and Sierra | North Valley | ANTLER 1101 | 103271101 | Feeder | None | None | None | 56.07% | 0 | 0% | 5.35 | 3 | 56.07% | 0 | 0% | 5.35 | 3 | 56.07% | 0 | 0% | 5.35 | 3 | 56.07% | 0 | 0% | 5.35 | 3 | 56.07% | 0 | 0% | 5.35 | 3 | 56.07% | 0 | 0%
GNA_1022104_Capacity | North Valley and Sierra | North Valley | BUCKS CREEK BANK 4 | 1022104 | Bank | None | None | None | 31.91% | 0 | 0% | 2.82 | 0.9 | 31.91% | 0 | 0% | 2.82 | 0.89 | 31.56% | 0 | 0% | 2.82 | 0.89 | 31.56% | 0 | 0% | 2.82 | 0.89 | 31.56% | 0 | 0% | 2.82 | 0.89 | 31.56% | 0 | 0%
GNA_102211102_Capacity | North Valley and Sierra | North Valley | BUCKS CREEK 1102 | 102211102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_102211103_Capacity | North Valley and Sierra | North Valley | BUCKS CREEK 1103 | 102211103 | Feeder | None | None | None | 27.34% | 0 | 0% | 2.78 | 0.76 | 27.34% | 0 | 0% | 2.78 | 0.75 | 26.98% | 0 | 0% | 2.78 | 0.75 | 26.98% | 0 | 0% | 2.78 | 0.75 | 26.98% | 0 | 0% | 2.78 | 0.75 | 26.98% | 0 | 0%
GNA_1033101_Capacity | North Valley and Sierra | North Valley | BURNEY BANK 1 | 1033101 | Bank | Demand Growth | Capacity | 2023 | 110.4% | 0.49 | 10.4% | 4.71 | 4.75 | 100.8% | 0.04 | 0.8493% | 4.71 | 4.8 | 101.9% | 0.09 | 1.911% | 4.71 | 4.87 | 103.4% | 0.16 | 3.397% | 4.71 | 5.03 | 106.8% | 0.32 | 6.794% | 4.71 | 5.2 | 110.4% | 0.49 | 10.4%
GNA_103311101_Capacity | North Valley and Sierra | North Valley | BURNEY 1101 | 103311101 | Feeder | None | None | None | 75.7% | 0 | 0% | 7.12 | 4.95 | 69.52% | 0 | 0% | 7.12 | 4.99 | 70.08% | 0 | 0% | 7.12 | 5.07 | 71.21% | 0 | 0% | 7.12 | 5.23 | 73.46% | 0 | 0% | 7.12 | 5.39 | 75.7% | 0 | 0%
GNA_1033102_Capacity | North Valley and Sierra | North Valley | BURNEY BANK 2 | 1033102 | Bank | None | None | None | 95.28% | 0 | 0% | 2.12 | 1.98 | 93.4% | 0 | 0% | 2.12 | 1.95 | 91.98% | 0 | 0% | 2.12 | 1.94 | 91.51% | 0 | 0% | 2.12 | 1.99 | 93.87% | 0 | 0% | 2.12 | 2.02 | 95.28% | 0 | 0%
GNA_103311102_Capacity | North Valley and Sierra | North Valley | BURNEY 1102 | 103311102 | Feeder | None | None | None | 53.74% | 0 | 0% | 3.74 | 1.97 | 52.67% | 0 | 0% | 3.74 | 1.94 | 51.87% | 0 | 0% | 3.74 | 1.93 | 51.6% | 0 | 0% | 3.74 | 1.98 | 52.94% | 0 | 0% | 3.74 | 2.01 | 53.74% | 0 | 0%
GNA_1033201_Capacity | North Valley and Sierra | North Valley | CEDAR CREEK BANK 1 | 1033201 | Bank | None | None | None | 52.12% | 0 | 0% | 3.07 | 1.55 | 50.49% | 0 | 0% | 3.07 | 1.55 | 50.49% | 0 | 0% | 3.07 | 1.56 | 50.81% | 0 | 0% | 3.07 | 1.58 | 51.47% | 0 | 0% | 3.07 | 1.6 | 52.12% | 0 | 0%
GNA_103321101_Capacity | North Valley and Sierra | North Valley | CEDAR CREEK 1101 | 103321101 | Feeder | None | None | None | 57.75% | 0 | 0% | 2.84 | 1.59 | 55.99% | 0 | 0% | 2.84 | 1.59 | 55.99% | 0 | 0% | 2.84 | 1.6 | 56.34% | 0 | 0% | 2.84 | 1.61 | 56.69% | 0 | 0% | 2.84 | 1.64 | 57.75% | 0 | 0%
GNA_103501101_Capacity | North Valley and Sierra | North Valley | PIT NO 7 1101 | 103501101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1031801_Capacity | North Valley and Sierra | North Valley | CHESTER BANK 1 | 1031801 | Bank | None | None | None | 43.18% | 0 | 0% | 6.23 | 2.69 | 43.18% | 0 | 0% | 6.23 | 2.63 | 42.22% | 0 | 0% | 6.23 | 2.58 | 41.41% | 0 | 0% | 6.23 | 2.55 | 40.93% | 0 | 0% | 6.23 | 2.6 | 41.73% | 0 | 0%
GNA_103181101_Capacity | North Valley and Sierra | North Valley | CHESTER 1101 | 103181101 | Feeder | None | None | None | 30.58% | 0 | 0% | 6.05 | 1.85 | 30.58% | 0 | 0% | 6.05 | 1.8 | 29.75% | 0 | 0% | 6.05 | 1.78 | 29.42% | 0 | 0% | 6.05 | 1.74 | 28.76% | 0 | 0% | 6.05 | 1.73 | 28.6% | 0 | 0%
GNA_103181102_Capacity | North Valley and Sierra | North Valley | CHESTER 1102 | 103181102 | Feeder | None | None | None | 14.88% | 0 | 0% | 6.05 | 0.88 | 14.55% | 0 | 0% | 6.05 | 0.86 | 14.21% | 0 | 0% | 6.05 | 0.85 | 14.05% | 0 | 0% | 6.05 | 0.86 | 14.21% | 0 | 0% | 6.05 | 0.9 | 14.88% | 0 | 0%
GNA_1028401_Capacity | North Valley and Sierra | North Valley | ANITA BANK 1 | 1028401 | Bank | None | None | None | 87.35% | 0 | 0% | 7.43 | 5.67 | 76.31% | 0 | 0% | 7.43 | 5.87 | 79% | 0 | 0% | 7.43 | 6.07 | 81.7% | 0 | 0% | 7.43 | 6.28 | 84.52% | 0 | 0% | 7.43 | 6.49 | 87.35% | 0 | 0%
GNA_102841101_Capacity | North Valley and Sierra | North Valley | ANITA 1101 | 102841101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_102841102_Capacity | North Valley and Sierra | North Valley | ANITA 1102 | 102841102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1028402_Capacity | North Valley and Sierra | North Valley | ANITA BANK 2 | 1028402 | Bank | None | None | None | 56.6% | 0 | 0% | 29.7 | 15.78 | 53.13% | 0 | 0% | 29.7 | 15.99 | 53.84% | 0 | 0% | 29.7 | 16.25 | 54.71% | 0 | 0% | 29.7 | 16.51 | 55.59% | 0 | 0% | 29.7 | 16.81 | 56.6% | 0 | 0%
GNA_102841105_Capacity | North Valley and Sierra | North Valley | ANITA 1105 | 102841105 | Feeder | None | None | None | 69.6% | 0 | 0% | 12.83 | 8.4 | 65.47% | 0 | 0% | 12.83 | 8.5 | 66.25% | 0 | 0% | 12.83 | 8.63 | 67.26% | 0 | 0% | 12.83 | 8.77 | 68.36% | 0 | 0% | 12.83 | 8.93 | 69.6% | 0 | 0%
GNA_102841106_Capacity | North Valley and Sierra | North Valley | ANITA 1106 | 102841106 | Feeder | None | None | None | 62.35% | 0 | 0% | 12.83 | 7.53 | 58.69% | 0 | 0% | 12.83 | 7.63 | 59.47% | 0 | 0% | 12.83 | 7.76 | 60.48% | 0 | 0% | 12.83 | 7.87 | 61.34% | 0 | 0% | 12.83 | 8 | 62.35% | 0 | 0%
GNA_1030802_Capacity | North Valley and Sierra | North Valley | BUTTE BANK 2 | 1030802 | Bank | None | None | None | 83.11% | 0 | 0% | 24.22 | 19.01 | 78.49% | 0 | 0% | 24.22 | 19.24 | 79.44% | 0 | 0% | 24.22 | 19.48 | 80.43% | 0 | 0% | 24.22 | 19.78 | 81.67% | 0 | 0% | 24.22 | 20.13 | 83.11% | 0 | 0%
GNA_103081103_Capacity | North Valley and Sierra | North Valley | BUTTE 1103 | 103081103 | Feeder | None | None | None | 81.87% | 0 | 0% | 12.19 | 9.37 | 76.87% | 0 | 0% | 12.19 | 9.49 | 77.85% | 0 | 0% | 12.19 | 9.63 | 79% | 0 | 0% | 12.19 | 9.79 | 80.31% | 0 | 0% | 12.19 | 9.98 | 81.87% | 0 | 0%
GNA_103081104_Capacity | North Valley and Sierra | North Valley | BUTTE 1104 | 103081104 | Feeder | None | None | None | 92.21% | 0 | 0% | 12.19 | 10.73 | 88.02% | 0 | 0% | 12.19 | 10.85 | 89.01% | 0 | 0% | 12.19 | 10.95 | 89.83% | 0 | 0% | 12.19 | 11.08 | 90.89% | 0 | 0% | 12.19 | 11.24 | 92.21% | 0 | 0%
GNA_1030803_Capacity | North Valley and Sierra | North Valley | BUTTE BANK 3 | 1030803 | Bank | None | None | None | 88.28% | 0 | 0% | 29.7 | 24.05 | 80.98% | 0 | 0% | 29.7 | 25.11 | 84.55% | 0 | 0% | 29.7 | 25.47 | 85.76% | 0 | 0% | 29.7 | 25.79 | 86.84% | 0 | 0% | 29.7 | 26.22 | 88.28% | 0 | 0%
GNA_103081105_Capacity | North Valley and Sierra | North Valley | BUTTE 1105 | 103081105 | Feeder | None | None | None | 52.58% | 0 | 0% | 12.19 | 6.17 | 50.62% | 0 | 0% | 12.19 | 6.22 | 51.03% | 0 | 0% | 12.19 | 6.28 | 51.52% | 0 | 0% | 12.19 | 6.32 | 51.85% | 0 | 0% | 12.19 | 6.41 | 52.58% | 0 | 0%
GNA_103081106_Capacity | North Valley and Sierra | North Valley | BUTTE 1106 | 103081106 | Feeder | None | None | None | 71.16% | 0 | 0% | 12.83 | 8.69 | 67.73% | 0 | 0% | 12.83 | 8.84 | 68.9% | 0 | 0% | 12.83 | 8.95 | 69.76% | 0 | 0% | 12.83 | 9.02 | 70.3% | 0 | 0% | 12.83 | 9.13 | 71.16% | 0 | 0%
GNA_103081107_Capacity | North Valley and Sierra | North Valley | BUTTE 1107 | 103081107 | Feeder | None | None | None | 86.91% | 0 | 0% | 12.83 | 9.98 | 77.79% | 0 | 0% | 12.83 | 10.8 | 84.18% | 0 | 0% | 12.83 | 10.91 | 85.04% | 0 | 0% | 12.83 | 11.01 | 85.81% | 0 | 0% | 12.83 | 11.15 | 86.91% | 0 | 0%
GNA_1020502_Capacity | North Valley and Sierra | North Valley | CHICO A BANK 2 | 1020502 | Bank | None | None | None | 98.63% | 0 | 0% | 19.75 | 18.78 | 95.09% | 0 | 0% | 19.75 | 18.93 | 95.85% | 0 | 0% | 19.75 | 19.06 | 96.51% | 0 | 0% | 19.75 | 19.26 | 97.52% | 0 | 0% | 19.75 | 19.48 | 98.63% | 0 | 0%
GNA_1020501_Capacity | North Valley and Sierra | North Valley | CHICO A BANK 1 | 1020501 | Bank | None | None | None | 89.29% | 0 | 0% | 4.95 | 4.38 | 88.48% | 0 | 0% | 4.95 | 4.38 | 88.48% | 0 | 0% | 4.95 | 4.38 | 88.48% | 0 | 0% | 4.95 | 4.39 | 88.69% | 0 | 0% | 4.95 | 4.42 | 89.29% | 0 | 0%
GNA_102050401_Capacity | North Valley and Sierra | North Valley | CHICO A 0401 | 102050401 | Feeder | None | None | None | 50% | 0 | 0% | 2.34 | 1.16 | 49.57% | 0 | 0% | 2.34 | 1.15 | 49.15% | 0 | 0% | 2.34 | 1.16 | 49.57% | 0 | 0% | 2.34 | 1.16 | 49.57% | 0 | 0% | 2.34 | 1.17 | 50% | 0 | 0%
GNA_102050402_Capacity | North Valley and Sierra | North Valley | CHICO A 0402 | 102050402 | Feeder | None | None | None | 81.05% | 0 | 0% | 2.85 | 2.28 | 80% | 0 | 0% | 2.85 | 2.28 | 80% | 0 | 0% | 2.85 | 2.29 | 80.35% | 0 | 0% | 2.85 | 2.28 | 80% | 0 | 0% | 2.85 | 2.31 | 81.05% | 0 | 0%
GNA_102051101_Capacity | North Valley and Sierra | North Valley | CHICO A 1101 | 102051101 | Feeder | None | None | None | 42.17% | 0 | 0% | 12.83 | 4.95 | 38.58% | 0 | 0% | 12.83 | 5.05 | 39.36% | 0 | 0% | 12.83 | 5.15 | 40.14% | 0 | 0% | 12.83 | 5.27 | 41.08% | 0 | 0% | 12.83 | 5.41 | 42.17% | 0 | 0%
GNA_102051102_Capacity | North Valley and Sierra | North Valley | CHICO A 1102 | 102051102 | Feeder | None | None | None | 82.31% | 0 | 0% | 10.46 | 8.61 | 82.31% | 0 | 0% | 10.46 | 8.59 | 82.12% | 0 | 0% | 10.46 | 8.57 | 81.93% | 0 | 0% | 10.46 | 8.58 | 82.03% | 0 | 0% | 10.46 | 8.57 | 81.93% | 0 | 0%
GNA_102051103_Capacity | North Valley and Sierra | North Valley | CHICO A 1103 | 102051103 | Feeder | None | None | None | 44.7% | 0 | 0% | 10.76 | 4.48 | 41.64% | 0 | 0% | 10.76 | 4.58 | 42.57% | 0 | 0% | 10.76 | 4.65 | 43.22% | 0 | 0% | 10.76 | 4.73 | 43.96% | 0 | 0% | 10.76 | 4.81 | 44.7% | 0 | 0%
GNA_1029401_Capacity | North Valley and Sierra | North Valley | DAYTON ROAD BANK 1 | 1029401 | Bank | None | None | None | 73.23% | 0 | 0% | 1.98 | 1.45 | 73.23% | 0 | 0% | 1.98 | 1.45 | 73.23% | 0 | 0% | 1.98 | 1.45 | 73.23% | 0 | 0% | 1.98 | 1.45 | 73.23% | 0 | 0% | 1.98 | 1.45 | 73.23% | 0 | 0%
GNA_102940401_Capacity | North Valley and Sierra | North Valley | DAYTON ROAD 0401 | 102940401 | Feeder | None | None | None | 67.17% | 0 | 0% | 1.98 | 1.33 | 67.17% | 0 | 0% | 1.98 | 1.32 | 66.67% | 0 | 0% | 1.98 | 1.32 | 66.67% | 0 | 0% | 1.98 | 1.32 | 66.67% | 0 | 0% | 1.98 | 1.32 | 66.67% | 0 | 0%
GNA_1024901_Capacity | North Valley and Sierra | North Valley | CHICO B BANK 1 | 1024901 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_102491101_Capacity | North Valley and Sierra | North Valley | CHICO B 1101 | 102491101 | Feeder | None | None | None | 65.68% | 0 | 0% | 10.46 | 6.87 | 65.68% | 0 | 0% | 10.46 | 6.86 | 65.58% | 0 | 0% | 10.46 | 6.85 | 65.49% | 0 | 0% | 10.46 | 6.83 | 65.3% | 0 | 0% | 10.46 | 6.81 | 65.11% | 0 | 0%
GNA_102491102_Capacity | North Valley and Sierra | North Valley | CHICO B 1102 | 102491102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_102491103_Capacity | North Valley and Sierra | North Valley | CHICO B 1103 | 102491103 | Feeder | None | None | None | 60.8% | 0 | 0% | 10.46 | 6.19 | 59.18% | 0 | 0% | 10.46 | 6.22 | 59.46% | 0 | 0% | 10.46 | 6.25 | 59.75% | 0 | 0% | 10.46 | 6.29 | 60.13% | 0 | 0% | 10.46 | 6.36 | 60.8% | 0 | 0%
GNA_1024902_Capacity | North Valley and Sierra | North Valley | CHICO B BANK 2 | 1024902 | Bank | None | None | None | 99.68% | 0 | 0% | 15.84 | 15.79 | 99.68% | 0 | 0% | 15.84 | 15.64 | 98.74% | 0 | 0% | 15.84 | 15.47 | 97.66% | 0 | 0% | 15.84 | 15.32 | 96.72% | 0 | 0% | 15.84 | 15.18 | 95.83% | 0 | 0%
GNA_102491105_Capacity | North Valley and Sierra | North Valley | CHICO B 1105 | 102491105 | Feeder | None | None | None | 88.1% | 0 | 0% | 12.1 | 10.66 | 88.1% | 0 | 0% | 12.1 | 10.58 | 87.44% | 0 | 0% | 12.1 | 10.57 | 87.36% | 0 | 0% | 12.1 | 10.59 | 87.52% | 0 | 0% | 12.1 | 10.65 | 88.02% | 0 | 0%
GNA_102491106_Capacity | North Valley and Sierra | North Valley | CHICO B 1106 | 102491106 | Feeder | None | None | None | 41.23% | 0 | 0% | 12.83 | 5.29 | 41.23% | 0 | 0% | 12.83 | 5.28 | 41.15% | 0 | 0% | 12.83 | 5.28 | 41.15% | 0 | 0% | 12.83 | 5.25 | 40.92% | 0 | 0% | 12.83 | 5.23 | 40.76% | 0 | 0%
GNA_1021701_Capacity | North Valley and Sierra | North Valley | ESQUON BANK 1 | 1021701 | Bank | None | None | None | 95.98% | 0 | 0% | 8.21 | 6.86 | 83.56% | 0 | 0% | 8.21 | 7.1 | 86.48% | 0 | 0% | 8.21 | 7.35 | 89.52% | 0 | 0% | 8.21 | 7.61 | 92.69% | 0 | 0% | 8.21 | 7.88 | 95.98% | 0 | 0%
GNA_102171101_Capacity | North Valley and Sierra | North Valley | ESQUON 1101 | 102171101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_102171102_Capacity | North Valley and Sierra | North Valley | ESQUON 1102 | 102171102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_102171103_Capacity | North Valley and Sierra | North Valley | ESQUON 1103 | 102171103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1030701_Capacity | North Valley and Sierra | North Valley | NORD BANK 1 | 1030701 | Bank | None | None | None | 90.4% | 0 | 0% | 15.84 | 13.65 | 86.17% | 0 | 0% | 15.84 | 13.71 | 86.55% | 0 | 0% | 15.84 | 13.85 | 87.44% | 0 | 0% | 15.84 | 14.05 | 88.7% | 0 | 0% | 15.84 | 14.32 | 90.4% | 0 | 0%
GNA_103071103_Capacity | North Valley and Sierra | North Valley | NORD 1103 | 103071103 | Feeder | None | None | None | 79.73% | 0 | 0% | 12.83 | 10.02 | 78.1% | 0 | 0% | 12.83 | 10.03 | 78.18% | 0 | 0% | 12.83 | 10.05 | 78.33% | 0 | 0% | 12.83 | 10.12 | 78.88% | 0 | 0% | 12.83 | 10.23 | 79.73% | 0 | 0%
GNA_103071104_Capacity | North Valley and Sierra | North Valley | NORD 1104 | 103071104 | Feeder | None | None | None | 40.44% | 0 | 0% | 12.19 | 4.4 | 36.1% | 0 | 0% | 12.19 | 4.52 | 37.08% | 0 | 0% | 12.19 | 4.63 | 37.98% | 0 | 0% | 12.19 | 4.78 | 39.21% | 0 | 0% | 12.19 | 4.93 | 40.44% | 0 | 0%
GNA_1030702_Capacity | North Valley and Sierra | North Valley | NORD BANK 2 | 1030702 | Bank | None | None | None | 96.21% | 0 | 0% | 15.84 | 14.13 | 89.2% | 0 | 0% | 15.84 | 14.38 | 90.78% | 0 | 0% | 15.84 | 14.64 | 92.42% | 0 | 0% | 15.84 | 14.93 | 94.26% | 0 | 0% | 15.84 | 15.24 | 96.21% | 0 | 0%
GNA_103071105_Capacity | North Valley and Sierra | North Valley | NORD 1105 | 103071105 | Feeder | None | None | None | 78.67% | 0 | 0% | 12.19 | 9.01 | 73.91% | 0 | 0% | 12.19 | 9.14 | 74.98% | 0 | 0% | 12.19 | 9.27 | 76.05% | 0 | 0% | 12.19 | 9.43 | 77.36% | 0 | 0% | 12.19 | 9.59 | 78.67% | 0 | 0%
GNA_103071106_Capacity | North Valley and Sierra | North Valley | NORD 1106 | 103071106 | Feeder | None | None | None | 47.09% | 0 | 0% | 12.36 | 5.32 | 43.04% | 0 | 0% | 12.36 | 5.43 | 43.93% | 0 | 0% | 12.36 | 5.55 | 44.9% | 0 | 0% | 12.36 | 5.68 | 45.95% | 0 | 0% | 12.36 | 5.82 | 47.09% | 0 | 0%
GNA_1020401_Capacity | North Valley and Sierra | North Valley | NOTRE DAME BANK 1 | 1020401 | Bank | None | None | None | 94.84% | 0 | 0% | 44.55 | 37.94 | 85.16% | 0 | 0% | 44.55 | 38.64 | 86.73% | 0 | 0% | 44.55 | 39.38 | 88.4% | 0 | 0% | 44.55 | 40.54 | 91% | 0 | 0% | 44.55 | 42.25 | 94.84% | 0 | 0%
GNA_102041101_Capacity | North Valley and Sierra | North Valley | NOTRE DAME 1101 | 102041101 | Feeder | None | None | None | 47.49% | 0 | 0% | 12.36 | 5.45 | 44.09% | 0 | 0% | 12.36 | 5.56 | 44.98% | 0 | 0% | 12.36 | 5.65 | 45.71% | 0 | 0% | 12.36 | 5.76 | 46.6% | 0 | 0% | 12.36 | 5.87 | 47.49% | 0 | 0%
GNA_102041102_Capacity | North Valley and Sierra | North Valley | NOTRE DAME 1102 | 102041102 | Feeder | None | None | None | 98.87% | 0 | 0% | 12.36 | 8.95 | 72.41% | 0 | 0% | 12.36 | 9.45 | 76.46% | 0 | 0% | 12.36 | 9.96 | 80.58% | 0 | 0% | 12.36 | 10.97 | 88.75% | 0 | 0% | 12.36 | 12.22 | 98.87% | 0 | 0%
GNA_102041103_Capacity | North Valley and Sierra | North Valley | NOTRE DAME 1103 | 102041103 | Feeder | None | None | None | 92.36% | 0 | 0% | 12.83 | 11.22 | 87.45% | 0 | 0% | 12.83 | 11.32 | 88.23% | 0 | 0% | 12.83 | 11.45 | 89.24% | 0 | 0% | 12.83 | 11.65 | 90.8% | 0 | 0% | 12.83 | 11.85 | 92.36% | 0 | 0%
GNA_102041104_Capacity | North Valley and Sierra | North Valley | NOTRE DAME 1104 | 102041104 | Feeder | None | None | None | 90.34% | 0 | 0% | 12.83 | 10.91 | 85.04% | 0 | 0% | 12.83 | 11.04 | 86.05% | 0 | 0% | 12.83 | 11.19 | 87.22% | 0 | 0% | 12.83 | 11.36 | 88.54% | 0 | 0% | 12.83 | 11.59 | 90.34% | 0 | 0%
GNA_1029701_Capacity | North Valley and Sierra | North Valley | SYCAMORE CREEK BANK 1 | 1029701 | Bank | None | None | None | 98.65% | 0 | 0% | 29.7 | 28.24 | 95.08% | 0 | 0% | 29.7 | 28.45 | 95.79% | 0 | 0% | 29.7 | 28.64 | 96.43% | 0 | 0% | 29.7 | 28.92 | 97.37% | 0 | 0% | 29.7 | 29.3 | 98.65% | 0 | 0%
GNA_102971101_Capacity | North Valley and Sierra | North Valley | SYCAMORE CREEK 1101 | 102971101 | Feeder | None | None | None | 89.31% | 0 | 0% | 10.76 | 9.46 | 87.92% | 0 | 0% | 10.76 | 9.48 | 88.1% | 0 | 0% | 10.76 | 9.54 | 88.66% | 0 | 0% | 10.76 | 9.58 | 89.03% | 0 | 0% | 10.76 | 9.61 | 89.31% | 0 | 0%
GNA_102971102_Capacity | North Valley and Sierra | North Valley | SYCAMORE CREEK 1102 | 102971102 | Feeder | None | None | None | 89.96% | 0 | 0% | 10.76 | 9.33 | 86.71% | 0 | 0% | 10.76 | 9.41 | 87.45% | 0 | 0% | 10.76 | 9.49 | 88.2% | 0 | 0% | 10.76 | 9.57 | 88.94% | 0 | 0% | 10.76 | 9.68 | 89.96% | 0 | 0%
GNA_102971103_Capacity | North Valley and Sierra | North Valley | SYCAMORE CREEK 1103 | 102971103 | Feeder | None | None | None | 56.13% | 0 | 0% | 10.76 | 5.51 | 51.21% | 0 | 0% | 10.76 | 5.62 | 52.23% | 0 | 0% | 10.76 | 5.74 | 53.35% | 0 | 0% | 10.76 | 5.87 | 54.55% | 0 | 0% | 10.76 | 6.04 | 56.13% | 0 | 0%
GNA_102971104_Capacity | North Valley and Sierra | North Valley | SYCAMORE CREEK 1104 | 102971104 | Feeder | None | None | None | 40.96% | 0 | 0% | 11.67 | 4.6 | 39.42% | 0 | 0% | 11.67 | 4.64 | 39.76% | 0 | 0% | 11.67 | 4.65 | 39.85% | 0 | 0% | 11.67 | 4.7 | 40.27% | 0 | 0% | 11.67 | 4.78 | 40.96% | 0 | 0%
GNA_1029702_Capacity | North Valley and Sierra | North Valley | SYCAMORE CREEK BANK 2 | 1029702 | Bank | None | None | None | 77.02% | 0 | 0% | 29.59 | 21.63 | 73.1% | 0 | 0% | 29.59 | 21.71 | 73.37% | 0 | 0% | 29.59 | 21.86 | 73.88% | 0 | 0% | 29.59 | 22.24 | 75.16% | 0 | 0% | 29.59 | 22.79 | 77.02% | 0 | 0%
GNA_102971105_Capacity | North Valley and Sierra | North Valley | SYCAMORE CREEK 1105 | 102971105 | Feeder | None | None | None | 99.74% | 0 | 0% | 11.67 | 11.22 | 96.14% | 0 | 0% | 11.67 | 11.26 | 96.49% | 0 | 0% | 11.67 | 11.33 | 97.09% | 0 | 0% | 11.67 | 11.44 | 98.03% | 0 | 0% | 11.67 | 11.64 | 99.74% | 0 | 0%
GNA_1026501_Capacity | North Valley and Sierra | North Valley | CHICO C BANK 1 | 1026501 | Bank | None | None | None | 54.04% | 0 | 0% | 1.98 | 1.04 | 52.53% | 0 | 0% | 1.98 | 1.04 | 52.53% | 0 | 0% | 1.98 | 1.05 | 53.03% | 0 | 0% | 1.98 | 1.06 | 53.54% | 0 | 0% | 1.98 | 1.07 | 54.04% | 0 | 0%
GNA_102650401_Capacity | North Valley and Sierra | North Valley | CHICO C 0401 | 102650401 | Feeder | None | None | None | 43.59% | 0 | 0% | 2.34 | 1 | 42.74% | 0 | 0% | 2.34 | 0.99 | 42.31% | 0 | 0% | 2.34 | 1 | 42.74% | 0 | 0% | 2.34 | 1.01 | 43.16% | 0 | 0% | 2.34 | 1.02 | 43.59% | 0 | 0%
GNA_102971107_Capacity | North Valley and Sierra | North Valley | SYCAMORE CREEK 1107 | 102971107 | Feeder | None | None | None | 93.61% | 0 | 0% | 10.95 | 9.52 | 86.94% | 0 | 0% | 10.95 | 9.57 | 87.4% | 0 | 0% | 10.95 | 9.67 | 88.31% | 0 | 0% | 10.95 | 9.94 | 90.78% | 0 | 0% | 10.95 | 10.25 | 93.61% | 0 | 0%
GNA_1029703_Capacity | North Valley and Sierra | North Valley | SYCAMORE CREEK BANK 3 | 1029703 | Bank | None | None | None | 99.63% | 0 | 0% | 29.7 | 28.15 | 94.78% | 0 | 0% | 29.7 | 28.41 | 95.66% | 0 | 0% | 29.7 | 28.73 | 96.73% | 0 | 0% | 29.7 | 29.12 | 98.05% | 0 | 0% | 29.7 | 29.59 | 99.63% | 0 | 0%
GNA_102971109_Capacity | North Valley and Sierra | North Valley | SYCAMORE CREEK 1109 | 102971109 | Feeder | None | None | None | 94.6% | 0 | 0% | 11.67 | 10.26 | 87.92% | 0 | 0% | 11.67 | 10.42 | 89.29% | 0 | 0% | 11.67 | 10.59 | 90.75% | 0 | 0% | 11.67 | 10.81 | 92.63% | 0 | 0% | 11.67 | 11.04 | 94.6% | 0 | 0%
GNA_102971110_Capacity | North Valley and Sierra | North Valley | SYCAMORE CREEK 1110 | 102971110 | Feeder | None | None | None | 93.88% | 0 | 0% | 10.95 | 10.28 | 93.88% | 0 | 0% | 10.95 | 10.23 | 93.42% | 0 | 0% | 10.95 | 10.23 | 93.42% | 0 | 0% | 10.95 | 10.22 | 93.33% | 0 | 0% | 10.95 | 10.21 | 93.24% | 0 | 0%
GNA_102971111_Capacity | North Valley and Sierra | North Valley | SYCAMORE CREEK 1111 | 102971111 | Feeder | None | None | None | 98.42% | 0 | 0% | 10.76 | 10.38 | 96.47% | 0 | 0% | 10.76 | 10.38 | 96.47% | 0 | 0% | 10.76 | 10.37 | 96.38% | 0 | 0% | 10.76 | 10.41 | 96.75% | 0 | 0% | 10.76 | 10.59 | 98.42% | 0 | 0%
GNA_1030901_Capacity | North Valley and Sierra | North Valley | CLARK ROAD BANK 1 | 1030901 | Bank | None | None | None | 62.75% | 0 | 0% | 9.88 | 6.2 | 62.75% | 0 | 0% | 9.88 | 6.06 | 61.34% | 0 | 0% | 9.88 | 5.91 | 59.82% | 0 | 0% | 9.88 | 5.82 | 58.91% | 0 | 0% | 9.88 | 5.79 | 58.6% | 0 | 0%
GNA_103091101_Capacity | North Valley and Sierra | North Valley | CLARK ROAD 1101 | 103091101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_103091102_Capacity | North Valley and Sierra | North Valley | CLARK ROAD 1102 | 103091102 | Feeder | None | None | None | 59.06% | 0 | 0% | 8.55 | 5.05 | 59.06% | 0 | 0% | 8.55 | 4.9 | 57.31% | 0 | 0% | 8.55 | 4.76 | 55.67% | 0 | 0% | 8.55 | 4.69 | 54.85% | 0 | 0% | 8.55 | 4.69 | 54.85% | 0 | 0%
GNA_1033302_Capacity | North Valley and Sierra | North Valley | CORNING BANK 2 | 1033302 | Bank | None | None | None | 91.17% | 0 | 0% | 22.99 | 20.96 | 91.17% | 0 | 0% | 29.99 | 21.03 | 70.12% | 0 | 0% | 29.99 | 21.23 | 70.79% | 0 | 0% | 29.99 | 21.38 | 71.29% | 0 | 0% | 29.99 | 21.64 | 72.16% | 0 | 0%
GNA_103331101_Capacity | North Valley and Sierra | North Valley | CORNING 1101 | 103331101 | Feeder | Demand Growth | Capacity | 2027 | 101% | 0.11 | 1.029% | 10.69 | 10.61 | 99.25% | 0 | 0% | 10.69 | 10.57 | 98.88% | 0 | 0% | 10.69 | 10.67 | 99.81% | 0 | 0% | 10.69 | 10.72 | 100.3% | 0.03 | 0.2806% | 10.69 | 10.8 | 101% | 0.11 | 1.029%
GNA_103331102_Capacity | North Valley and Sierra | North Valley | CORNING 1102 | 103331102 | Feeder | Demand Growth | Capacity | 2027 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1033303_Capacity | North Valley and Sierra | North Valley | CORNING BANK 3 | 1033303 | Bank | None | None | None | 84.28% | 0 | 0% | 29.7 | 24.71 | 83.2% | 0 | 0% | 29.7 | 24.75 | 83.33% | 0 | 0% | 29.7 | 24.79 | 83.47% | 0 | 0% | 29.7 | 24.89 | 83.8% | 0 | 0% | 29.7 | 25.03 | 84.28% | 0 | 0%
GNA_103331103_Capacity | North Valley and Sierra | North Valley | CORNING 1103 | 103331103 | Feeder | None | None | None | 96.18% | 0 | 0% | 12.83 | 12.07 | 94.08% | 0 | 0% | 12.83 | 12.14 | 94.62% | 0 | 0% | 12.83 | 12.18 | 94.93% | 0 | 0% | 12.83 | 12.25 | 95.48% | 0 | 0% | 12.83 | 12.34 | 96.18% | 0 | 0%
GNA_103331104_Capacity | North Valley and Sierra | North Valley | CORNING 1104 | 103331104 | Feeder | None | None | None | 88.44% | 0 | 0% | 14.97 | 13.12 | 87.64% | 0 | 0% | 14.97 | 13.01 | 86.91% | 0 | 0% | 14.97 | 13.05 | 87.17% | 0 | 0% | 14.97 | 13.11 | 87.58% | 0 | 0% | 14.97 | 13.24 | 88.44% | 0 | 0%
GNA_1033901_Capacity | North Valley and Sierra | North Valley | GERBER BANK 1 | 1033901 | Bank | None | None | None | 98.75% | 0 | 0% | 8.82 | 7.67 | 86.96% | 0 | 0% | 8.82 | 7.93 | 89.91% | 0 | 0% | 8.82 | 8.18 | 92.74% | 0 | 0% | 8.82 | 8.45 | 95.8% | 0 | 0% | 8.82 | 8.71 | 98.75% | 0 | 0%
GNA_103391101_Capacity | North Valley and Sierra | North Valley | GERBER 1101 | 103391101 | Feeder | None | None | None | 50% | 0 | 0% | 7.12 | 2.97 | 41.71% | 0 | 0% | 7.12 | 3.09 | 43.4% | 0 | 0% | 7.12 | 3.23 | 45.37% | 0 | 0% | 7.12 | 3.4 | 47.75% | 0 | 0% | 7.12 | 3.56 | 50% | 0 | 0%
GNA_103391102_Capacity | North Valley and Sierra | North Valley | GERBER 1102 | 103391102 | Feeder | None | None | None | 74.16% | 0 | 0% | 7.12 | 4.83 | 67.84% | 0 | 0% | 7.12 | 4.95 | 69.52% | 0 | 0% | 7.12 | 5.06 | 71.07% | 0 | 0% | 7.12 | 5.18 | 72.75% | 0 | 0% | 7.12 | 5.28 | 74.16% | 0 | 0%
GNA_1034801_Capacity | North Valley and Sierra | North Valley | LOS MOLINOS BANK 1 | 1034801 | Bank | None | None | None | 87.92% | 0 | 0% | 11.84 | 10.41 | 87.92% | 0 | 0% | 11.84 | 10.37 | 87.58% | 0 | 0% | 11.84 | 10.35 | 87.42% | 0 | 0% | 11.84 | 10.33 | 87.25% | 0 | 0% | 11.84 | 10.27 | 86.74% | 0 | 0%
GNA_103481101_Capacity | North Valley and Sierra | North Valley | LOS MOLINOS 1101 | 103481101 | Feeder | None | None | None | 56.08% | 0 | 0% | 6.99 | 3.92 | 56.08% | 0 | 0% | 6.99 | 3.91 | 55.94% | 0 | 0% | 6.99 | 3.91 | 55.94% | 0 | 0% | 6.99 | 3.9 | 55.79% | 0 | 0% | 6.99 | 3.89 | 55.65% | 0 | 0%
GNA_103481102_Capacity | North Valley and Sierra | North Valley | LOS MOLINOS 1102 | 103481102 | Feeder | None | None | None | 95.76% | 0 | 0% | 6.84 | 6.55 | 95.76% | 0 | 0% | 6.84 | 6.52 | 95.32% | 0 | 0% | 6.84 | 6.51 | 95.18% | 0 | 0% | 6.84 | 6.5 | 95.03% | 0 | 0% | 6.84 | 6.46 | 94.44% | 0 | 0%
GNA_1035801_Capacity | North Valley and Sierra | North Valley | VINA BANK 1 | 1035801 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_103581101_Capacity | North Valley and Sierra | North Valley | VINA 1101 | 103581101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1027801_Capacity | North Valley and Sierra | North Valley | ELK CREEK BANK 1 | 1027801 | Bank | None | None | None | 79.72% | 0 | 0% | 2.81 | 2.24 | 79.72% | 0 | 0% | 2.81 | 2.19 | 77.94% | 0 | 0% | 2.81 | 2.19 | 77.94% | 0 | 0% | 2.81 | 2.18 | 77.58% | 0 | 0% | 2.81 | 2.2 | 78.29% | 0 | 0%
GNA_102781101_Capacity | North Valley and Sierra | North Valley | ELK CREEK 1101 | 102781101 | Feeder | None | None | None | 83.1% | 0 | 0% | 2.84 | 2.36 | 83.1% | 0 | 0% | 2.84 | 2.32 | 81.69% | 0 | 0% | 2.84 | 2.31 | 81.34% | 0 | 0% | 2.84 | 2.3 | 80.99% | 0 | 0% | 2.84 | 2.32 | 81.69% | 0 | 0%
GNA_1033801_Capacity | North Valley and Sierra | North Valley | FRENCH GULCH BANK 1 | 1033801 | Bank | None | None | None | 42.86% | 0 | 0% | 1.89 | 0.67 | 35.45% | 0 | 0% | 1.89 | 0.7 | 37.04% | 0 | 0% | 1.89 | 0.78 | 41.27% | 0 | 0% | 1.89 | 0.8 | 42.33% | 0 | 0% | 1.89 | 0.81 | 42.86% | 0 | 0%
GNA_103381101_Capacity | North Valley and Sierra | North Valley | FRENCH GULCH 1101 | 103381101 | Feeder | None | None | None | 21.43% | 0 | 0% | 4.06 | 0.73 | 17.98% | 0 | 0% | 4.06 | 0.76 | 18.72% | 0 | 0% | 4.06 | 0.84 | 20.69% | 0 | 0% | 4.06 | 0.85 | 20.94% | 0 | 0% | 4.06 | 0.87 | 21.43% | 0 | 0%
GNA_103381102_Capacity | North Valley and Sierra | North Valley | FRENCH GULCH 1102 | 103381102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1025301_Capacity | North Valley and Sierra | North Valley | GRAYS FLAT BANK 1 | 1025301 | Bank | None | None | None | 13.48% | 0 | 0% | 1.41 | 0.19 | 13.48% | 0 | 0% | 1.41 | 0.19 | 13.48% | 0 | 0% | 1.41 | 0.19 | 13.48% | 0 | 0% | 1.41 | 0.19 | 13.48% | 0 | 0% | 1.41 | 0.19 | 13.48% | 0 | 0%
GNA_102530401_Capacity | North Valley and Sierra | North Valley | GRAYS FLAT 0401 | 102530401 | Feeder | None | None | None | 16.13% | 0 | 0% | 1.24 | 0.19 | 15.32% | 0 | 0% | 1.24 | 0.2 | 16.13% | 0 | 0% | 1.24 | 0.2 | 16.13% | 0 | 0% | 1.24 | 0.19 | 15.32% | 0 | 0% | 1.24 | 0.2 | 16.13% | 0 | 0%
GNA_1032101_Capacity | North Valley and Sierra | North Valley | HONCUT BANK 1 | 1032101 | Bank | Demand Growth | Capacity | 2023 | 110.2% | 1.61 | 10.16% | 15.84 | 17.28 | 109.1% | 1.44 | 9.091% | 15.84 | 17.28 | 109.1% | 1.44 | 9.091% | 15.84 | 17.28 | 109.1% | 1.44 | 9.091% | 15.84 | 17.34 | 109.5% | 1.5 | 9.47% | 15.84 | 17.45 | 110.2% | 1.61 | 10.16%
GNA_103211101_Capacity | North Valley and Sierra | North Valley | HONCUT 1101 | 103211101 | Feeder | None | None | None | 85.73% | 0 | 0% | 8.55 | 7.32 | 85.61% | 0 | 0% | 8.55 | 7.3 | 85.38% | 0 | 0% | 8.55 | 7.28 | 85.15% | 0 | 0% | 8.55 | 7.29 | 85.26% | 0 | 0% | 8.55 | 7.33 | 85.73% | 0 | 0%
GNA_103211102_Capacity | North Valley and Sierra | North Valley | HONCUT 1102 | 103211102 | Feeder | None | None | None | 85.97% | 0 | 0% | 11.33 | 9.7 | 85.61% | 0 | 0% | 11.33 | 9.67 | 85.35% | 0 | 0% | 11.33 | 9.64 | 85.08% | 0 | 0% | 11.33 | 9.68 | 85.44% | 0 | 0% | 11.33 | 9.74 | 85.97% | 0 | 0%
GNA_1032401_Capacity | North Valley and Sierra | North Valley | PEACHTON BANK 1 | 1032401 | Bank | None | None | None | 92.26% | 0 | 0% | 8.79 | 8.11 | 92.26% | 0 | 0% | 8.79 | 8.1 | 92.15% | 0 | 0% | 8.79 | 8.09 | 92.04% | 0 | 0% | 8.79 | 8.08 | 91.92% | 0 | 0% | 8.79 | 8.1 | 92.15% | 0 | 0%
GNA_103241102_Capacity | North Valley and Sierra | North Valley | PEACHTON 1102 | 103241102 | Feeder | None | None | None | 69.85% | 0 | 0% | 9.62 | 6.72 | 69.85% | 0 | 0% | 9.62 | 6.72 | 69.85% | 0 | 0% | 9.62 | 6.72 | 69.85% | 0 | 0% | 9.62 | 6.71 | 69.75% | 0 | 0% | 9.62 | 6.71 | 69.75% | 0 | 0%
GNA_103241103_Capacity | North Valley and Sierra | North Valley | PEACHTON 1103 | 103241103 | Feeder | None | None | None | 44.62% | 0 | 0% | 8.92 | 3.98 | 44.62% | 0 | 0% | 8.92 | 3.96 | 44.39% | 0 | 0% | 8.92 | 3.96 | 44.39% | 0 | 0% | 8.92 | 3.95 | 44.28% | 0 | 0% | 8.92 | 3.96 | 44.39% | 0 | 0%
GNA_1032402_Capacity | North Valley and Sierra | North Valley | PEACHTON BANK 2 | 1032402 | Bank | None | None | None | 94.43% | 0 | 0% | 4.49 | 3.82 | 85.08% | 0 | 0% | 4.49 | 3.9 | 86.86% | 0 | 0% | 4.49 | 4.01 | 89.31% | 0 | 0% | 4.49 | 4.12 | 91.76% | 0 | 0% | 4.49 | 4.24 | 94.43% | 0 | 0%
GNA_103241101_Capacity | North Valley and Sierra | North Valley | PEACHTON 1101 | 103241101 | Feeder | None | None | None | 67.65% | 0 | 0% | 8.13 | 5.08 | 62.48% | 0 | 0% | 8.13 | 5.16 | 63.47% | 0 | 0% | 8.13 | 5.27 | 64.82% | 0 | 0% | 8.13 | 5.38 | 66.17% | 0 | 0% | 8.13 | 5.5 | 67.65% | 0 | 0%
GNA_1032502_Capacity | North Valley and Sierra | North Valley | TRES VIAS BANK 2 | 1032502 | Bank | None | None | None | 80.7% | 0 | 0% | 15.8 | 12.34 | 78.1% | 0 | 0% | 15.8 | 12.43 | 78.67% | 0 | 0% | 15.8 | 12.53 | 79.3% | 0 | 0% | 15.8 | 12.63 | 79.94% | 0 | 0% | 15.8 | 12.75 | 80.7% | 0 | 0%
GNA_103251101_Capacity | North Valley and Sierra | North Valley | TRES VIAS 1101 | 103251101 | Feeder | None | None | None | 99.53% | 0 | 0% | 12.83 | 12.36 | 96.34% | 0 | 0% | 12.83 | 12.45 | 97.04% | 0 | 0% | 12.83 | 12.55 | 97.82% | 0 | 0% | 12.83 | 12.64 | 98.52% | 0 | 0% | 12.83 | 12.77 | 99.53% | 0 | 0%
GNA_1028101_Capacity | North Valley and Sierra | North Valley | BIG MEADOWS BANK 1 | 1028101 | Bank | None | None | None | 38.44% | 0 | 0% | 14.1 | 5.37 | 38.09% | 0 | 0% | 14.1 | 5.37 | 38.09% | 0 | 0% | 14.1 | 5.37 | 38.09% | 0 | 0% | 14.1 | 5.4 | 38.3% | 0 | 0% | 14.1 | 5.42 | 38.44% | 0 | 0%
GNA_102812101_Capacity | North Valley and Sierra | North Valley | BIG MEADOWS 2101 | 102812101 | Feeder | None | None | None | 89.5% | 0 | 0% | 6.19 | 5.49 | 88.69% | 0 | 0% | 6.19 | 5.49 | 88.69% | 0 | 0% | 6.19 | 5.49 | 88.69% | 0 | 0% | 6.19 | 5.52 | 89.18% | 0 | 0% | 6.19 | 5.54 | 89.5% | 0 | 0%
GNA_1023602_Capacity | North Valley and Sierra | North Valley | HAMILTON BRANCH BANK 2 | 1023602 | Bank | None | None | None | 46.64% | 0 | 0% | 8.64 | 4.03 | 46.64% | 0 | 0% | 8.64 | 3.96 | 45.83% | 0 | 0% | 8.64 | 3.95 | 45.72% | 0 | 0% | 8.64 | 3.97 | 45.95% | 0 | 0% | 8.64 | 4.01 | 46.41% | 0 | 0%
GNA_102361101_Capacity | North Valley and Sierra | North Valley | HAMILTON BRANCH 1101 | 102361101 | Feeder | None | None | None | 50.18% | 0 | 0% | 8.55 | 4.29 | 50.18% | 0 | 0% | 8.55 | 4.22 | 49.36% | 0 | 0% | 8.55 | 4.2 | 49.12% | 0 | 0% | 8.55 | 4.22 | 49.36% | 0 | 0% | 8.55 | 4.26 | 49.82% | 0 | 0%
GNA_1031001_Capacity | North Valley and Sierra | North Valley | SPANISH CREEK BANK 1 | 1031001 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_103104401_Capacity | North Valley and Sierra | North Valley | SPANISH CREEK 4401 | 103104401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1031301_Capacity | North Valley and Sierra | North Valley | CRESCENT MILLS BANK 1 | 1031301 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_103132101_Capacity | North Valley and Sierra | North Valley | CRESCENT MILLS. 2101 | 103132101 | Feeder | None | None | None | 18.03% | 0 | 0% | 9.26 | 1.52 | 16.41% | 0 | 0% | 9.26 | 1.55 | 16.74% | 0 | 0% | 9.26 | 1.58 | 17.06% | 0 | 0% | 9.26 | 1.59 | 17.17% | 0 | 0% | 9.26 | 1.67 | 18.03% | 0 | 0%
GNA_1034901_Capacity | North Valley and Sierra | North Valley | MC ARTHUR BANK 1 | 1034901 | Bank | None | None | None | 93.62% | 0 | 0% | 8 | 7.44 | 93% | 0 | 0% | 8 | 7.44 | 93% | 0 | 0% | 8 | 7.44 | 93% | 0 | 0% | 8 | 7.45 | 93.12% | 0 | 0% | 8 | 7.49 | 93.62% | 0 | 0%
GNA_103491101_Capacity | North Valley and Sierra | North Valley | MC ARTHUR 1101 | 103491101 | Feeder | None | None | None | 61.99% | 0 | 0% | 8.55 | 5.26 | 61.52% | 0 | 0% | 8.55 | 5.26 | 61.52% | 0 | 0% | 8.55 | 5.26 | 61.52% | 0 | 0% | 8.55 | 5.27 | 61.64% | 0 | 0% | 8.55 | 5.3 | 61.99% | 0 | 0%
GNA_103491102_Capacity | North Valley and Sierra | North Valley | MC ARTHUR 1102 | 103491102 | Feeder | None | None | None | 26.43% | 0 | 0% | 8.55 | 2.25 | 26.32% | 0 | 0% | 8.55 | 2.25 | 26.32% | 0 | 0% | 8.55 | 2.25 | 26.32% | 0 | 0% | 8.55 | 2.25 | 26.32% | 0 | 0% | 8.55 | 2.26 | 26.43% | 0 | 0%
GNA_1037204_Capacity | North Valley and Sierra | North Valley | PIT NO 1 BANK 4 | 1037204 | Bank | None | None | None | 27.22% | 0 | 0% | 11.24 | 3.04 | 27.05% | 0 | 0% | 11.24 | 3.05 | 27.14% | 0 | 0% | 11.24 | 3.06 | 27.22% | 0 | 0% | 11.24 | 3.06 | 27.22% | 0 | 0% | 11.24 | 3.06 | 27.22% | 0 | 0%
GNA_103721101_Capacity | North Valley and Sierra | North Valley | PIT NO 1 1101 | 103721101 | Feeder | None | None | None | 68.37% | 0 | 0% | 4.49 | 3.05 | 67.93% | 0 | 0% | 4.49 | 3.06 | 68.15% | 0 | 0% | 4.49 | 3.07 | 68.37% | 0 | 0% | 4.49 | 3.07 | 68.37% | 0 | 0% | 4.49 | 3.07 | 68.37% | 0 | 0%
GNA_1021101_Capacity | North Valley and Sierra | North Valley | CAPAY BANK 1 | 1021101 | Bank | None | None | None | 100% | 0 | 0% | 9.4 | 9.4 | 100% | 0 | 0% | 9.4 | 9.27 | 98.62% | 0 | 0% | 9.4 | 9.15 | 97.34% | 0 | 0% | 9.4 | 9.03 | 96.06% | 0 | 0% | 9.4 | 8.97 | 95.43% | 0 | 0%
GNA_102111101_Capacity | North Valley and Sierra | North Valley | CAPAY 1101 | 102111101 | Feeder | None | None | None | 91.13% | 0 | 0% | 3.72 | 3.39 | 91.13% | 0 | 0% | 3.72 | 3.32 | 89.25% | 0 | 0% | 3.72 | 3.27 | 87.9% | 0 | 0% | 3.72 | 3.25 | 87.37% | 0 | 0% | 3.72 | 3.26 | 87.63% | 0 | 0%
GNA_102111102_Capacity | North Valley and Sierra | North Valley | CAPAY 1102 | 102111102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1026003_Capacity | North Valley and Sierra | North Valley | GLENN BANK 3 | 1026003 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_102601101_Capacity | North Valley and Sierra | North Valley | GLENN 1101 | 102601101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1021201_Capacity | North Valley and Sierra | North Valley | HAMILTON A BANK 1 | 1021201 | Bank | None | None | None | 98.64% | 0 | 0% | 8.1 | 7.99 | 98.64% | 0 | 0% | 8.1 | 7.97 | 98.4% | 0 | 0% | 8.1 | 7.97 | 98.4% | 0 | 0% | 8.1 | 7.97 | 98.4% | 0 | 0% | 8.1 | 7.98 | 98.52% | 0 | 0%
GNA_102121101_Capacity | North Valley and Sierra | North Valley | HAMILTON A 1101 | 102121101 | Feeder | None | None | None | 83.91% | 0 | 0% | 6.09 | 5.11 | 83.91% | 0 | 0% | 6.09 | 5.1 | 83.74% | 0 | 0% | 6.09 | 5.11 | 83.91% | 0 | 0% | 6.09 | 5.1 | 83.74% | 0 | 0% | 6.09 | 5.11 | 83.91% | 0 | 0%
GNA_102121102_Capacity | North Valley and Sierra | North Valley | HAMILTON A 1102 | 102121102 | Feeder | None | None | None | 59.11% | 0 | 0% | 6.09 | 3.6 | 59.11% | 0 | 0% | 6.09 | 3.59 | 58.95% | 0 | 0% | 6.09 | 3.59 | 58.95% | 0 | 0% | 6.09 | 3.59 | 58.95% | 0 | 0% | 6.09 | 3.59 | 58.95% | 0 | 0%
GNA_1027001_Capacity | North Valley and Sierra | North Valley | ORLAND B BANK 1 | 1027001 | Bank | Demand Growth | Capacity | 2025 | 106.2% | 0.7 | 6.228% | 11.24 | 11.01 | 97.95% | 0 | 0% | 11.24 | 11.29 | 100.4% | 0.05 | 0.4448% | 11.24 | 11.48 | 102.1% | 0.24 | 2.135% | 11.24 | 11.7 | 104.1% | 0.46 | 4.093% | 11.24 | 11.94 | 106.2% | 0.7 | 6.228%
GNA_102701101_Capacity | North Valley and Sierra | North Valley | ORLAND B 1101 | 102701101 | Feeder | None | None | None | 72.86% | 0 | 0% | 7.48 | 4.9 | 65.51% | 0 | 0% | 7.48 | 5.11 | 68.32% | 0 | 0% | 7.48 | 5.21 | 69.65% | 0 | 0% | 7.48 | 5.32 | 71.12% | 0 | 0% | 7.48 | 5.45 | 72.86% | 0 | 0%
GNA_102701102_Capacity | North Valley and Sierra | North Valley | ORLAND B 1102 | 102701102 | Feeder | None | None | None | 62.99% | 0 | 0% | 10.16 | 5.98 | 58.86% | 0 | 0% | 10.16 | 6.08 | 59.84% | 0 | 0% | 10.16 | 6.17 | 60.73% | 0 | 0% | 10.16 | 6.28 | 61.81% | 0 | 0% | 10.16 | 6.4 | 62.99% | 0 | 0%
GNA_1027002_Capacity | North Valley and Sierra | North Valley | ORLAND B BANK 2 | 1027002 | Bank | None | None | None | 95.23% | 0 | 0% | 12.38 | 11.72 | 94.67% | 0 | 0% | 12.38 | 11.7 | 94.51% | 0 | 0% | 12.38 | 11.7 | 94.51% | 0 | 0% | 12.38 | 11.72 | 94.67% | 0 | 0% | 12.38 | 11.79 | 95.23% | 0 | 0%
GNA_102701103_Capacity | North Valley and Sierra | North Valley | ORLAND B 1103 | 102701103 | Feeder | None | None | None | 94.67% | 0 | 0% | 12.19 | 11.48 | 94.18% | 0 | 0% | 12.19 | 11.46 | 94.01% | 0 | 0% | 12.19 | 11.45 | 93.93% | 0 | 0% | 12.19 | 11.48 | 94.18% | 0 | 0% | 12.19 | 11.54 | 94.67% | 0 | 0%
GNA_1031901_Capacity | North Valley and Sierra | North Valley | BANGOR BANK 1 | 1031901 | Bank | None | None | None | 58.01% | 0 | 0% | 12.36 | 7.09 | 57.36% | 0 | 0% | 12.36 | 7.11 | 57.52% | 0 | 0% | 12.36 | 7.12 | 57.61% | 0 | 0% | 12.36 | 7.16 | 57.93% | 0 | 0% | 12.36 | 7.17 | 58.01% | 0 | 0%
GNA_103191101_Capacity | North Valley and Sierra | North Valley | BANGOR 1101 | 103191101 | Feeder | None | None | None | 91.23% | 0 | 0% | 8.55 | 7.8 | 91.23% | 0 | 0% | 12.83 | 7.82 | 60.95% | 0 | 0% | 12.83 | 7.83 | 61.03% | 0 | 0% | 12.83 | 7.87 | 61.34% | 0 | 0% | 12.83 | 7.88 | 61.42% | 0 | 0%
GNA_1032001_Capacity | North Valley and Sierra | North Valley | CHALLENGE BANK 1 | 1032001 | Bank | None | None | None | 87.23% | 0 | 0% | 2.82 | 2.45 | 86.88% | 0 | 0% | 2.82 | 2.45 | 86.88% | 0 | 0% | 2.82 | 2.45 | 86.88% | 0 | 0% | 2.82 | 2.45 | 86.88% | 0 | 0% | 2.82 | 2.46 | 87.23% | 0 | 0%
GNA_103201101_Capacity | North Valley and Sierra | North Valley | CHALLENGE 1101 | 103201101 | Feeder | None | None | None | 45.45% | 0 | 0% | 2.97 | 1.33 | 44.78% | 0 | 0% | 2.97 | 1.33 | 44.78% | 0 | 0% | 2.97 | 1.34 | 45.12% | 0 | 0% | 2.97 | 1.34 | 45.12% | 0 | 0% | 2.97 | 1.35 | 45.45% | 0 | 0%
GNA_103201102_Capacity | North Valley and Sierra | North Valley | CHALLENGE 1102 | 103201102 | Feeder | None | None | None | 45.32% | 0 | 0% | 4.06 | 1.84 | 45.32% | 0 | 0% | 4.06 | 1.84 | 45.32% | 0 | 0% | 4.06 | 1.83 | 45.07% | 0 | 0% | 4.06 | 1.83 | 45.07% | 0 | 0% | 4.06 | 1.83 | 45.07% | 0 | 0%
GNA_1032201_Capacity | North Valley and Sierra | North Valley | KANAKA BANK 1 | 1032201 | Bank | None | None | None | 38.19% | 0 | 0% | 3.09 | 1.18 | 38.19% | 0 | 0% | 3.09 | 1.16 | 37.54% | 0 | 0% | 3.09 | 1.16 | 37.54% | 0 | 0% | 3.09 | 1.14 | 36.89% | 0 | 0% | 3.09 | 1.13 | 36.57% | 0 | 0%
GNA_103221101_Capacity | North Valley and Sierra | North Valley | KANAKA 1101 | 103221101 | Feeder | None | None | None | 41.03% | 0 | 0% | 3.12 | 1.28 | 41.03% | 0 | 0% | 3.12 | 1.27 | 40.71% | 0 | 0% | 3.12 | 1.26 | 40.38% | 0 | 0% | 3.12 | 1.25 | 40.06% | 0 | 0% | 3.12 | 1.24 | 39.74% | 0 | 0%
GNA_1025202_Capacity | North Valley and Sierra | North Valley | OROVILLE BANK 2 | 1025202 | Bank | None | None | None | 98.8% | 0 | 0% | 15.84 | 15.56 | 98.23% | 0 | 0% | 15.84 | 15.65 | 98.8% | 0 | 0% | 15.84 | 15.21 | 96.02% | 0 | 0% | 15.84 | 15.32 | 96.72% | 0 | 0% | 15.84 | 15.51 | 97.92% | 0 | 0%
GNA_102521101_Capacity | North Valley and Sierra | North Valley | OROVILLE 1101 | 102521101 | Feeder | Demand Growth | Capacity | 2023 | 119.9% | 1.62 | 19.93% | 8.13 | 9.66 | 118.8% | 1.53 | 18.82% | 8.13 | 9.75 | 119.9% | 1.62 | 19.93% | 8.13 | 9.29 | 114.3% | 1.16 | 14.27% | 8.13 | 9.41 | 115.7% | 1.28 | 15.74% | 8.13 | 9.57 | 117.7% | 1.44 | 17.71%
GNA_102521102_Capacity | North Valley and Sierra | North Valley | OROVILLE 1102 | 102521102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1025203_Capacity | North Valley and Sierra | North Valley | OROVILLE BANK 3 | 1025203 | Bank | Demand Growth | Capacity | 2025 | 107.9% | 0.73 | 7.866% | 9.28 | 9.04 | 97.41% | 0 | 0% | 9.28 | 9.12 | 98.28% | 0 | 0% | 9.28 | 9.77 | 105.3% | 0.49 | 5.28% | 9.28 | 9.88 | 106.5% | 0.6 | 6.466% | 9.28 | 10.01 | 107.9% | 0.73 | 7.866%
GNA_102521103_Capacity | North Valley and Sierra | North Valley | OROVILLE 1103 | 102521103 | Feeder | None | None | None | 32.89% | 0 | 0% | 10.46 | 2.92 | 27.92% | 0 | 0% | 10.46 | 2.9 | 27.72% | 0 | 0% | 10.46 | 3.44 | 32.89% | 0 | 0% | 10.46 | 3.44 | 32.89% | 0 | 0% | 10.46 | 3.44 | 32.89% | 0 | 0%
GNA_102521104_Capacity | North Valley and Sierra | North Valley | OROVILLE 1104 | 102521104 | Feeder | None | None | None | 67.33% | 0 | 0% | 9.58 | 6.05 | 63.15% | 0 | 0% | 9.58 | 6.14 | 64.09% | 0 | 0% | 9.58 | 6.23 | 65.03% | 0 | 0% | 9.58 | 6.33 | 66.08% | 0 | 0% | 9.58 | 6.45 | 67.33% | 0 | 0%
GNA_1029101_Capacity | North Valley and Sierra | North Valley | WYANDOTTE BANK 1 | 1029101 | Bank | None | None | None | 54.82% | 0 | 0% | 44.6 | 24.36 | 54.62% | 0 | 0% | 44.6 | 24.45 | 54.82% | 0 | 0% | 44.6 | 24.11 | 54.06% | 0 | 0% | 44.6 | 24.22 | 54.3% | 0 | 0% | 44.6 | 24.41 | 54.73% | 0 | 0%
GNA_102911102_Capacity | North Valley and Sierra | North Valley | WYANDOTTE 1102 | 102911102 | Feeder | None | None | None | 99.22% | 0 | 0% | 12.83 | 12.71 | 99.06% | 0 | 0% | 12.83 | 12.7 | 98.99% | 0 | 0% | 12.83 | 12.69 | 98.91% | 0 | 0% | 12.83 | 12.69 | 98.91% | 0 | 0% | 12.83 | 12.73 | 99.22% | 0 | 0%
GNA_102911103_Capacity | North Valley and Sierra | North Valley | WYANDOTTE 1103 | 102911103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1029102_Capacity | North Valley and Sierra | North Valley | WYANDOTTE BANK 2 | 1029102 | Bank | None | None | None | 48.68% | 0 | 0% | 29.5 | 13.89 | 47.08% | 0 | 0% | 29.5 | 13.97 | 47.36% | 0 | 0% | 29.5 | 14.08 | 47.73% | 0 | 0% | 29.5 | 14.2 | 48.14% | 0 | 0% | 29.5 | 14.36 | 48.68% | 0 | 0%
GNA_102911105_Capacity | North Valley and Sierra | North Valley | WYANDOTTE 1105 | 102911105 | Feeder | None | None | None | 41.15% | 0 | 0% | 7.63 | 3.11 | 40.76% | 0 | 0% | 7.63 | 3.1 | 40.63% | 0 | 0% | 7.63 | 3.12 | 40.89% | 0 | 0% | 7.63 | 3.13 | 41.02% | 0 | 0% | 7.63 | 3.14 | 41.15% | 0 | 0%
GNA_103751101_Capacity | North Valley and Sierra | North Valley | BIG BEND 1101 | 103751101 | Feeder | None | None | None | 23.02% | 0 | 0% | 3.91 | 0.9 | 23.02% | 0 | 0% | 3.91 | 0.9 | 23.02% | 0 | 0% | 3.91 | 0.9 | 23.02% | 0 | 0% | 3.91 | 0.9 | 23.02% | 0 | 0% | 3.91 | 0.9 | 23.02% | 0 | 0%
GNA_103751102_Capacity | North Valley and Sierra | North Valley | BIG BEND 1102 | 103751102 | Feeder | None | None | None | 22% | 0 | 0% | 2.5 | 0.55 | 22% | 0 | 0% | 2.5 | 0.55 | 22% | 0 | 0% | 2.5 | 0.55 | 22% | 0 | 0% | 2.5 | 0.55 | 22% | 0 | 0% | 2.5 | 0.55 | 22% | 0 | 0%
GNA_102911106_Capacity | North Valley and Sierra | North Valley | WYANDOTTE 1106 | 102911106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1029103_Capacity | North Valley and Sierra | North Valley | WYANDOTTE BANK 3 | 1029103 | Bank | None | None | None | 73.95% | 0 | 0% | 44.6 | 31.45 | 70.52% | 0 | 0% | 44.6 | 31.56 | 70.76% | 0 | 0% | 44.6 | 32.14 | 72.06% | 0 | 0% | 44.6 | 32.44 | 72.74% | 0 | 0% | 44.6 | 32.98 | 73.95% | 0 | 0%
GNA_102911107_Capacity | North Valley and Sierra | North Valley | WYANDOTTE 1107 | 102911107 | Feeder | None | None | None | 87.43% | 0 | 0% | 12.25 | 10.06 | 82.12% | 0 | 0% | 12.25 | 10.05 | 82.04% | 0 | 0% | 12.25 | 10.48 | 85.55% | 0 | 0% | 12.25 | 10.52 | 85.88% | 0 | 0% | 12.25 | 10.71 | 87.43% | 0 | 0%
GNA_102911109_Capacity | North Valley and Sierra | North Valley | WYANDOTTE 1109 | 102911109 | Feeder | None | None | None | 95.95% | 0 | 0% | 12.83 | 11.86 | 92.44% | 0 | 0% | 12.83 | 11.92 | 92.91% | 0 | 0% | 12.83 | 12.01 | 93.61% | 0 | 0% | 12.83 | 12.12 | 94.47% | 0 | 0% | 12.83 | 12.31 | 95.95% | 0 | 0%
GNA_102911110_Capacity | North Valley and Sierra | North Valley | WYANDOTTE 1110 | 102911110 | Feeder | None | None | None | 91.66% | 0 | 0% | 12.83 | 11.46 | 89.32% | 0 | 0% | 12.83 | 11.47 | 89.4% | 0 | 0% | 12.83 | 11.51 | 89.71% | 0 | 0% | 12.83 | 11.61 | 90.49% | 0 | 0% | 12.83 | 11.76 | 91.66% | 0 | 0%
GNA_1025201_Capacity | North Valley and Sierra | North Valley | OROVILLE BANK 1 | 1025201 | Bank | None | None | None | 34.96% | 0 | 0% | 4.52 | 1.58 | 34.96% | 0 | 0% | 4.52 | 1.56 | 34.51% | 0 | 0% | 4.52 | 1.58 | 34.96% | 0 | 0% | 4.52 | 1.57 | 34.73% | 0 | 0% | 4.52 | 1.55 | 34.29% | 0 | 0%
GNA_102520402_Capacity | North Valley and Sierra | North Valley | OROVILLE 0402 | 102520402 | Feeder | None | None | None | 75.79% | 0 | 0% | 1.9 | 1.44 | 75.79% | 0 | 0% | 1.9 | 1.43 | 75.26% | 0 | 0% | 1.9 | 1.44 | 75.79% | 0 | 0% | 1.9 | 1.44 | 75.79% | 0 | 0% | 1.9 | 1.43 | 75.26% | 0 | 0%
GNA_102520403_Capacity | North Valley and Sierra | North Valley | OROVILLE 0403 | 102520403 | Feeder | None | None | None | 47.37% | 0 | 0% | 1.9 | 0.88 | 46.32% | 0 | 0% | 1.9 | 0.88 | 46.32% | 0 | 0% | 1.9 | 0.89 | 46.84% | 0 | 0% | 1.9 | 0.9 | 47.37% | 0 | 0% | 1.9 | 0.9 | 47.37% | 0 | 0%
GNA_1030301_Capacity | North Valley and Sierra | North Valley | ORO FINO BANK 1 | 1030301 | Bank | None | None | None | 74.38% | 0 | 0% | 12.92 | 9.46 | 73.22% | 0 | 0% | 12.92 | 9.39 | 72.68% | 0 | 0% | 12.92 | 9.42 | 72.91% | 0 | 0% | 12.92 | 9.48 | 73.37% | 0 | 0% | 12.92 | 9.61 | 74.38% | 0 | 0%
GNA_103031101_Capacity | North Valley and Sierra | North Valley | ORO FINO 1101 | 103031101 | Feeder | None | None | None | 46.59% | 0 | 0% | 10.69 | 4.98 | 46.59% | 0 | 0% | 10.69 | 4.91 | 45.93% | 0 | 0% | 10.69 | 4.87 | 45.56% | 0 | 0% | 10.69 | 4.82 | 45.09% | 0 | 0% | 10.69 | 4.8 | 44.9% | 0 | 0%
GNA_103031102_Capacity | North Valley and Sierra | North Valley | ORO FINO 1102 | 103031102 | Feeder | None | None | None | 45.04% | 0 | 0% | 10.28 | 4.44 | 43.19% | 0 | 0% | 10.28 | 4.45 | 43.29% | 0 | 0% | 10.28 | 4.46 | 43.39% | 0 | 0% | 10.28 | 4.52 | 43.97% | 0 | 0% | 10.28 | 4.63 | 45.04% | 0 | 0%
GNA_1028301_Capacity | North Valley and Sierra | North Valley | PARADISE BANK 1 | 1028301 | Bank | None | None | None | 20.74% | 0 | 0% | 44.6 | 7.68 | 17.22% | 0 | 0% | 44.6 | 8.46 | 18.97% | 0 | 0% | 44.6 | 9.25 | 20.74% | 0 | 0% | 44.6 | 9.24 | 20.72% | 0 | 0% | 44.6 | 9.24 | 20.72% | 0 | 0%
GNA_102831106_Capacity | North Valley and Sierra | North Valley | PARADISE 1106 | 102831106 | Feeder | None | None | None | 82.44% | 0 | 0% | 12.19 | 8.49 | 69.65% | 0 | 0% | 12.19 | 9.27 | 76.05% | 0 | 0% | 12.19 | 10.05 | 82.44% | 0 | 0% | 12.19 | 10.05 | 82.44% | 0 | 0% | 12.19 | 10.04 | 82.36% | 0 | 0%
GNA_1028302_Capacity | North Valley and Sierra | North Valley | PARADISE BANK 2 | 1028302 | Bank | None | None | None | 47.87% | 0 | 0% | 44.6 | 15.67 | 35.13% | 0 | 0% | 44.6 | 18.93 | 42.44% | 0 | 0% | 44.6 | 21.35 | 47.87% | 0 | 0% | 44.6 | 21.25 | 47.65% | 0 | 0% | 44.6 | 21.15 | 47.42% | 0 | 0%
GNA_102831103_Capacity | North Valley and Sierra | North Valley | PARADISE 1103 | 102831103 | Feeder | None | None | None | 84% | 0 | 0% | 12.19 | 8.21 | 67.35% | 0 | 0% | 12.19 | 9.22 | 75.64% | 0 | 0% | 12.19 | 10.24 | 84% | 0 | 0% | 12.19 | 10.22 | 83.84% | 0 | 0% | 12.19 | 10.21 | 83.76% | 0 | 0%
GNA_102831104_Capacity | North Valley and Sierra | North Valley | PARADISE 1104 | 102831104 | Feeder | None | None | None | 78.96% | 0 | 0% | 13.21 | 8.31 | 62.91% | 0 | 0% | 13.21 | 9.81 | 74.26% | 0 | 0% | 13.21 | 10.43 | 78.96% | 0 | 0% | 13.21 | 10.38 | 78.58% | 0 | 0% | 13.21 | 10.37 | 78.5% | 0 | 0%
GNA_102831105_Capacity | North Valley and Sierra | North Valley | PARADISE 1105 | 102831105 | Feeder | None | None | None | 34.78% | 0 | 0% | 12.19 | 2.83 | 23.22% | 0 | 0% | 12.19 | 3.53 | 28.96% | 0 | 0% | 12.19 | 4.24 | 34.78% | 0 | 0% | 12.19 | 4.2 | 34.45% | 0 | 0% | 12.19 | 4.13 | 33.88% | 0 | 0%
GNA_1037302_Capacity | North Valley and Sierra | North Valley | PIT NO 3 BANK 2 | 1037302 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_103732101_Capacity | North Valley and Sierra | North Valley | PIT NO 3 2101 | 103732101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1013205_Capacity | North Valley and Sierra | North Valley | PIT NO 5 BANK 5 | 1013205 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_101321101_Capacity | North Valley and Sierra | North Valley | PIT NO 5 1101 | 101321101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1025501_Capacity | North Valley and Sierra | North Valley | EAST QUINCY BANK 1 | 1025501 | Bank | None | None | None | 55.78% | 0 | 0% | 6.06 | 3.38 | 55.78% | 0 | 0% | 6.06 | 3.29 | 54.29% | 0 | 0% | 6.06 | 3.2 | 52.81% | 0 | 0% | 6.06 | 3.21 | 52.97% | 0 | 0% | 6.06 | 3.26 | 53.8% | 0 | 0%
GNA_102551101_Capacity | North Valley and Sierra | North Valley | EAST QUINCY 1101 | 102551101 | Feeder | None | None | None | 48.51% | 0 | 0% | 7.36 | 3.57 | 48.51% | 0 | 0% | 7.36 | 3.48 | 47.28% | 0 | 0% | 7.36 | 3.38 | 45.92% | 0 | 0% | 7.36 | 3.38 | 45.92% | 0 | 0% | 7.36 | 3.43 | 46.6% | 0 | 0%
GNA_1030201_Capacity | North Valley and Sierra | North Valley | GANSNER BANK 1 | 1030201 | Bank | None | None | None | 27.33% | 0 | 0% | 10.5 | 2.87 | 27.33% | 0 | 0% | 10.5 | 2.78 | 26.48% | 0 | 0% | 10.5 | 2.72 | 25.9% | 0 | 0% | 10.5 | 2.73 | 26% | 0 | 0% | 10.5 | 2.77 | 26.38% | 0 | 0%
GNA_103021101_Capacity | North Valley and Sierra | North Valley | GANSNER 1101 | 103021101 | Feeder | None | None | None | 38.24% | 0 | 0% | 7.48 | 2.86 | 38.24% | 0 | 0% | 7.48 | 2.76 | 36.9% | 0 | 0% | 7.48 | 2.7 | 36.1% | 0 | 0% | 7.48 | 2.72 | 36.36% | 0 | 0% | 7.48 | 2.76 | 36.9% | 0 | 0%
GNA_1033401_Capacity | North Valley and Sierra | North Valley | DAIRYVILLE BANK 1 | 1033401 | Bank | None | None | None | 81.56% | 0 | 0% | 4.23 | 3.44 | 81.32% | 0 | 0% | 4.23 | 3.43 | 81.09% | 0 | 0% | 4.23 | 3.42 | 80.85% | 0 | 0% | 4.23 | 3.42 | 80.85% | 0 | 0% | 4.23 | 3.45 | 81.56% | 0 | 0%
GNA_103341101_Capacity | North Valley and Sierra | North Valley | DAIRYVILLE 1101 | 103341101 | Feeder | None | None | None | 49.77% | 0 | 0% | 6.41 | 3.18 | 49.61% | 0 | 0% | 6.41 | 3.17 | 49.45% | 0 | 0% | 6.41 | 3.16 | 49.3% | 0 | 0% | 6.41 | 3.16 | 49.3% | 0 | 0% | 6.41 | 3.19 | 49.77% | 0 | 0%
GNA_1035301_Capacity | North Valley and Sierra | North Valley | RAWSON BANK 1 | 1035301 | Bank | None | None | None | 80.73% | 0 | 0% | 14.84 | 11.02 | 74.26% | 0 | 0% | 14.84 | 10.97 | 73.92% | 0 | 0% | 14.84 | 11.98 | 80.73% | 0 | 0% | 14.84 | 11.95 | 80.53% | 0 | 0% | 14.84 | 11.96 | 80.59% | 0 | 0%
GNA_103531103_Capacity | North Valley and Sierra | North Valley | RAWSON 1103 | 103531103 | Feeder | None | None | None | 97.43% | 0 | 0% | 12.83 | 11.54 | 89.95% | 0 | 0% | 12.83 | 11.49 | 89.56% | 0 | 0% | 12.83 | 12.5 | 97.43% | 0 | 0% | 12.83 | 12.47 | 97.19% | 0 | 0% | 12.83 | 12.48 | 97.27% | 0 | 0%
GNA_1035401_Capacity | North Valley and Sierra | North Valley | RED BLUFF BANK 1 | 1035401 | Bank | None | None | None | 57.81% | 0 | 0% | 29.7 | 16.21 | 54.58% | 0 | 0% | 29.7 | 16.39 | 55.19% | 0 | 0% | 29.7 | 16.58 | 55.82% | 0 | 0% | 29.7 | 16.85 | 56.73% | 0 | 0% | 29.7 | 17.17 | 57.81% | 0 | 0%
GNA_103541103_Capacity | North Valley and Sierra | North Valley | RED BLUFF 1103 | 103541103 | Feeder | None | None | None | 96.94% | 0 | 0% | 10.46 | 9.8 | 93.69% | 0 | 0% | 10.46 | 9.87 | 94.36% | 0 | 0% | 10.46 | 9.93 | 94.93% | 0 | 0% | 10.46 | 10.04 | 95.98% | 0 | 0% | 10.46 | 10.14 | 96.94% | 0 | 0%
GNA_103541104_Capacity | North Valley and Sierra | North Valley | RED BLUFF 1104 | 103541104 | Feeder | None | None | None | 68.07% | 0 | 0% | 10.46 | 6.62 | 63.29% | 0 | 0% | 10.46 | 6.71 | 64.15% | 0 | 0% | 10.46 | 6.81 | 65.11% | 0 | 0% | 10.46 | 6.94 | 66.35% | 0 | 0% | 10.46 | 7.12 | 68.07% | 0 | 0%
GNA_1035402_Capacity | North Valley and Sierra | North Valley | RED BLUFF BANK 2 | 1035402 | Bank | None | None | None | 100.1% | 0.01 | 0.09615% | 10.4 | 10.3 | 99.04% | 0 | 0% | 10.4 | 10.41 | 100.1% | 0.01 | 0.09615% | 10.4 | 9.46 | 90.96% | 0 | 0% | 10.4 | 10.21 | 98.17% | 0 | 0% | 10.4 | 10.39 | 99.9% | 0 | 0%
GNA_103541105_Capacity | North Valley and Sierra | North Valley | RED BLUFF 1105 | 103541105 | Feeder | None | None | None | 89.56% | 0 | 0% | 11.4 | 10.1 | 88.6% | 0 | 0% | 11.4 | 10.21 | 89.56% | 0 | 0% | 11.4 | 9.27 | 81.32% | 0 | 0% | 11.4 | 10.02 | 87.89% | 0 | 0% | 11.4 | 10.19 | 89.39% | 0 | 0%
GNA_1035403_Capacity | North Valley and Sierra | North Valley | RED BLUFF BANK 3 | 1035403 | Bank | None | None | None | 98.41% | 0 | 0% | 8.82 | 8.43 | 95.58% | 0 | 0% | 8.82 | 8.54 | 96.83% | 0 | 0% | 8.82 | 8.68 | 98.41% | 0 | 0% | 8.82 | 8.24 | 93.42% | 0 | 0% | 8.82 | 8.42 | 95.46% | 0 | 0%
GNA_103541101_Capacity | North Valley and Sierra | North Valley | RED BLUFF 1101 | 103541101 | Feeder | None | None | None | 68.55% | 0 | 0% | 10.46 | 6.6 | 63.1% | 0 | 0% | 10.46 | 6.71 | 64.15% | 0 | 0% | 10.46 | 6.84 | 65.39% | 0 | 0% | 10.46 | 7 | 66.92% | 0 | 0% | 10.46 | 7.17 | 68.55% | 0 | 0%
GNA_103541102_Capacity | North Valley and Sierra | North Valley | RED BLUFF 1102 | 103541102 | Feeder | None | None | None | 21.7% | 0 | 0% | 10.46 | 2.27 | 21.7% | 0 | 0% | 10.46 | 2.26 | 21.61% | 0 | 0% | 10.46 | 2.25 | 21.51% | 0 | 0% | 10.46 | 1.65 | 15.77% | 0 | 0% | 10.46 | 1.63 | 15.58% | 0 | 0%
GNA_1035701_Capacity | North Valley and Sierra | North Valley | TYLER BANK 1 | 1035701 | Bank | Demand Growth | Capacity | 2025 | 259.8% | 14.37 | 159.8% | 8.99 | 8.48 | 94.33% | 0 | 0% | 8.99 | 8.58 | 95.44% | 0 | 0% | 8.99 | 23.23 | 258.4% | 14.24 | 158.4% | 8.99 | 23.29 | 259.1% | 14.3 | 159.1% | 8.99 | 23.36 | 259.8% | 14.37 | 159.8%
GNA_103571103_Capacity | North Valley and Sierra | North Valley | TYLER 1103 | 103571103 | Feeder | Demand Growth | Capacity | 2025 | 107.8% | 0.79 | 7.776% | 10.16 | 3.66 | 36.02% | 0 | 0% | 10.16 | 3.74 | 36.81% | 0 | 0% | 10.16 | 10.91 | 107.4% | 0.75 | 7.382% | 10.16 | 10.93 | 107.6% | 0.77 | 7.579% | 10.16 | 10.95 | 107.8% | 0.79 | 7.776%
GNA_103571104_Capacity | North Valley and Sierra | North Valley | TYLER 1104 | 103571104 | Feeder | Demand Growth | Capacity | 2025 | 121.6% | 2.26 | 21.61% | 10.46 | 5.62 | 53.73% | 0 | 0% | 10.46 | 5.64 | 53.92% | 0 | 0% | 10.46 | 12.68 | 121.2% | 2.22 | 21.22% | 10.46 | 12.69 | 121.3% | 2.23 | 21.32% | 10.46 | 12.72 | 121.6% | 2.26 | 21.61%
GNA_1035702_Capacity | North Valley and Sierra | North Valley | TYLER BANK 2 | 1035702 | Bank | None | None | None | 63.55% | 0 | 0% | 15.28 | 9.31 | 60.93% | 0 | 0% | 15.28 | 9.38 | 61.39% | 0 | 0% | 15.28 | 9.47 | 61.98% | 0 | 0% | 15.28 | 9.59 | 62.76% | 0 | 0% | 15.28 | 9.71 | 63.55% | 0 | 0%
GNA_103571105_Capacity | North Valley and Sierra | North Valley | TYLER 1105 | 103571105 | Feeder | None | None | None | 92.93% | 0 | 0% | 10.46 | 9.32 | 89.1% | 0 | 0% | 10.46 | 9.39 | 89.77% | 0 | 0% | 10.46 | 9.48 | 90.63% | 0 | 0% | 10.46 | 9.6 | 91.78% | 0 | 0% | 10.46 | 9.72 | 92.93% | 0 | 0%
GNA_1032601_Capacity | North Valley and Sierra | North Valley | ANDERSON BANK 1 | 1032601 | Bank | None | None | None | 54.18% | 0 | 0% | 29.7 | 15.74 | 53% | 0 | 0% | 29.7 | 15.89 | 53.5% | 0 | 0% | 29.7 | 16.09 | 54.18% | 0 | 0% | 29.7 | 15.6 | 52.53% | 0 | 0% | 29.7 | 15.89 | 53.5% | 0 | 0%
GNA_103261101_Capacity | North Valley and Sierra | North Valley | ANDERSON 1101 | 103261101 | Feeder | None | None | None | 77.26% | 0 | 0% | 9.41 | 7.16 | 76.09% | 0 | 0% | 9.41 | 7.21 | 76.62% | 0 | 0% | 9.41 | 7.27 | 77.26% | 0 | 0% | 9.41 | 6.59 | 70.03% | 0 | 0% | 9.41 | 6.69 | 71.09% | 0 | 0%
GNA_103261102_Capacity | North Valley and Sierra | North Valley | ANDERSON 1102 | 103261102 | Feeder | None | None | None | 57.9% | 0 | 0% | 10.76 | 5.97 | 55.48% | 0 | 0% | 10.76 | 6.05 | 56.23% | 0 | 0% | 10.76 | 6.11 | 56.78% | 0 | 0% | 10.76 | 6.17 | 57.34% | 0 | 0% | 10.76 | 6.23 | 57.9% | 0 | 0%
GNA_103261103_Capacity | North Valley and Sierra | North Valley | ANDERSON 1103 | 103261103 | Feeder | None | None | None | 42.94% | 0 | 0% | 9.92 | 3.83 | 38.61% | 0 | 0% | 9.92 | 3.93 | 39.62% | 0 | 0% | 9.92 | 4.03 | 40.63% | 0 | 0% | 9.92 | 4.14 | 41.73% | 0 | 0% | 9.92 | 4.26 | 42.94% | 0 | 0%
GNA_1029306_Capacity | North Valley and Sierra | North Valley | COTTONWOOD BANK 6 | 1029306 | Bank | None | None | None | 50.51% | 0 | 0% | 29.7 | 13.98 | 47.07% | 0 | 0% | 29.7 | 13.98 | 47.07% | 0 | 0% | 29.7 | 13.99 | 47.1% | 0 | 0% | 29.7 | 14.85 | 50% | 0 | 0% | 29.7 | 15 | 50.51% | 0 | 0%
GNA_102931101_Capacity | North Valley and Sierra | North Valley | COTTONWOOD 1101 | 102931101 | Feeder | None | None | None | 82.78% | 0 | 0% | 7.78 | 6.37 | 81.88% | 0 | 0% | 7.78 | 6.36 | 81.75% | 0 | 0% | 7.78 | 6.36 | 81.75% | 0 | 0% | 7.78 | 6.37 | 81.88% | 0 | 0% | 7.78 | 6.44 | 82.78% | 0 | 0%
GNA_102931102_Capacity | North Valley and Sierra | North Valley | COTTONWOOD 1102 | 102931102 | Feeder | None | None | None | 83.2% | 0 | 0% | 11.01 | 8.25 | 74.93% | 0 | 0% | 11.01 | 8.25 | 74.93% | 0 | 0% | 11.01 | 8.25 | 74.93% | 0 | 0% | 11.01 | 9.08 | 82.47% | 0 | 0% | 11.01 | 9.16 | 83.2% | 0 | 0%
GNA_1029308_Capacity | North Valley and Sierra | North Valley | COTTONWOOD BANK 8 | 1029308 | Bank | None | None | None | 27.69% | 0 | 0% | 44.5 | 12.17 | 27.35% | 0 | 0% | 44.5 | 12.14 | 27.28% | 0 | 0% | 44.5 | 12.15 | 27.3% | 0 | 0% | 44.5 | 12.22 | 27.46% | 0 | 0% | 44.5 | 12.32 | 27.69% | 0 | 0%
GNA_102931103_Capacity | North Valley and Sierra | North Valley | COTTONWOOD 1103 | 102931103 | Feeder | None | None | None | 82.61% | 0 | 0% | 15.12 | 12.34 | 81.61% | 0 | 0% | 15.12 | 12.31 | 81.42% | 0 | 0% | 15.12 | 12.32 | 81.48% | 0 | 0% | 15.12 | 12.38 | 81.88% | 0 | 0% | 15.12 | 12.49 | 82.61% | 0 | 0%
GNA_1033501_Capacity | North Valley and Sierra | North Valley | DESCHUTES BANK 1 | 1033501 | Bank | None | None | None | 42.73% | 0 | 0% | 12.31 | 5.26 | 42.73% | 0 | 0% | 12.31 | 5.24 | 42.57% | 0 | 0% | 12.31 | 5.24 | 42.57% | 0 | 0% | 12.31 | 5.25 | 42.65% | 0 | 0% | 12.31 | 5.25 | 42.65% | 0 | 0%
GNA_103351101_Capacity | North Valley and Sierra | North Valley | DESCHUTES 1101 | 103351101 | Feeder | None | None | None | 42.25% | 0 | 0% | 12.19 | 5.15 | 42.25% | 0 | 0% | 12.19 | 5.13 | 42.08% | 0 | 0% | 12.19 | 5.12 | 42% | 0 | 0% | 12.19 | 5.14 | 42.17% | 0 | 0% | 12.19 | 5.14 | 42.17% | 0 | 0%
GNA_1033502_Capacity | North Valley and Sierra | North Valley | DESCHUTES BANK 2 | 1033502 | Bank | None | None | None | 35.89% | 0 | 0% | 29.7 | 10.61 | 35.72% | 0 | 0% | 29.7 | 10.6 | 35.69% | 0 | 0% | 29.7 | 10.61 | 35.72% | 0 | 0% | 29.7 | 10.62 | 35.76% | 0 | 0% | 29.7 | 10.66 | 35.89% | 0 | 0%
GNA_103351104_Capacity | North Valley and Sierra | North Valley | DESCHUTES 1104 | 103351104 | Feeder | None | None | None | 85.5% | 0 | 0% | 12.83 | 10.92 | 85.11% | 0 | 0% | 12.83 | 10.92 | 85.11% | 0 | 0% | 12.83 | 10.93 | 85.19% | 0 | 0% | 12.83 | 10.93 | 85.19% | 0 | 0% | 12.83 | 10.97 | 85.5% | 0 | 0%
GNA_1034001_Capacity | North Valley and Sierra | North Valley | GIRVAN BANK 1 | 1034001 | Bank | None | None | None | 84.43% | 0 | 0% | 15.8 | 12.02 | 76.08% | 0 | 0% | 15.8 | 12.29 | 77.78% | 0 | 0% | 15.8 | 12.52 | 79.24% | 0 | 0% | 15.8 | 12.91 | 81.71% | 0 | 0% | 15.8 | 13.34 | 84.43% | 0 | 0%
GNA_103401101_Capacity | North Valley and Sierra | North Valley | GIRVAN 1101 | 103401101 | Feeder | None | None | None | 67.32% | 0 | 0% | 10.16 | 6.27 | 61.71% | 0 | 0% | 10.16 | 6.38 | 62.8% | 0 | 0% | 10.16 | 6.51 | 64.07% | 0 | 0% | 10.16 | 6.68 | 65.75% | 0 | 0% | 10.16 | 6.84 | 67.32% | 0 | 0%
GNA_103401102_Capacity | North Valley and Sierra | North Valley | GIRVAN 1102 | 103401102 | Feeder | None | None | None | 72.79% | 0 | 0% | 9.26 | 6 | 64.79% | 0 | 0% | 9.26 | 6.15 | 66.41% | 0 | 0% | 9.26 | 6.26 | 67.6% | 0 | 0% | 9.26 | 6.48 | 69.98% | 0 | 0% | 9.26 | 6.74 | 72.79% | 0 | 0%
GNA_1034401_Capacity | North Valley and Sierra | North Valley | JESSUP BANK 1 | 1034401 | Bank | None | None | None | 77.34% | 0 | 0% | 29.57 | 21.79 | 73.69% | 0 | 0% | 29.57 | 21.98 | 74.33% | 0 | 0% | 29.57 | 22.2 | 75.08% | 0 | 0% | 29.57 | 22.49 | 76.06% | 0 | 0% | 29.57 | 22.87 | 77.34% | 0 | 0%
GNA_103441101_Capacity | North Valley and Sierra | North Valley | JESSUP 1101 | 103441101 | Feeder | None | None | None | 64.07% | 0 | 0% | 12.08 | 7.66 | 63.41% | 0 | 0% | 12.08 | 7.65 | 63.33% | 0 | 0% | 12.08 | 7.65 | 63.33% | 0 | 0% | 12.08 | 7.68 | 63.58% | 0 | 0% | 12.08 | 7.74 | 64.07% | 0 | 0%
GNA_103441102_Capacity | North Valley and Sierra | North Valley | JESSUP 1102 | 103441102 | Feeder | None | None | None | 75.59% | 0 | 0% | 12.25 | 8.79 | 71.76% | 0 | 0% | 12.25 | 8.88 | 72.49% | 0 | 0% | 12.25 | 8.99 | 73.39% | 0 | 0% | 12.25 | 9.1 | 74.29% | 0 | 0% | 12.25 | 9.26 | 75.59% | 0 | 0%
GNA_103441103_Capacity | North Valley and Sierra | North Valley | JESSUP 1103 | 103441103 | Feeder | None | None | None | 59.58% | 0 | 0% | 11.33 | 6.23 | 54.99% | 0 | 0% | 11.33 | 6.33 | 55.87% | 0 | 0% | 11.33 | 6.45 | 56.93% | 0 | 0% | 11.33 | 6.59 | 58.16% | 0 | 0% | 11.33 | 6.75 | 59.58% | 0 | 0%
GNA_1034501_Capacity | North Valley and Sierra | North Valley | KESWICK BANK 1 | 1034501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_103451101_Capacity | North Valley and Sierra | North Valley | KESWICK 1101 | 103451101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1035201_Capacity | North Valley and Sierra | North Valley | OREGON TRAIL BANK 1 | 1035201 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_103521102_Capacity | North Valley and Sierra | North Valley | OREGON TRAIL 1102 | 103521102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1035202_Capacity | North Valley and Sierra | North Valley | OREGON TRAIL BANK 2 | 1035202 | Bank | None | None | None | 91.54% | 0 | 0% | 15.84 | 12.74 | 80.43% | 0 | 0% | 15.84 | 13.64 | 86.11% | 0 | 0% | 15.84 | 13.85 | 87.44% | 0 | 0% | 15.84 | 14.14 | 89.27% | 0 | 0% | 15.84 | 14.5 | 91.54% | 0 | 0%
GNA_103521103_Capacity | North Valley and Sierra | North Valley | OREGON TRAIL 1103 | 103521103 | Feeder | None | None | None | 86.16% | 0 | 0% | 10.69 | 8 | 74.84% | 0 | 0% | 10.69 | 8.78 | 82.13% | 0 | 0% | 10.69 | 8.89 | 83.16% | 0 | 0% | 10.69 | 9.03 | 84.47% | 0 | 0% | 10.69 | 9.21 | 86.16% | 0 | 0%
GNA_103521104_Capacity | North Valley and Sierra | North Valley | OREGON TRAIL 1104 | 103521104 | Feeder | None | None | None | 79.12% | 0 | 0% | 8.19 | 5.93 | 72.41% | 0 | 0% | 8.19 | 6.04 | 73.75% | 0 | 0% | 8.19 | 6.14 | 74.97% | 0 | 0% | 8.19 | 6.29 | 76.8% | 0 | 0% | 8.19 | 6.48 | 79.12% | 0 | 0%
GNA_1034601_Capacity | North Valley and Sierra | North Valley | PANORAMA BANK 1 | 1034601 | Bank | None | None | None | 61.95% | 0 | 0% | 25.1 | 14.93 | 59.48% | 0 | 0% | 25.1 | 15.01 | 59.8% | 0 | 0% | 25.1 | 15.14 | 60.32% | 0 | 0% | 25.1 | 15.32 | 61.04% | 0 | 0% | 25.1 | 15.55 | 61.95% | 0 | 0%
GNA_103461101_Capacity | North Valley and Sierra | North Valley | PANORAMA 1101 | 103461101 | Feeder | None | None | None | 64.08% | 0 | 0% | 10.69 | 6.3 | 58.93% | 0 | 0% | 10.69 | 6.41 | 59.96% | 0 | 0% | 10.69 | 6.52 | 60.99% | 0 | 0% | 10.69 | 6.68 | 62.49% | 0 | 0% | 10.69 | 6.85 | 64.08% | 0 | 0%
GNA_103461102_Capacity | North Valley and Sierra | North Valley | PANORAMA 1102 | 103461102 | Feeder | None | None | None | 79.44% | 0 | 0% | 11.33 | 8.93 | 78.82% | 0 | 0% | 11.33 | 8.91 | 78.64% | 0 | 0% | 11.33 | 8.92 | 78.73% | 0 | 0% | 11.33 | 8.95 | 78.99% | 0 | 0% | 11.33 | 9 | 79.44% | 0 | 0%
GNA_1035601_Capacity | North Valley and Sierra | North Valley | STILLWATER STATION BANK 1 | 1035601 | Bank | None | None | None | 90.53% | 0 | 0% | 9.29 | 8.25 | 88.81% | 0 | 0% | 9.29 | 8.25 | 88.81% | 0 | 0% | 9.29 | 8.25 | 88.81% | 0 | 0% | 9.29 | 8.29 | 89.24% | 0 | 0% | 9.29 | 8.41 | 90.53% | 0 | 0%
GNA_103561101_Capacity | North Valley and Sierra | North Valley | STILLWATER 1101 | 103561101 | Feeder | None | None | None | 36.41% | 0 | 0% | 8.13 | 2.93 | 36.04% | 0 | 0% | 8.13 | 2.92 | 35.92% | 0 | 0% | 8.13 | 2.91 | 35.79% | 0 | 0% | 8.13 | 2.93 | 36.04% | 0 | 0% | 8.13 | 2.96 | 36.41% | 0 | 0%
GNA_103561102_Capacity | North Valley and Sierra | North Valley | STILLWATER 1102 | 103561102 | Feeder | None | None | None | 77.64% | 0 | 0% | 7.38 | 5.6 | 75.88% | 0 | 0% | 7.38 | 5.61 | 76.02% | 0 | 0% | 7.38 | 5.62 | 76.15% | 0 | 0% | 7.38 | 5.63 | 76.29% | 0 | 0% | 7.38 | 5.73 | 77.64% | 0 | 0%
GNA_1035501_Capacity | North Valley and Sierra | North Valley | RISING RIVER BANK 1 | 1035501 | Bank | None | None | None | 18.17% | 0 | 0% | 9.85 | 1.79 | 18.17% | 0 | 0% | 9.85 | 1.77 | 17.97% | 0 | 0% | 9.85 | 1.76 | 17.87% | 0 | 0% | 9.85 | 1.75 | 17.77% | 0 | 0% | 9.85 | 1.79 | 18.17% | 0 | 0%
GNA_103551101_Capacity | North Valley and Sierra | North Valley | RISING RIVER 1101 | 103551101 | Feeder | None | None | None | 57.94% | 0 | 0% | 3.21 | 1.85 | 57.63% | 0 | 0% | 3.21 | 1.83 | 57.01% | 0 | 0% | 3.21 | 1.83 | 57.01% | 0 | 0% | 3.21 | 1.82 | 56.7% | 0 | 0% | 3.21 | 1.86 | 57.94% | 0 | 0%
GNA_1025402_Capacity | North Valley and Sierra | North Valley | VOLTA BANK 2 | 1025402 | Bank | None | None | None | 38.93% | 0 | 0% | 17.7 | 6.78 | 38.31% | 0 | 0% | 17.7 | 6.78 | 38.31% | 0 | 0% | 17.7 | 6.79 | 38.36% | 0 | 0% | 17.7 | 6.83 | 38.59% | 0 | 0% | 17.7 | 6.89 | 38.93% | 0 | 0%
GNA_102541101_Capacity | North Valley and Sierra | North Valley | VOLTA 1101 | 102541101 | Feeder | None | None | None | 46.03% | 0 | 0% | 4.28 | 1.95 | 45.56% | 0 | 0% | 4.28 | 1.95 | 45.56% | 0 | 0% | 4.28 | 1.95 | 45.56% | 0 | 0% | 4.28 | 1.95 | 45.56% | 0 | 0% | 4.28 | 1.97 | 46.03% | 0 | 0%
GNA_102541102_Capacity | North Valley and Sierra | North Valley | VOLTA 1102 | 102541102 | Feeder | None | None | None | 64.91% | 0 | 0% | 8.55 | 5.46 | 63.86% | 0 | 0% | 8.55 | 5.47 | 63.98% | 0 | 0% | 8.55 | 5.47 | 63.98% | 0 | 0% | 8.55 | 5.51 | 64.44% | 0 | 0% | 8.55 | 5.55 | 64.91% | 0 | 0%
GNA_1036001_Capacity | North Valley and Sierra | North Valley | WHITMORE BANK 1 | 1036001 | Bank | None | None | None | 55.59% | 0 | 0% | 3.4 | 1.89 | 55.59% | 0 | 0% | 3.4 | 1.89 | 55.59% | 0 | 0% | 3.4 | 1.89 | 55.59% | 0 | 0% | 3.4 | 1.89 | 55.59% | 0 | 0% | 3.4 | 1.89 | 55.59% | 0 | 0%
GNA_103601101_Capacity | North Valley and Sierra | North Valley | WHITMORE 1101 | 103601101 | Feeder | None | None | None | 63.24% | 0 | 0% | 3.21 | 2.03 | 63.24% | 0 | 0% | 3.21 | 2.02 | 62.93% | 0 | 0% | 3.21 | 2.03 | 63.24% | 0 | 0% | 3.21 | 2.02 | 62.93% | 0 | 0% | 3.21 | 2.02 | 62.93% | 0 | 0%
GNA_1036101_Capacity | North Valley and Sierra | North Valley | WILDWOOD BANK 1 | 1036101 | Bank | None | None | None | 32.77% | 0 | 0% | 2.96 | 0.97 | 32.77% | 0 | 0% | 2.96 | 0.97 | 32.77% | 0 | 0% | 2.96 | 0.97 | 32.77% | 0 | 0% | 2.96 | 0.96 | 32.43% | 0 | 0% | 2.96 | 0.96 | 32.43% | 0 | 0%
GNA_103611101_Capacity | North Valley and Sierra | North Valley | WILDWOOD 1101 | 103611101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1028501_Capacity | North Valley and Sierra | North Valley | JACINTO BANK 1 | 1028501 | Bank | None | None | None | 67.87% | 0 | 0% | 15.84 | 10.75 | 67.87% | 0 | 0% | 15.84 | 10.71 | 67.61% | 0 | 0% | 15.84 | 10.62 | 67.05% | 0 | 0% | 15.84 | 10.56 | 66.67% | 0 | 0% | 15.84 | 10.5 | 66.29% | 0 | 0%
GNA_102851101_Capacity | North Valley and Sierra | North Valley | JACINTO 1101 | 102851101 | Feeder | None | None | None | 91.74% | 0 | 0% | 6.05 | 5.55 | 91.74% | 0 | 0% | 6.05 | 5.53 | 91.4% | 0 | 0% | 6.05 | 5.49 | 90.74% | 0 | 0% | 6.05 | 5.46 | 90.25% | 0 | 0% | 6.05 | 5.42 | 89.59% | 0 | 0%
GNA_102851102_Capacity | North Valley and Sierra | North Valley | JACINTO 1102 | 102851102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1031401_Capacity | North Valley and Sierra | North Valley | LOGAN CREEK BANK 1 * | 1031401 | Bank | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_103142101_Capacity | North Valley and Sierra | North Valley | LOGAN CREEK 2101 * | 103142101 | Feeder | Demand Growth | Capacity | 2025 | 123.8% | 3.53 * | 23.84% | 14.81 | 9.9 | 66.85% | 0 | 0% | 14.81 | 9.89 | 66.78% | 0 | 0% | 14.81 | 18.34 | 123.8% | 3.53 | 23.84% | 14.81 | 18.32 | 123.7% | 3.51 | 23.7% | 14.81 | 18.3 | 123.6% | 3.49 | 23.57%
GNA_103142102_Capacity | North Valley and Sierra | North Valley | LOGAN CREEK 2102 | 103142102 | Feeder | None | None | None | 88.7% | 0 | 0% | 22.22 | 19.71 | 88.7% | 0 | 0% | 22.22 | 19.67 | 88.52% | 0 | 0% | 22.22 | 19.64 | 88.39% | 0 | 0% | 22.22 | 19.66 | 88.48% | 0 | 0% | 22.22 | 19.67 | 88.52% | 0 | 0%
GNA_103142103_Capacity | North Valley and Sierra | North Valley | LOGAN CREEK 2103 | 103142103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1027401_Capacity | North Valley and Sierra | North Valley | WILLOWS A BANK 1 | 1027401 | Bank | None | None | None | 97.01% | 0 | 0% | 12.38 | 11.88 | 95.96% | 0 | 0% | 12.38 | 11.89 | 96.04% | 0 | 0% | 12.38 | 11.91 | 96.2% | 0 | 0% | 12.38 | 11.95 | 96.53% | 0 | 0% | 12.38 | 12.01 | 97.01% | 0 | 0%
GNA_102741101_Capacity | North Valley and Sierra | North Valley | WILLOWS A 1101 | 102741101 | Feeder | None | None | None | 39.57% | 0 | 0% | 7.48 | 2.95 | 39.44% | 0 | 0% | 7.48 | 2.94 | 39.3% | 0 | 0% | 7.48 | 2.94 | 39.3% | 0 | 0% | 7.48 | 2.95 | 39.44% | 0 | 0% | 7.48 | 2.96 | 39.57% | 0 | 0%
GNA_102741103_Capacity | North Valley and Sierra | North Valley | WILLOWS A 1103 | 102741103 | Feeder | None | None | None | 52.57% | 0 | 0% | 10.69 | 5.57 | 52.1% | 0 | 0% | 10.69 | 5.57 | 52.1% | 0 | 0% | 10.69 | 5.58 | 52.2% | 0 | 0% | 10.69 | 5.6 | 52.39% | 0 | 0% | 10.69 | 5.62 | 52.57% | 0 | 0%
GNA_102741104_Capacity | North Valley and Sierra | North Valley | WILLOWS A 1104 | 102741104 | Feeder | None | None | None | 69.98% | 0 | 0% | 5.73 | 4.01 | 69.98% | 0 | 0% | 5.73 | 4 | 69.81% | 0 | 0% | 5.73 | 3.96 | 69.11% | 0 | 0% | 5.73 | 3.95 | 68.94% | 0 | 0% | 5.73 | 3.95 | 68.94% | 0 | 0%
GNA_0240102_Capacity | Bay Area | Peninsula | BAY MEADOWS BANK 2 | 240102 | Bank | None | None | None | 50.71% | 0 | 0% | 29.7 | 15.06 | 50.71% | 0 | 0% | 29.7 | 14.78 | 49.76% | 0 | 0% | 29.7 | 14.57 | 49.06% | 0 | 0% | 29.7 | 14.55 | 48.99% | 0 | 0% | 29.7 | 14.6 | 49.16% | 0 | 0%
GNA_024011107_Capacity | Bay Area | Peninsula | BAY MEADOWS 1107 | 24011107 | Feeder | None | None | None | 95.85% | 0 | 0% | 11.57 | 11.09 | 95.85% | 0 | 0% | 11.57 | 11.04 | 95.42% | 0 | 0% | 11.57 | 11 | 95.07% | 0 | 0% | 11.57 | 11.05 | 95.51% | 0 | 0% | 11.57 | 11.05 | 95.51% | 0 | 0%
GNA_024011108_Capacity | Bay Area | Peninsula | BAY MEADOWS 1108 | 24011108 | Feeder | None | None | None | 56.42% | 0 | 0% | 10.28 | 5.41 | 52.63% | 0 | 0% | 10.28 | 5.29 | 51.46% | 0 | 0% | 10.28 | 5.31 | 51.65% | 0 | 0% | 10.28 | 5.49 | 53.4% | 0 | 0% | 10.28 | 5.8 | 56.42% | 0 | 0%
GNA_0240103_Capacity | Bay Area | Peninsula | BAY MEADOWS BANK 3 | 240103 | Bank | None | None | None | 97.71% | 0 | 0% | 44.6 | 43.53 | 97.6% | 0 | 0% | 44.6 | 43.09 | 96.61% | 0 | 0% | 44.6 | 42.88 | 96.14% | 0 | 0% | 44.6 | 43.15 | 96.75% | 0 | 0% | 44.6 | 43.58 | 97.71% | 0 | 0%
GNA_024011102_Capacity | Bay Area | Peninsula | BAY MEADOWS 1102 | 24011102 | Feeder | None | None | None | 51.75% | 0 | 0% | 10.28 | 5.31 | 51.65% | 0 | 0% | 10.28 | 5.26 | 51.17% | 0 | 0% | 10.28 | 5.23 | 50.88% | 0 | 0% | 10.28 | 5.25 | 51.07% | 0 | 0% | 10.28 | 5.32 | 51.75% | 0 | 0%
GNA_024011103_Capacity | Bay Area | Peninsula | BAY MEADOWS 1103 | 24011103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024011104_Capacity | Bay Area | Peninsula | BAY MEADOWS 1104 | 24011104 | Feeder | None | None | None | 86.34% | 0 | 0% | 11.57 | 9.83 | 84.96% | 0 | 0% | 11.57 | 9.69 | 83.75% | 0 | 0% | 11.57 | 9.57 | 82.71% | 0 | 0% | 11.57 | 9.79 | 84.62% | 0 | 0% | 11.57 | 9.99 | 86.34% | 0 | 0%
GNA_024011105_Capacity | Bay Area | Peninsula | BAY MEADOWS 1105 | 24011105 | Feeder | None | None | None | 94.16% | 0 | 0% | 11.65 | 10.67 | 91.59% | 0 | 0% | 11.65 | 10.73 | 92.1% | 0 | 0% | 11.65 | 10.79 | 92.62% | 0 | 0% | 11.65 | 10.87 | 93.3% | 0 | 0% | 11.65 | 10.97 | 94.16% | 0 | 0%
GNA_024011106_Capacity | Bay Area | Peninsula | BAY MEADOWS 1106 | 24011106 | Feeder | None | None | None | 88.33% | 0 | 0% | 10.28 | 8.87 | 86.28% | 0 | 0% | 10.28 | 8.81 | 85.7% | 0 | 0% | 10.28 | 8.81 | 85.7% | 0 | 0% | 10.28 | 8.88 | 86.38% | 0 | 0% | 10.28 | 9.08 | 88.33% | 0 | 0%
GNA_0240301_Capacity | Bay Area | Peninsula | BELMONT BANK 1 | 240301 | Bank | None | None | None | 95.38% | 0 | 0% | 44.6 | 41.11 | 92.17% | 0 | 0% | 44.6 | 40.63 | 91.1% | 0 | 0% | 44.6 | 41.55 | 93.16% | 0 | 0% | 44.6 | 42.36 | 94.98% | 0 | 0% | 44.6 | 42.54 | 95.38% | 0 | 0%
GNA_0240304_Capacity | Bay Area | Peninsula | BELMONT BANK 4 | 240304 | Bank | None | None | None | 72.54% | 0 | 0% | 12.38 | 7.84 | 63.33% | 0 | 0% | 12.38 | 7.88 | 63.65% | 0 | 0% | 12.38 | 7.91 | 63.89% | 0 | 0% | 12.38 | 8.89 | 71.81% | 0 | 0% | 12.38 | 8.98 | 72.54% | 0 | 0%
GNA_024030401_Capacity | Bay Area | Peninsula | BELMONT 0401 | 24030401 | Feeder | None | None | None | 98.52% | 0 | 0% | 2.71 | 2.67 | 98.52% | 0 | 0% | 2.71 | 2.66 | 98.15% | 0 | 0% | 2.71 | 2.65 | 97.79% | 0 | 0% | 2.71 | 2.64 | 97.42% | 0 | 0% | 2.71 | 2.63 | 97.05% | 0 | 0%
GNA_024030402_Capacity | Bay Area | Peninsula | BELMONT 0402 | 24030402 | Feeder | None | None | None | 91.7% | 0 | 0% | 2.77 | 1.75 | 63.18% | 0 | 0% | 2.77 | 1.77 | 63.9% | 0 | 0% | 2.77 | 1.79 | 64.62% | 0 | 0% | 2.77 | 2.45 | 88.45% | 0 | 0% | 2.77 | 2.54 | 91.7% | 0 | 0%
GNA_024030403_Capacity | Bay Area | Peninsula | BELMONT 0403 | 24030403 | Feeder | None | None | None | 63.04% | 0 | 0% | 3.03 | 1.56 | 51.49% | 0 | 0% | 3.03 | 1.57 | 51.82% | 0 | 0% | 3.03 | 1.58 | 52.15% | 0 | 0% | 3.03 | 1.9 | 62.71% | 0 | 0% | 3.03 | 1.91 | 63.04% | 0 | 0%
GNA_024031101_Capacity | Bay Area | Peninsula | BELMONT 1101 | 24031101 | Feeder | None | None | None | 89.45% | 0 | 0% | 10.24 | 8.93 | 87.21% | 0 | 0% | 10.24 | 8.95 | 87.4% | 0 | 0% | 10.24 | 8.98 | 87.7% | 0 | 0% | 10.24 | 9.05 | 88.38% | 0 | 0% | 10.24 | 9.16 | 89.45% | 0 | 0%
GNA_024031102_Capacity | Bay Area | Peninsula | BELMONT 1102 | 24031102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024031103_Capacity | Bay Area | Peninsula | BELMONT 1103 | 24031103 | Feeder | None | None | None | 90.27% | 0 | 0% | 10.48 | 9.08 | 86.64% | 0 | 0% | 10.48 | 8.3 | 79.2% | 0 | 0% | 10.48 | 9.46 | 90.27% | 0 | 0% | 10.48 | 9.43 | 89.98% | 0 | 0% | 10.48 | 9.37 | 89.41% | 0 | 0%
GNA_024031104_Capacity | Bay Area | Peninsula | BELMONT 1104 | 24031104 | Feeder | None | None | None | 87.6% | 0 | 0% | 11.05 | 9.18 | 83.08% | 0 | 0% | 11.05 | 9.67 | 87.51% | 0 | 0% | 11.05 | 9.68 | 87.6% | 0 | 0% | 11.05 | 9.66 | 87.42% | 0 | 0% | 11.05 | 9.67 | 87.51% | 0 | 0%
GNA_0240302_Capacity | Bay Area | Peninsula | BELMONT BANK 2 | 240302 | Bank | None | None | None | 66.05% | 0 | 0% | 44.6 | 24.95 | 55.94% | 0 | 0% | 44.6 | 28.15 | 63.12% | 0 | 0% | 44.6 | 29.26 | 65.61% | 0 | 0% | 44.6 | 29.28 | 65.65% | 0 | 0% | 44.6 | 29.46 | 66.05% | 0 | 0%
GNA_024031105_Capacity | Bay Area | Peninsula | BELMONT 1105 | 24031105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024031106_Capacity | Bay Area | Peninsula | BELMONT 1106 | 24031106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024031107_Capacity | Bay Area | Peninsula | BELMONT 1107 | 24031107 | Feeder | None | None | None | 97.84% | 0 | 0% | 11.57 | 9.77 | 84.44% | 0 | 0% | 11.57 | 11.32 | 97.84% | 0 | 0% | 11.57 | 11.32 | 97.84% | 0 | 0% | 11.57 | 11.32 | 97.84% | 0 | 0% | 11.57 | 11.32 | 97.84% | 0 | 0%
GNA_024031108_Capacity | Bay Area | Peninsula | BELMONT 1108 | 24031108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0240303_Capacity | Bay Area | Peninsula | BELMONT BANK 3 | 240303 | Bank | None | None | None | 73.48% | 0 | 0% | 44.6 | 30.6 | 68.61% | 0 | 0% | 44.6 | 31.99 | 71.73% | 0 | 0% | 44.6 | 32.34 | 72.51% | 0 | 0% | 44.6 | 32.54 | 72.96% | 0 | 0% | 44.6 | 32.77 | 73.48% | 0 | 0%
GNA_024031109_Capacity | Bay Area | Peninsula | BELMONT 1109 | 24031109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024031110_Capacity | Bay Area | Peninsula | BELMONT 1110 | 24031110 | Feeder | Demand Growth | Capacity | 2024 | 108.5% | 0.99 | 8.498% | 11.65 | 11.3 | 97% | 0 | 0% | 11.65 | 12.59 | 108.1% | 0.94 | 8.069% | 11.65 | 12.51 | 107.4% | 0.86 | 7.382% | 11.65 | 12.56 | 107.8% | 0.91 | 7.811% | 11.65 | 12.64 | 108.5% | 0.99 | 8.498%
GNA_024031111_Capacity | Bay Area | Peninsula | BELMONT 1111 | 24031111 | Feeder | None | None | None | 58.74% | 0 | 0% | 12.19 | 7.16 | 58.74% | 0 | 0% | 12.19 | 7.16 | 58.74% | 0 | 0% | 12.19 | 7.16 | 58.74% | 0 | 0% | 12.19 | 7.16 | 58.74% | 0 | 0% | 12.19 | 7.15 | 58.65% | 0 | 0%
GNA_0240305_Capacity | Bay Area | Peninsula | BELMONT BANK 5 | 240305 | Bank | None | None | None | 27.14% | 0 | 0% | 12.38 | 3.01 | 24.31% | 0 | 0% | 12.38 | 2.99 | 24.15% | 0 | 0% | 12.38 | 3.35 | 27.06% | 0 | 0% | 12.38 | 3.35 | 27.06% | 0 | 0% | 12.38 | 3.36 | 27.14% | 0 | 0%
GNA_024030406_Capacity | Bay Area | Peninsula | BELMONT 0406 | 24030406 | Feeder | None | None | None | 90.21% | 0 | 0% | 2.35 | 1.77 | 75.32% | 0 | 0% | 2.35 | 1.75 | 74.47% | 0 | 0% | 2.35 | 2.1 | 89.36% | 0 | 0% | 2.35 | 2.1 | 89.36% | 0 | 0% | 2.35 | 2.12 | 90.21% | 0 | 0%
GNA_0241401_Capacity | Bay Area | Peninsula | RALSTON BANK 1 | 241401 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024141101_Capacity | Bay Area | Peninsula | RALSTON 1101 | 24141101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0241402_Capacity | Bay Area | Peninsula | RALSTON BANK 2 | 241402 | Bank | None | None | None | 93.15% | 0 | 0% | 5.4 | 5.03 | 93.15% | 0 | 0% | 5.4 | 4.93 | 91.3% | 0 | 0% | 5.4 | 4.82 | 89.26% | 0 | 0% | 5.4 | 4.77 | 88.33% | 0 | 0% | 5.4 | 4.81 | 89.07% | 0 | 0%
GNA_024141102_Capacity | Bay Area | Peninsula | RALSTON 1102 | 24141102 | Feeder | None | None | None | 85.14% | 0 | 0% | 6.26 | 5.33 | 85.14% | 0 | 0% | 6.26 | 5.22 | 83.39% | 0 | 0% | 6.26 | 5.12 | 81.79% | 0 | 0% | 6.26 | 5.06 | 80.83% | 0 | 0% | 6.26 | 5.09 | 81.31% | 0 | 0%
GNA_0240101_Capacity | Bay Area | Peninsula | BAY MEADOWS BANK 1 | 240101 | Bank | Demand Growth | Capacity | 2027 | 100.6% | 0.26 | 0.583% | 44.6 | 40.76 | 91.39% | 0 | 0% | 44.6 | 44.82 | 100.5% | 0.22 | 0.4933% | 44.6 | 44.67 | 100.2% | 0.07 | 0.157% | 44.6 | 44.78 | 100.4% | 0.18 | 0.4036% | 44.6 | 44.86 | 100.6% | 0.26 | 0.583%
GNA_024012101_Capacity | Bay Area | Peninsula | BAY MEADOWS 2101 | 24012101 | Feeder | None | None | None | 60.19% | 0 | 0% | 17.81 | 10.46 | 58.73% | 0 | 0% | 17.81 | 10.49 | 58.9% | 0 | 0% | 17.81 | 10.52 | 59.07% | 0 | 0% | 17.81 | 10.61 | 59.57% | 0 | 0% | 17.81 | 10.72 | 60.19% | 0 | 0%
GNA_024012102_Capacity | Bay Area | Peninsula | BAY MEADOWS 2102 | 24012102 | Feeder | None | None | None | 67.49% | 0 | 0% | 17.81 | 12.02 | 67.49% | 0 | 0% | 17.81 | 11.79 | 66.2% | 0 | 0% | 17.81 | 11.74 | 65.92% | 0 | 0% | 17.81 | 11.88 | 66.7% | 0 | 0% | 17.81 | 12 | 67.38% | 0 | 0%
GNA_0240105_Capacity | Bay Area | Peninsula | BAY MEADOWS BANK 5 | 240105 | Bank | None | None | None | 96.14% | 0 | 0% | 44.6 | 42.18 | 94.57% | 0 | 0% | 44.6 | 42.34 | 94.93% | 0 | 0% | 44.6 | 42.45 | 95.18% | 0 | 0% | 44.6 | 42.66 | 95.65% | 0 | 0% | 44.6 | 42.88 | 96.14% | 0 | 0%
GNA_024012103_Capacity | Bay Area | Peninsula | BAY MEADOWS 2103 | 24012103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024012104_Capacity | Bay Area | Peninsula | BAY MEADOWS 2104 | 24012104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024012105_Capacity | Bay Area | Peninsula | BAY MEADOWS 2105 | 24012105 | Feeder | None | None | None | 66.33% | 0 | 0% | 16.81 | 10.73 | 63.83% | 0 | 0% | 16.81 | 10.84 | 64.49% | 0 | 0% | 16.81 | 10.93 | 65.02% | 0 | 0% | 16.81 | 11.04 | 65.68% | 0 | 0% | 16.81 | 11.15 | 66.33% | 0 | 0%
GNA_024012106_Capacity | Bay Area | Peninsula | BAY MEADOWS 2106 | 24012106 | Feeder | None | None | None | 64.36% | 0 | 0% | 22.22 | 14.3 | 64.36% | 0 | 0% | 22.22 | 14.27 | 64.22% | 0 | 0% | 22.22 | 14.25 | 64.13% | 0 | 0% | 22.22 | 14.24 | 64.09% | 0 | 0% | 22.22 | 14.25 | 64.13% | 0 | 0%
GNA_0240501_Capacity | Bay Area | Peninsula | BURLINGAME BANK 1 | 240501 | Bank | None | None | None | 94.24% | 0 | 0% | 29.7 | 15.38 | 51.78% | 0 | 0% | 29.7 | 15.44 | 51.99% | 0 | 0% | 29.7 | 27.53 | 92.69% | 0 | 0% | 29.7 | 27.73 | 93.37% | 0 | 0% | 29.7 | 27.99 | 94.24% | 0 | 0%
GNA_024052101_Capacity | Bay Area | Peninsula | BURLINGAME 2101 | 24052101 | Feeder | None | None | None | 98.68% | 0 | 0% | 19.74 | 7.29 | 36.93% | 0 | 0% | 19.74 | 7.29 | 36.93% | 0 | 0% | 19.74 | 19.35 | 98.02% | 0 | 0% | 19.74 | 19.41 | 98.33% | 0 | 0% | 19.74 | 19.48 | 98.68% | 0 | 0%
GNA_0240503_Capacity | Bay Area | Peninsula | BURLINGAME BANK 3 | 240503 | Bank | None | None | None | 91.06% | 0 | 0% | 10.4 | 9.03 | 86.83% | 0 | 0% | 10.4 | 9.1 | 87.5% | 0 | 0% | 10.4 | 9.13 | 87.79% | 0 | 0% | 10.4 | 9.28 | 89.23% | 0 | 0% | 10.4 | 9.47 | 91.06% | 0 | 0%
GNA_024050401_Capacity | Bay Area | Peninsula | BURLINGAME 0401 | 24050401 | Feeder | None | None | None | 82.55% | 0 | 0% | 2.35 | 1.86 | 79.15% | 0 | 0% | 2.35 | 1.87 | 79.57% | 0 | 0% | 2.35 | 1.88 | 80% | 0 | 0% | 2.35 | 1.9 | 80.85% | 0 | 0% | 2.35 | 1.94 | 82.55% | 0 | 0%
GNA_024050402_Capacity | Bay Area | Peninsula | BURLINGAME 0402 | 24050402 | Feeder | None | None | None | 89.02% | 0 | 0% | 2.46 | 2.03 | 82.52% | 0 | 0% | 2.46 | 2.06 | 83.74% | 0 | 0% | 2.46 | 2.07 | 84.15% | 0 | 0% | 2.46 | 2.12 | 86.18% | 0 | 0% | 2.46 | 2.19 | 89.02% | 0 | 0%
GNA_024050403_Capacity | Bay Area | Peninsula | BURLINGAME 0403 | 24050403 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024050404_Capacity | Bay Area | Peninsula | BURLINGAME 0404 | 24050404 | Feeder | None | None | None | 81.7% | 0 | 0% | 2.35 | 1.82 | 77.45% | 0 | 0% | 2.35 | 1.84 | 78.3% | 0 | 0% | 2.35 | 1.86 | 79.15% | 0 | 0% | 2.35 | 1.89 | 80.43% | 0 | 0% | 2.35 | 1.92 | 81.7% | 0 | 0%
GNA_024050405_Capacity | Bay Area | Peninsula | BURLINGAME 0405 | 24050405 | Feeder | None | None | None | 64.68% | 0 | 0% | 2.35 | 1.44 | 61.28% | 0 | 0% | 2.35 | 1.45 | 61.7% | 0 | 0% | 2.35 | 1.46 | 62.13% | 0 | 0% | 2.35 | 1.48 | 62.98% | 0 | 0% | 2.35 | 1.52 | 64.68% | 0 | 0%
GNA_0241909_Capacity | Bay Area | Peninsula | SAN MATEO BANK 9 | 241909 | Bank | None | None | None | 68.73% | 0 | 0% | 44.52 | 25.85 | 58.06% | 0 | 0% | 44.52 | 30.6 | 68.73% | 0 | 0% | 44.52 | 26.55 | 59.64% | 0 | 0% | 44.52 | 27.03 | 60.71% | 0 | 0% | 44.52 | 27.17 | 61.03% | 0 | 0%
GNA_024192101_Capacity | Bay Area | Peninsula | SAN MATEO 2101 | 24192101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024192102_Capacity | Bay Area | Peninsula | SAN MATEO 2102 | 24192102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0240401_Capacity | Bay Area | Peninsula | BERESFORD BANK 1 | 240401 | Bank | None | None | None | 96.77% | 0 | 0% | 6.19 | 5.94 | 95.96% | 0 | 0% | 6.19 | 5.99 | 96.77% | 0 | 0% | 6.19 | 5.72 | 92.41% | 0 | 0% | 6.19 | 5.82 | 94.02% | 0 | 0% | 6.19 | 5.92 | 95.64% | 0 | 0%
GNA_024040401_Capacity | Bay Area | Peninsula | BERESFORD 0401 | 24040401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024040402_Capacity | Bay Area | Peninsula | BERESFORD 0402 | 24040402 | Feeder | None | None | None | 74.17% | 0 | 0% | 2.71 | 1.95 | 71.96% | 0 | 0% | 2.71 | 1.96 | 72.32% | 0 | 0% | 2.71 | 1.96 | 72.32% | 0 | 0% | 2.71 | 1.98 | 73.06% | 0 | 0% | 2.71 | 2.01 | 74.17% | 0 | 0%
GNA_024040403_Capacity | Bay Area | Peninsula | BERESFORD 0403 | 24040403 | Feeder | None | None | None | 64.6% | 0 | 0% | 3.39 | 2.14 | 63.13% | 0 | 0% | 3.39 | 2.19 | 64.6% | 0 | 0% | 3.39 | 1.93 | 56.93% | 0 | 0% | 3.39 | 2 | 59% | 0 | 0% | 3.39 | 2.08 | 61.36% | 0 | 0%
GNA_0240402_Capacity | Bay Area | Peninsula | BERESFORD BANK 2 | 240402 | Bank | None | None | None | 89.64% | 0 | 0% | 3.86 | 3.4 | 88.08% | 0 | 0% | 3.86 | 3.39 | 87.82% | 0 | 0% | 3.86 | 3.37 | 87.31% | 0 | 0% | 3.86 | 3.42 | 88.6% | 0 | 0% | 3.86 | 3.46 | 89.64% | 0 | 0%
GNA_024040404_Capacity | Bay Area | Peninsula | BERESFORD 0404 | 24040404 | Feeder | None | None | None | 86.72% | 0 | 0% | 2.71 | 2.19 | 80.81% | 0 | 0% | 2.71 | 2.22 | 81.92% | 0 | 0% | 2.71 | 2.24 | 82.66% | 0 | 0% | 2.71 | 2.3 | 84.87% | 0 | 0% | 2.71 | 2.35 | 86.72% | 0 | 0%
GNA_0240601_Capacity | Bay Area | Peninsula | CAROLANDS BANK 1 | 240601 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024060401_Capacity | Bay Area | Peninsula | CAROLANDS 0401 | 24060401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024060402_Capacity | Bay Area | Peninsula | CAROLANDS 0402 | 24060402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0240602_Capacity | Bay Area | Peninsula | CAROLANDS BANK 2 | 240602 | Bank | None | None | None | 65.19% | 0 | 0% | 10.4 | 6.41 | 61.63% | 0 | 0% | 10.4 | 6.46 | 62.12% | 0 | 0% | 10.4 | 6.53 | 62.79% | 0 | 0% | 10.4 | 6.68 | 64.23% | 0 | 0% | 10.4 | 6.78 | 65.19% | 0 | 0%
GNA_024060403_Capacity | Bay Area | Peninsula | CAROLANDS 0403 | 24060403 | Feeder | None | None | None | 95.48% | 0 | 0% | 3.1 | 2.79 | 90% | 0 | 0% | 3.1 | 2.8 | 90.32% | 0 | 0% | 3.1 | 2.83 | 91.29% | 0 | 0% | 3.1 | 2.91 | 93.87% | 0 | 0% | 3.1 | 2.96 | 95.48% | 0 | 0%
GNA_024060404_Capacity | Bay Area | Peninsula | CAROLANDS 0404 | 24060404 | Feeder | Demand Growth | Capacity | 2023 | 121% | 0.73 | 21.04% | 3.47 | 4 | 115.3% | 0.53 | 15.27% | 3.47 | 4.04 | 116.4% | 0.57 | 16.43% | 3.47 | 4.08 | 117.6% | 0.61 | 17.58% | 3.47 | 4.15 | 119.6% | 0.68 | 19.6% | 3.47 | 4.2 | 121% | 0.73 | 21.04%
GNA_0241101_Capacity | Bay Area | Peninsula | HILLSDALE BANK 1 | 241101 | Bank | None | None | None | 97.84% | 0 | 0% | 8.8 | 8.51 | 96.7% | 0 | 0% | 8.8 | 8.61 | 97.84% | 0 | 0% | 8.8 | 8.33 | 94.66% | 0 | 0% | 8.8 | 7.6 | 86.36% | 0 | 0% | 8.8 | 7.88 | 89.55% | 0 | 0%
GNA_024110401_Capacity | Bay Area | Peninsula | HILLSDALE 0401 | 24110401 | Feeder | None | None | None | 77.87% | 0 | 0% | 2.35 | 1.81 | 77.02% | 0 | 0% | 2.35 | 1.83 | 77.87% | 0 | 0% | 2.35 | 1.49 | 63.4% | 0 | 0% | 2.35 | 1.53 | 65.11% | 0 | 0% | 2.35 | 1.6 | 68.09% | 0 | 0%
GNA_024110402_Capacity | Bay Area | Peninsula | HILLSDALE 0402 | 24110402 | Feeder | None | None | None | 98.72% | 0 | 0% | 2.35 | 2.29 | 97.45% | 0 | 0% | 2.35 | 2.3 | 97.87% | 0 | 0% | 2.35 | 2.32 | 98.72% | 0 | 0% | 2.35 | 1.44 | 61.28% | 0 | 0% | 2.35 | 1.51 | 64.26% | 0 | 0%
GNA_024110403_Capacity | Bay Area | Peninsula | HILLSDALE 0403 | 24110403 | Feeder | None | None | None | 38.3% | 0 | 0% | 2.35 | 0.8 | 34.04% | 0 | 0% | 2.35 | 0.82 | 34.89% | 0 | 0% | 2.35 | 0.83 | 35.32% | 0 | 0% | 2.35 | 0.86 | 36.6% | 0 | 0% | 2.35 | 0.9 | 38.3% | 0 | 0%
GNA_024110404_Capacity | Bay Area | Peninsula | HILLSDALE 0404 | 24110404 | Feeder | None | None | None | 65.53% | 0 | 0% | 2.35 | 1.43 | 60.85% | 0 | 0% | 2.35 | 1.45 | 61.7% | 0 | 0% | 2.35 | 1.47 | 62.55% | 0 | 0% | 2.35 | 1.5 | 63.83% | 0 | 0% | 2.35 | 1.54 | 65.53% | 0 | 0%
GNA_024110405_Capacity | Bay Area | Peninsula | HILLSDALE 0405 | 24110405 | Feeder | None | None | None | 87.23% | 0 | 0% | 2.35 | 1.9 | 80.85% | 0 | 0% | 2.35 | 1.92 | 81.7% | 0 | 0% | 2.35 | 1.95 | 82.98% | 0 | 0% | 2.35 | 1.99 | 84.68% | 0 | 0% | 2.35 | 2.05 | 87.23% | 0 | 0%
GNA_0241904_Capacity | Bay Area | Peninsula | SAN MATEO BANK 4 | 241904 | Bank | Demand Growth | Capacity | 2023 | 116.1% | 1.42 | 16.14% | 8.8 | 9.69 | 110.1% | 0.89 | 10.11% | 8.8 | 9.69 | 110.1% | 0.89 | 10.11% | 8.8 | 10.02 | 113.9% | 1.22 | 13.86% | 8.8 | 10.09 | 114.7% | 1.29 | 14.66% | 8.8 | 10.22 | 116.1% | 1.42 | 16.14%
GNA_024190404_Capacity | Bay Area | Peninsula | SAN MATEO 0404 | 24190404 | Feeder | None | None | None | 72.34% | 0 | 0% | 3.94 | 2.62 | 66.5% | 0 | 0% | 3.94 | 2.57 | 65.23% | 0 | 0% | 3.94 | 2.83 | 71.83% | 0 | 0% | 3.94 | 2.82 | 71.57% | 0 | 0% | 3.94 | 2.85 | 72.34% | 0 | 0%
GNA_024190407_Capacity | Bay Area | Peninsula | SAN MATEO 0407 | 24190407 | Feeder | None | None | None | 92.86% | 0 | 0% | 2.94 | 2.73 | 92.86% | 0 | 0% | 2.94 | 2.71 | 92.18% | 0 | 0% | 2.94 | 2.7 | 91.84% | 0 | 0% | 2.94 | 2.68 | 91.16% | 0 | 0% | 2.94 | 2.67 | 90.82% | 0 | 0%
GNA_024190408_Capacity | Bay Area | Peninsula | SAN MATEO 0408 | 24190408 | Feeder | None | None | None | 84.68% | 0 | 0% | 2.35 | 1.97 | 83.83% | 0 | 0% | 2.35 | 1.96 | 83.4% | 0 | 0% | 2.35 | 1.96 | 83.4% | 0 | 0% | 2.35 | 1.97 | 83.83% | 0 | 0% | 2.35 | 1.99 | 84.68% | 0 | 0%
GNA_024190409_Capacity | Bay Area | Peninsula | SAN MATEO 0409 | 24190409 | Feeder | None | None | None | 36.99% | 0 | 0% | 2.92 | 1.04 | 35.62% | 0 | 0% | 2.92 | 1.04 | 35.62% | 0 | 0% | 2.92 | 1.05 | 35.96% | 0 | 0% | 2.92 | 1.07 | 36.64% | 0 | 0% | 2.92 | 1.08 | 36.99% | 0 | 0%
GNA_024190410_Capacity | Bay Area | Peninsula | SAN MATEO 0410 | 24190410 | Feeder | None | None | None | 73.19% | 0 | 0% | 2.35 | 1.6 | 68.09% | 0 | 0% | 2.35 | 1.62 | 68.94% | 0 | 0% | 2.35 | 1.65 | 70.21% | 0 | 0% | 2.35 | 1.68 | 71.49% | 0 | 0% | 2.35 | 1.72 | 73.19% | 0 | 0%
GNA_0225701_Capacity | Bay Area | Peninsula | EAST GRAND BANK 1 | 225701 | Bank | Demand Growth | Capacity | 2024 | 119.1% | 8.28 | 19.14% | 43.25 | 41.55 | 96.07% | 0 | 0% | 43.25 | 43.73 | 101.1% | 0.48 | 1.11% | 43.25 | 48.35 | 111.8% | 5.1 | 11.79% | 43.25 | 51.53 | 119.1% | 8.28 | 19.14% | 43.25 | 51.35 | 118.7% | 8.1 | 18.73%
GNA_022571102_Capacity | Bay Area | Peninsula | EAST GRAND 1102 | 22571102 | Feeder | Demand Growth | Capacity | 2026 | 101% | 0.12 | 1.037% | 11.57 | 7.77 | 67.16% | 0 | 0% | 11.57 | 7.77 | 67.16% | 0 | 0% | 11.57 | 10.18 | 87.99% | 0 | 0% | 11.57 | 11.67 | 100.9% | 0.1 | 0.8643% | 11.57 | 11.69 | 101% | 0.12 | 1.037%
GNA_022571104_Capacity | Bay Area | Peninsula | EAST GRAND 1104 | 22571104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0224401_Capacity | Bay Area | Peninsula | LAWNDALE BANK 1 | 224401 | Bank | None | None | None | 40.73% | 0 | 0% | 2.48 | 1 | 40.32% | 0 | 0% | 2.48 | 1 | 40.32% | 0 | 0% | 2.48 | 1 | 40.32% | 0 | 0% | 2.48 | 1 | 40.32% | 0 | 0% | 2.48 | 1.01 | 40.73% | 0 | 0%
GNA_022440401_Capacity | Bay Area | Peninsula | LAWNDALE 0401 | 22440401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0224402_Capacity | Bay Area | Peninsula | LAWNDALE BANK 2 | 224402 | Bank | None | None | None | 38.87% | 0 | 0% | 2.47 | 0.96 | 38.87% | 0 | 0% | 2.47 | 0.96 | 38.87% | 0 | 0% | 2.47 | 0.96 | 38.87% | 0 | 0% | 2.47 | 0.96 | 38.87% | 0 | 0% | 2.47 | 0.96 | 38.87% | 0 | 0%
GNA_022440402_Capacity | Bay Area | Peninsula | LAWNDALE 0402 | 22440402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022571109_Capacity | Bay Area | Peninsula | EAST GRAND 1109 | 22571109 | Feeder | Demand Growth | Capacity | 2023 | 187% | 10.07 | 87.04% | 11.57 | 18.22 | 157.5% | 6.65 | 57.48% | 11.57 | 19.67 | 170% | 8.1 | 70.01% | 11.57 | 20.62 | 178.2% | 9.05 | 78.22% | 11.57 | 21.64 | 187% | 10.07 | 87.04% | 11.57 | 21.63 | 186.9% | 10.06 | 86.95%
GNA_022571112_Capacity | Bay Area | Peninsula | EAST GRAND 1112 | 22571112 | Feeder | Demand Growth | Capacity | 2024 | 124.2% | 2.8 | 24.2% | 11.57 | 11.21 | 96.89% | 0 | 0% | 11.57 | 13.46 | 116.3% | 1.89 | 16.34% | 11.57 | 14.37 | 124.2% | 2.8 | 24.2% | 11.57 | 14.36 | 124.1% | 2.79 | 24.11% | 11.57 | 14.36 | 124.1% | 2.79 | 24.11%
GNA_0225704_Capacity | Bay Area | Peninsula | EAST GRAND BANK 4 | 225704 | Bank | None | None | None | 97.35% | 0 | 0% | 44.53 | 42.35 | 95.1% | 0 | 0% | 44.53 | 39.35 | 88.37% | 0 | 0% | 44.53 | 39.63 | 89% | 0 | 0% | 44.53 | 43.19 | 96.99% | 0 | 0% | 44.53 | 43.35 | 97.35% | 0 | 0%
GNA_022571105_Capacity | Bay Area | Peninsula | EAST GRAND 1105 | 22571105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022571106_Capacity | Bay Area | Peninsula | EAST GRAND 1106 | 22571106 | Feeder | Demand Growth | Capacity | 2023 | 108.9% | 1.62 | 8.945% | 18.11 | 18.4 | 101.6% | 0.29 | 1.601% | 18.11 | 19.73 | 108.9% | 1.62 | 8.945% | 18.11 | 18.91 | 104.4% | 0.8 | 4.417% | 18.11 | 18.94 | 104.6% | 0.83 | 4.583% | 18.11 | 18.95 | 104.6% | 0.84 | 4.638%
GNA_022571107_Capacity | Bay Area | Peninsula | EAST GRAND 1107 | 22571107 | Feeder | None | None | None | 74.2% | 0 | 0% | 12.83 | 9.52 | 74.2% | 0 | 0% | 12.83 | 2.93 | 22.84% | 0 | 0% | 12.83 | 2.91 | 22.68% | 0 | 0% | 12.83 | 3 | 23.38% | 0 | 0% | 12.83 | 3.09 | 24.08% | 0 | 0%
GNA_022571108_Capacity | Bay Area | Peninsula | EAST GRAND 1108 | 22571108 | Feeder | None | None | None | 98.67% | 0 | 0% | 12.83 | 11.51 | 89.71% | 0 | 0% | 12.83 | 11.51 | 89.71% | 0 | 0% | 12.83 | 12.63 | 98.44% | 0 | 0% | 12.83 | 12.64 | 98.52% | 0 | 0% | 12.83 | 12.66 | 98.67% | 0 | 0%
GNA_0225705_Capacity | Bay Area | Peninsula | EAST GRAND BANK 5 | 225705 | Bank | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022571101_Capacity | Bay Area | Peninsula | EAST GRAND 1101 | 22571101 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022571110_Capacity | Bay Area | Peninsula | EAST GRAND 1110 | 22571110 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022571113_Capacity | Bay Area | Peninsula | EAST GRAND 1113 | 22571113 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022571114_Capacity | Bay Area | Peninsula | EAST GRAND 1114 | 22571114 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0225706_Capacity | Bay Area | Peninsula | EAST GRAND BANK 6 | 225706 | Bank | None | None | None | 62.81% | 0 | 0% | 42.24 | 26.53 | 62.81% | 0 | 0% | 42.24 | 26.43 | 62.57% | 0 | 0% | 42.24 | 26.34 | 62.36% | 0 | 0% | 42.24 | 26.31 | 62.29% | 0 | 0% | 42.24 | 26.3 | 62.26% | 0 | 0%
GNA_02257BK2-3_Capacity | Bay Area | Peninsula | EAST GRAND BK2-3 | 02257BK2-3 | Feeder | None | None | None | 32.35% | 0 | 0% | 12.83 | 4.02 | 31.33% | 0 | 0% | 12.83 | 4.03 | 31.41% | 0 | 0% | 12.83 | 4.04 | 31.49% | 0 | 0% | 12.83 | 4.09 | 31.88% | 0 | 0% | 12.83 | 4.15 | 32.35% | 0 | 0%
GNA_0225723_Capacity | Bay Area | Peninsula | EAST GRAND BANK 23 | 225723 | Bank | None | None | None | 32.55% | 0 | 0% | 8.91 | 2.77 | 31.09% | 0 | 0% | 8.91 | 2.78 | 31.2% | 0 | 0% | 8.91 | 2.79 | 31.31% | 0 | 0% | 8.91 | 2.84 | 31.87% | 0 | 0% | 8.91 | 2.9 | 32.55% | 0 | 0%
GNA_022570401_Capacity | Bay Area | Peninsula | EAST GRAND 0401 | 22570401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022570404_Capacity | Bay Area | Peninsula | EAST GRAND 0404 | 22570404 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022571103_Capacity | Bay Area | Peninsula | EAST GRAND 1103 | 22571103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022571111_Capacity | Bay Area | Peninsula | EAST GRAND 1111 | 22571111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022571115_Capacity | Bay Area | Peninsula | EAST GRAND 1115 | 22571115 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0226903_Capacity | Bay Area | Peninsula | MILLBRAE BANK 3 | 226903 | Bank | Demand Growth | Capacity | 2023 | 135.8% | 10.63 | 35.79% | 29.7 | 30.45 | 102.5% | 0.75 | 2.525% | 29.7 | 36.73 | 123.7% | 7.03 | 23.67% | 29.7 | 38.33 | 129.1% | 8.63 | 29.06% | 29.7 | 40.26 | 135.6% | 10.56 | 35.56% | 29.7 | 40.33 | 135.8% | 10.63 | 35.79%
GNA_022691102_Capacity | Bay Area | Peninsula | MILLBRAE 1102 | 22691102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022691106_Capacity | Bay Area | Peninsula | MILLBRAE 1106 | 22691106 | Feeder | Demand Growth | Capacity | 2026 | 112.3% | 1.14 | 12.26% | 9.3 | 8.92 | 95.91% | 0 | 0% | 9.3 | 8.9 | 95.7% | 0 | 0% | 9.3 | 8.45 | 90.86% | 0 | 0% | 9.3 | 10.44 | 112.3% | 1.14 | 12.26% | 9.3 | 10.44 | 112.3% | 1.14 | 12.26%
GNA_022691108_Capacity | Bay Area | Peninsula | MILLBRAE 1108 | 22691108 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0226904_Capacity | Bay Area | Peninsula | MILLBRAE BANK 4 | 226904 | Bank | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022691101_Capacity | Bay Area | Peninsula | MILLBRAE 1101 | 22691101 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022691104_Capacity | Bay Area | Peninsula | MILLBRAE 1104 | 22691104 | Feeder | None | None | None | 77.53% | 0 | 0% | 9.3 | 6.62 | 71.18% | 0 | 0% | 9.3 | 6.56 | 70.54% | 0 | 0% | 9.3 | 6.66 | 71.61% | 0 | 0% | 9.3 | 6.95 | 74.73% | 0 | 0% | 9.3 | 7.21 | 77.53% | 0 | 0%
GNA_022691107_Capacity | Bay Area | Peninsula | MILLBRAE 1107 | 22691107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0226901_Capacity | Bay Area | Peninsula | MILLBRAE BANK 1 | 226901 | Bank | None | None | None | 96.45% | 0 | 0% | 5.64 | 5.15 | 91.31% | 0 | 0% | 5.64 | 5.21 | 92.38% | 0 | 0% | 5.64 | 5.23 | 92.73% | 0 | 0% | 5.64 | 5.33 | 94.5% | 0 | 0% | 5.64 | 5.44 | 96.45% | 0 | 0%
GNA_022690401_Capacity | Bay Area | Peninsula | MILLBRAE 0401 | 22690401 | Feeder | None | None | None | 75.32% | 0 | 0% | 2.35 | 1.76 | 74.89% | 0 | 0% | 2.35 | 1.76 | 74.89% | 0 | 0% | 2.35 | 1.74 | 74.04% | 0 | 0% | 2.35 | 1.76 | 74.89% | 0 | 0% | 2.35 | 1.77 | 75.32% | 0 | 0%
GNA_022690403_Capacity | Bay Area | Peninsula | MILLBRAE 0403 | 22690403 | Feeder | None | None | None | 82.13% | 0 | 0% | 2.35 | 1.84 | 78.3% | 0 | 0% | 2.35 | 1.87 | 79.57% | 0 | 0% | 2.35 | 1.88 | 80% | 0 | 0% | 2.35 | 1.91 | 81.28% | 0 | 0% | 2.35 | 1.93 | 82.13% | 0 | 0%
GNA_022690404_Capacity | Bay Area | Peninsula | MILLBRAE 0404 | 22690404 | Feeder | None | None | None | 71.49% | 0 | 0% | 2.35 | 1.54 | 65.53% | 0 | 0% | 2.35 | 1.55 | 65.96% | 0 | 0% | 2.35 | 1.57 | 66.81% | 0 | 0% | 2.35 | 1.62 | 68.94% | 0 | 0% | 2.35 | 1.68 | 71.49% | 0 | 0%
GNA_0227001_Capacity | Bay Area | Peninsula | SAN BRUNO BANK 1 | 227001 | Bank | None | None | None | 68.72% | 0 | 0% | 4.7 | 3.02 | 64.26% | 0 | 0% | 4.7 | 3.19 | 67.87% | 0 | 0% | 4.7 | 3.18 | 67.66% | 0 | 0% | 4.7 | 3.19 | 67.87% | 0 | 0% | 4.7 | 3.23 | 68.72% | 0 | 0%
GNA_022700401_Capacity | Bay Area | Peninsula | SAN BRUNO 0401 | 22700401 | Feeder | None | None | None | 46.43% | 0 | 0% | 2.24 | 1.03 | 45.98% | 0 | 0% | 2.24 | 1.03 | 45.98% | 0 | 0% | 2.24 | 1.03 | 45.98% | 0 | 0% | 2.24 | 1.03 | 45.98% | 0 | 0% | 2.24 | 1.04 | 46.43% | 0 | 0%
GNA_022700402_Capacity | Bay Area | Peninsula | SAN BRUNO 0402 | 22700402 | Feeder | None | None | None | 59.56% | 0 | 0% | 1.83 | 0.82 | 44.81% | 0 | 0% | 1.83 | 1.09 | 59.56% | 0 | 0% | 1.83 | 1.08 | 59.02% | 0 | 0% | 1.83 | 1.08 | 59.02% | 0 | 0% | 1.83 | 1.09 | 59.56% | 0 | 0%
GNA_022700403_Capacity | Bay Area | Peninsula | SAN BRUNO 0403 | 22700403 | Feeder | None | None | None | 53.12% | 0 | 0% | 2.24 | 1.16 | 51.79% | 0 | 0% | 2.24 | 1.16 | 51.79% | 0 | 0% | 2.24 | 1.15 | 51.34% | 0 | 0% | 2.24 | 1.16 | 51.79% | 0 | 0% | 2.24 | 1.19 | 53.12% | 0 | 0%
GNA_0226401_Capacity | Bay Area | Peninsula | DALY CITY BANK 1 | 226401 | Bank | None | None | None | 81.64% | 0 | 0% | 44.55 | 33.93 | 76.16% | 0 | 0% | 44.55 | 35.23 | 79.08% | 0 | 0% | 44.55 | 35.35 | 79.35% | 0 | 0% | 44.55 | 35.77 | 80.29% | 0 | 0% | 44.55 | 36.37 | 81.64% | 0 | 0%
GNA_022641104_Capacity | Bay Area | Peninsula | DALY CITY 1104 | 22641104 | Feeder | None | None | None | 79.77% | 0 | 0% | 12.06 | 9.23 | 76.53% | 0 | 0% | 12.06 | 9.3 | 77.11% | 0 | 0% | 12.06 | 9.35 | 77.53% | 0 | 0% | 12.06 | 9.45 | 78.36% | 0 | 0% | 12.06 | 9.62 | 79.77% | 0 | 0%
GNA_022641105_Capacity | Bay Area | Peninsula | DALY CITY 1105 | 22641105 | Feeder | None | None | None | 48.34% | 0 | 0% | 12.06 | 5.51 | 45.69% | 0 | 0% | 12.06 | 5.55 | 46.02% | 0 | 0% | 12.06 | 5.59 | 46.35% | 0 | 0% | 12.06 | 5.7 | 47.26% | 0 | 0% | 12.06 | 5.83 | 48.34% | 0 | 0%
GNA_022641107_Capacity | Bay Area | Peninsula | DALY CITY 1107 | 22641107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022641112_Capacity | Bay Area | Peninsula | DALY CITY 1112 | 22641112 | Feeder | None | None | None | 87.52% | 0 | 0% | 10.26 | 7.4 | 72.12% | 0 | 0% | 10.26 | 8.57 | 83.53% | 0 | 0% | 10.26 | 8.59 | 83.72% | 0 | 0% | 10.26 | 8.75 | 85.28% | 0 | 0% | 10.26 | 8.98 | 87.52% | 0 | 0%
GNA_0226402_Capacity | Bay Area | Peninsula | DALY CITY BANK 2 | 226402 | Bank | None | None | None | 57.13% | 0 | 0% | 44.55 | 25 | 56.12% | 0 | 0% | 44.55 | 23.98 | 53.83% | 0 | 0% | 44.55 | 24.48 | 54.95% | 0 | 0% | 44.55 | 24.89 | 55.87% | 0 | 0% | 44.55 | 25.45 | 57.13% | 0 | 0%
GNA_022641102_Capacity | Bay Area | Peninsula | DALY CITY 1102 | 22641102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0226003_Capacity | Bay Area | Peninsula | WESTLAKE BANK 3 | 226003 | Bank | None | None | None | 48.99% | 0 | 0% | 1.98 | 0.93 | 46.97% | 0 | 0% | 1.98 | 0.93 | 46.97% | 0 | 0% | 1.98 | 0.94 | 47.47% | 0 | 0% | 1.98 | 0.94 | 47.47% | 0 | 0% | 1.98 | 0.97 | 48.99% | 0 | 0%
GNA_022600403_Capacity | Bay Area | Peninsula | WESTLAKE 0403 | 22600403 | Feeder | None | None | None | 51.11% | 0 | 0% | 1.8 | 0.88 | 48.89% | 0 | 0% | 1.8 | 0.88 | 48.89% | 0 | 0% | 1.8 | 0.89 | 49.44% | 0 | 0% | 1.8 | 0.89 | 49.44% | 0 | 0% | 1.8 | 0.92 | 51.11% | 0 | 0%
GNA_022641108_Capacity | Bay Area | Peninsula | DALY CITY 1108 | 22641108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022641109_Capacity | Bay Area | Peninsula | DALY CITY 1109 | 22641109 | Feeder | None | None | None | 85.73% | 0 | 0% | 10.16 | 8.01 | 78.84% | 0 | 0% | 10.16 | 7.41 | 72.93% | 0 | 0% | 10.16 | 8.3 | 81.69% | 0 | 0% | 10.16 | 8.48 | 83.46% | 0 | 0% | 10.16 | 8.71 | 85.73% | 0 | 0%
GNA_0226801_Capacity | Bay Area | Peninsula | PLYMOUTH BANK 1 | 226801 | Bank | None | None | None | 81.58% | 0 | 0% | 2.28 | 1.86 | 81.58% | 0 | 0% | 2.28 | 1.64 | 71.93% | 0 | 0% | 2.28 | 1.66 | 72.81% | 0 | 0% | 2.28 | 1.72 | 75.44% | 0 | 0% | 2.28 | 1.84 | 80.7% | 0 | 0%
GNA_022680401_Capacity | Bay Area | Peninsula | PLYMOUTH 0401 | 22680401 | Feeder | None | None | None | 67.9% | 0 | 0% | 2.71 | 1.84 | 67.9% | 0 | 0% | 2.71 | 1.63 | 60.15% | 0 | 0% | 2.71 | 1.65 | 60.89% | 0 | 0% | 2.71 | 1.71 | 63.1% | 0 | 0% | 2.71 | 1.82 | 67.16% | 0 | 0%
GNA_0225901_Capacity | Bay Area | Peninsula | RANDOLPH BANK 1 | 225901 | Bank | None | None | None | 30.81% | 0 | 0% | 1.98 | 0.6 | 30.3% | 0 | 0% | 1.98 | 0.61 | 30.81% | 0 | 0% | 1.98 | 0.61 | 30.81% | 0 | 0% | 1.98 | 0.61 | 30.81% | 0 | 0% | 1.98 | 0.61 | 30.81% | 0 | 0%
GNA_022590401_Capacity | Bay Area | Peninsula | RANDOLPH 0401 | 22590401 | Feeder | None | None | None | 25.21% | 0 | 0% | 2.38 | 0.59 | 24.79% | 0 | 0% | 2.38 | 0.6 | 25.21% | 0 | 0% | 2.38 | 0.6 | 25.21% | 0 | 0% | 2.38 | 0.6 | 25.21% | 0 | 0% | 2.38 | 0.6 | 25.21% | 0 | 0%
GNA_0225902_Capacity | Bay Area | Peninsula | RANDOLPH BANK 2 | 225902 | Bank | None | None | None | 57.46% | 0 | 0% | 2.28 | 1.25 | 54.82% | 0 | 0% | 2.28 | 1.27 | 55.7% | 0 | 0% | 2.28 | 1.28 | 56.14% | 0 | 0% | 2.28 | 1.3 | 57.02% | 0 | 0% | 2.28 | 1.31 | 57.46% | 0 | 0%
GNA_022590402_Capacity | Bay Area | Peninsula | RANDOLPH 0402 | 22590402 | Feeder | None | None | None | 47.62% | 0 | 0% | 2.73 | 1.25 | 45.79% | 0 | 0% | 2.73 | 1.26 | 46.15% | 0 | 0% | 2.73 | 1.27 | 46.52% | 0 | 0% | 2.73 | 1.29 | 47.25% | 0 | 0% | 2.73 | 1.3 | 47.62% | 0 | 0%
GNA_0225903_Capacity | Bay Area | Peninsula | RANDOLPH BANK 3 | 225903 | Bank | None | None | None | 53.07% | 0 | 0% | 2.28 | 1.06 | 46.49% | 0 | 0% | 2.28 | 1.07 | 46.93% | 0 | 0% | 2.28 | 1.1 | 48.25% | 0 | 0% | 2.28 | 1.15 | 50.44% | 0 | 0% | 2.28 | 1.21 | 53.07% | 0 | 0%
GNA_022590403_Capacity | Bay Area | Peninsula | RANDOLPH 0403 | 22590403 | Feeder | None | None | None | 43.59% | 0 | 0% | 2.73 | 1.05 | 38.46% | 0 | 0% | 2.73 | 1.06 | 38.83% | 0 | 0% | 2.73 | 1.09 | 39.93% | 0 | 0% | 2.73 | 1.14 | 41.76% | 0 | 0% | 2.73 | 1.19 | 43.59% | 0 | 0%
GNA_022641110_Capacity | Bay Area | Peninsula | DALY CITY 1110 | 22641110 | Feeder | None | None | None | 90.98% | 0 | 0% | 12.19 | 11.09 | 90.98% | 0 | 0% | 12.19 | 11 | 90.24% | 0 | 0% | 12.19 | 10.92 | 89.58% | 0 | 0% | 12.19 | 10.85 | 89.01% | 0 | 0% | 12.19 | 10.82 | 88.76% | 0 | 0%
GNA_0226403_Capacity | Bay Area | Peninsula | DALY CITY BANK 3 | 226403 | Bank | None | None | None | 57.85% | 0 | 0% | 44.6 | 22.65 | 50.78% | 0 | 0% | 44.6 | 24.81 | 55.63% | 0 | 0% | 44.6 | 25 | 56.05% | 0 | 0% | 44.6 | 25.33 | 56.79% | 0 | 0% | 44.6 | 25.8 | 57.85% | 0 | 0%
GNA_022641101_Capacity | Bay Area | Peninsula | DALY CITY 1101 | 22641101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0226001_Capacity | Bay Area | Peninsula | WESTLAKE BANK 1 | 226001 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022600401_Capacity | Bay Area | Peninsula | WESTLAKE 0401 | 22600401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022641103_Capacity | Bay Area | Peninsula | DALY CITY 1103 | 22641103 | Feeder | None | None | None | 42.73% | 0 | 0% | 7.7 | 3.2 | 41.56% | 0 | 0% | 7.7 | 3.22 | 41.82% | 0 | 0% | 7.7 | 3.23 | 41.95% | 0 | 0% | 7.7 | 3.24 | 42.08% | 0 | 0% | 7.7 | 3.29 | 42.73% | 0 | 0%
GNA_0228501_Capacity | Bay Area | Peninsula | SULLIVAN BANK 1 | 228501 | Bank | None | None | None | 55.56% | 0 | 0% | 1.98 | 1.05 | 53.03% | 0 | 0% | 1.98 | 1.06 | 53.54% | 0 | 0% | 1.98 | 1.06 | 53.54% | 0 | 0% | 1.98 | 1.07 | 54.04% | 0 | 0% | 1.98 | 1.1 | 55.56% | 0 | 0%
GNA_022850402_Capacity | Bay Area | Peninsula | SULLIVAN 0402 | 22850402 | Feeder | None | None | None | 45.73% | 0 | 0% | 2.34 | 1.03 | 44.02% | 0 | 0% | 2.34 | 1.03 | 44.02% | 0 | 0% | 2.34 | 1.04 | 44.44% | 0 | 0% | 2.34 | 1.04 | 44.44% | 0 | 0% | 2.34 | 1.07 | 45.73% | 0 | 0%
GNA_022641106_Capacity | Bay Area | Peninsula | DALY CITY 1106 | 22641106 | Feeder | None | None | None | 58.34% | 0 | 0% | 11.57 | 4.75 | 41.05% | 0 | 0% | 11.57 | 6.31 | 54.54% | 0 | 0% | 11.57 | 6.39 | 55.23% | 0 | 0% | 11.57 | 6.56 | 56.7% | 0 | 0% | 11.57 | 6.75 | 58.34% | 0 | 0%
GNA_022641111_Capacity | Bay Area | Peninsula | DALY CITY 1111 | 22641111 | Feeder | None | None | None | 83.08% | 0 | 0% | 11.05 | 8.18 | 74.03% | 0 | 0% | 11.05 | 8.76 | 79.28% | 0 | 0% | 11.05 | 8.78 | 79.46% | 0 | 0% | 11.05 | 8.93 | 80.81% | 0 | 0% | 11.05 | 9.18 | 83.08% | 0 | 0%
GNA_0225102_Capacity | Bay Area | Peninsula | NORIEGA BANK 2 | 225102 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022510402_Capacity | Bay Area | Peninsula | NORIEGA 0402 | 22510402 | Feeder | None | None | None | 31.73% | 0 | 0% | 2.71 | 0.75 | 27.68% | 0 | 0% | 2.71 | 0.75 | 27.68% | 0 | 0% | 2.71 | 0.76 | 28.04% | 0 | 0% | 2.71 | 0.81 | 29.89% | 0 | 0% | 2.71 | 0.86 | 31.73% | 0 | 0%
GNA_0226501_Capacity | Bay Area | Peninsula | DALY CITY UNIT SUB | 226501 | Bank | None | None | None | 69.19% | 0 | 0% | 1.98 | 1.37 | 69.19% | 0 | 0% | 1.98 | 1.37 | 69.19% | 0 | 0% | 1.98 | 1.37 | 69.19% | 0 | 0% | 1.98 | 1.37 | 69.19% | 0 | 0% | 1.98 | 1.37 | 69.19% | 0 | 0%
GNA_022640401_Capacity | Bay Area | Peninsula | DALY CITY 0401 | 22640401 | Feeder | None | None | None | 44.78% | 0 | 0% | 2.97 | 1.33 | 44.78% | 0 | 0% | 2.97 | 1.33 | 44.78% | 0 | 0% | 2.97 | 1.33 | 44.78% | 0 | 0% | 2.97 | 1.33 | 44.78% | 0 | 0% | 2.97 | 1.33 | 44.78% | 0 | 0%
GNA_0228101_Capacity | Bay Area | Peninsula | PACIFICA BANK 1 | 228101 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022811101_Capacity | Bay Area | Peninsula | PACIFICA 1101 | 22811101 | Feeder | None | None | None | 48.58% | 0 | 0% | 6.67 | 3.05 | 45.73% | 0 | 0% | 6.67 | 3.06 | 45.88% | 0 | 0% | 6.67 | 3.1 | 46.48% | 0 | 0% | 6.67 | 3.15 | 47.23% | 0 | 0% | 6.67 | 3.24 | 48.58% | 0 | 0%
GNA_022811102_Capacity | Bay Area | Peninsula | PACIFICA 1102 | 22811102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0228102_Capacity | Bay Area | Peninsula | PACIFICA BANK 2 | 228102 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022811103_Capacity | Bay Area | Peninsula | PACIFICA 1103 | 22811103 | Feeder | None | None | None | 43.97% | 0 | 0% | 10.69 | 4.4 | 41.16% | 0 | 0% | 10.69 | 4.44 | 41.53% | 0 | 0% | 10.69 | 4.47 | 41.81% | 0 | 0% | 10.69 | 4.56 | 42.66% | 0 | 0% | 10.69 | 4.7 | 43.97% | 0 | 0%
GNA_022811104_Capacity | Bay Area | Peninsula | PACIFICA 1104 | 22811104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0228601_Capacity | Bay Area | Peninsula | SERRAMONTE BANK 1 | 228601 | Bank | None | None | None | 94.76% | 0 | 0% | 12.4 | 10.79 | 87.02% | 0 | 0% | 12.4 | 10.9 | 87.9% | 0 | 0% | 12.4 | 11.04 | 89.03% | 0 | 0% | 12.4 | 11.33 | 91.37% | 0 | 0% | 12.4 | 11.75 | 94.76% | 0 | 0%
GNA_022861103_Capacity | Bay Area | Peninsula | SERRAMONTE 1103 | 22861103 | Feeder | None | None | None | 50.48% | 0 | 0% | 11.57 | 5.43 | 46.93% | 0 | 0% | 11.57 | 5.49 | 47.45% | 0 | 0% | 11.57 | 5.55 | 47.97% | 0 | 0% | 11.57 | 5.69 | 49.18% | 0 | 0% | 11.57 | 5.84 | 50.48% | 0 | 0%
GNA_022861104_Capacity | Bay Area | Peninsula | SERRAMONTE 1104 | 22861104 | Feeder | None | None | None | 57.16% | 0 | 0% | 10.97 | 5.72 | 52.14% | 0 | 0% | 10.97 | 5.77 | 52.6% | 0 | 0% | 10.97 | 5.85 | 53.33% | 0 | 0% | 10.97 | 6 | 54.69% | 0 | 0% | 10.97 | 6.27 | 57.16% | 0 | 0%
GNA_0227201_Capacity | Bay Area | Peninsula | SNEATH LANE BANK 1 | 227201 | Bank | None | None | None | 56.26% | 0 | 0% | 29.7 | 16.07 | 54.11% | 0 | 0% | 29.7 | 16.13 | 54.31% | 0 | 0% | 29.7 | 16.23 | 54.65% | 0 | 0% | 29.7 | 16.45 | 55.39% | 0 | 0% | 29.7 | 16.71 | 56.26% | 0 | 0%
GNA_022721101_Capacity | Bay Area | Peninsula | SNEATH LANE 1101 | 22721101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022721102_Capacity | Bay Area | Peninsula | SNEATH LANE 1102 | 22721102 | Feeder | None | None | None | 60.33% | 0 | 0% | 7.31 | 3.85 | 52.67% | 0 | 0% | 7.31 | 3.9 | 53.35% | 0 | 0% | 7.31 | 4 | 54.72% | 0 | 0% | 7.31 | 4.18 | 57.18% | 0 | 0% | 7.31 | 4.41 | 60.33% | 0 | 0%
GNA_0227202_Capacity | Bay Area | Peninsula | SNEATH LANE BANK 2 | 227202 | Bank | None | None | None | 19.02% | 0 | 0% | 25.66 | 1.3 | 5.066% | 0 | 0% | 25.66 | 4.65 | 18.12% | 0 | 0% | 25.66 | 4.7 | 18.32% | 0 | 0% | 25.66 | 4.76 | 18.55% | 0 | 0% | 25.66 | 4.88 | 19.02% | 0 | 0%
GNA_022721106_Capacity | Bay Area | Peninsula | SNEATH LANE 1106 | 22721106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022721107_Capacity | Bay Area | Peninsula | SNEATH LANE 1107 | 22721107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0242602_Capacity | Bay Area | Peninsula | BAIR BANK 2 | 242602 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024261102_Capacity | Bay Area | Peninsula | BAIR 1102 | 24261102 | Feeder | None | None | None | 80.34% | 0 | 0% | 11.65 | 9.36 | 80.34% | 0 | 0% | 11.65 | 9.35 | 80.26% | 0 | 0% | 11.65 | 9.33 | 80.09% | 0 | 0% | 11.65 | 9.33 | 80.09% | 0 | 0% | 11.65 | 9.32 | 80% | 0 | 0%
GNA_0242603_Capacity | Bay Area | Peninsula | BAIR BANK 3 | 242603 | Bank | None | None | None | 57.93% | 0 | 0% | 44.55 | 22.21 | 49.85% | 0 | 0% | 44.55 | 24.99 | 56.09% | 0 | 0% | 44.55 | 25.29 | 56.77% | 0 | 0% | 44.55 | 25.64 | 57.55% | 0 | 0% | 44.55 | 25.81 | 57.93% | 0 | 0%
GNA_024261103_Capacity | Bay Area | Peninsula | BAIR 1103 | 24261103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024261104_Capacity | Bay Area | Peninsula | BAIR 1104 | 24261104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024261105_Capacity | Bay Area | Peninsula | BAIR 1105 | 24261105 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0240203_Capacity | Bay Area | Peninsula | BELLE HAVEN BANK 3 | 240203 | Bank | Demand Growth | Capacity | 2024 | 371.3% | 42.86 | 271.3% | 15.8 | 14.94 | 94.56% | 0 | 0% | 15.8 | 16.84 | 106.6% | 1.04 | 6.582% | 15.8 | 23.97 | 151.7% | 8.17 | 51.71% | 15.8 | 37 | 234.2% | 21.2 | 134.2% | 15.8 | 58.66 | 371.3% | 42.86 | 271.3%
GNA_024021103_Capacity | Bay Area | Peninsula | BELLE HAVEN 1103 | 24021103 | Feeder | Demand Growth | Capacity | 2025 | 134.3% | 4.18 | 34.29% | 12.19 | 8.75 | 71.78% | 0 | 0% | 12.19 | 9.63 | 79% | 0 | 0% | 12.19 | 13.8 | 113.2% | 1.61 | 13.21% | 12.19 | 16.27 | 133.5% | 4.08 | 33.47% | 12.19 | 16.37 | 134.3% | 4.18 | 34.29%
GNA_024021104_Capacity | Bay Area | Peninsula | BELLE HAVEN 1104 | 24021104 | Feeder | Demand Growth | Capacity | 2026 | 368.5% | 31.58 | 268.5% | 11.76 | 6.36 | 54.08% | 0 | 0% | 11.76 | 7.39 | 62.84% | 0 | 0% | 11.76 | 10.46 | 88.95% | 0 | 0% | 11.76 | 21.77 | 185.1% | 10.01 | 85.12% | 11.76 | 43.34 | 368.5% | 31.58 | 268.5%
GNA_0240204_Capacity | Bay Area | Peninsula | BELLE HAVEN BANK 4 | 240204 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024021101_Capacity | Bay Area | Peninsula | BELLE HAVEN 1101 | 24021101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024021102_Capacity | Bay Area | Peninsula | BELLE HAVEN 1102 | 24021102 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0240205_Capacity | Bay Area | Peninsula | BELLE HAVEN BANK 5 | 240205 | Bank | Demand Growth | Capacity | 2027 | 101% | 0.31 | 1.044% | 29.7 | 28.37 | 95.52% | 0 | 0% | 29.7 | 28.64 | 96.43% | 0 | 0% | 29.7 | 29.14 | 98.11% | 0 | 0% | 29.7 | 29.58 | 99.6% | 0 | 0% | 29.7 | 30.01 | 101% | 0.31 | 1.044%
GNA_024021105_Capacity | Bay Area | Peninsula | BELLE HAVEN 1105 | 24021105 | Feeder | Demand Growth | Capacity | 2023 | 129% | 3.54 | 29.04% | 12.19 | 13.87 | 113.8% | 1.68 | 13.78% | 12.19 | 14.33 | 117.6% | 2.14 | 17.56% | 12.19 | 14.95 | 122.6% | 2.76 | 22.64% | 12.19 | 15.34 | 125.8% | 3.15 | 25.84% | 12.19 | 15.73 | 129% | 3.54 | 29.04%
GNA_024021106_Capacity | Bay Area | Peninsula | BELLE HAVEN 1106 | 24021106 | Feeder | None | None | None | 99.59% | 0 | 0% | 12.19 | 12.14 | 99.59% | 0 | 0% | 12.19 | 12.1 | 99.26% | 0 | 0% | 12.19 | 12.06 | 98.93% | 0 | 0% | 12.19 | 12.05 | 98.85% | 0 | 0% | 12.19 | 12.01 | 98.52% | 0 | 0%
GNA_024021107_Capacity | Bay Area | Peninsula | BELLE HAVEN 1107 | 24021107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0240901_Capacity | Bay Area | Peninsula | GLENWOOD BANK 1 | 240901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024091101_Capacity | Bay Area | Peninsula | GLENWOOD 1101 | 24091101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0240903_Capacity | Bay Area | Peninsula | GLENWOOD BANK 3 | 240903 | Bank | None | None | None | 76.39% | 0 | 0% | 15.84 | 12.05 | 76.07% | 0 | 0% | 15.84 | 11.99 | 75.69% | 0 | 0% | 15.84 | 12.01 | 75.82% | 0 | 0% | 15.84 | 12.04 | 76.01% | 0 | 0% | 15.84 | 12.1 | 76.39% | 0 | 0%
GNA_024091102_Capacity | Bay Area | Peninsula | GLENWOOD 1102 | 24091102 | Feeder | None | None | None | 95% | 0 | 0% | 12.19 | 11.53 | 94.59% | 0 | 0% | 12.19 | 11.46 | 94.01% | 0 | 0% | 12.19 | 11.49 | 94.26% | 0 | 0% | 12.19 | 11.52 | 94.5% | 0 | 0% | 12.19 | 11.58 | 95% | 0 | 0%
GNA_0241601_Capacity | Bay Area | Peninsula | REDWOOD CITY BANK 1 | 241601 | Bank | None | None | None | 78.75% | 0 | 0% | 29.7 | 20.82 | 70.1% | 0 | 0% | 29.7 | 21.67 | 72.96% | 0 | 0% | 29.7 | 23.19 | 78.08% | 0 | 0% | 29.7 | 23.33 | 78.55% | 0 | 0% | 29.7 | 23.39 | 78.75% | 0 | 0%
GNA_024161101_Capacity | Bay Area | Peninsula | REDWOOD CITY 1101 | 24161101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024161102_Capacity | Bay Area | Peninsula | REDWOOD CITY 1102 | 24161102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0241602_Capacity | Bay Area | Peninsula | REDWOOD CITY BK 2 (12/4 kV) | 241602 | Bank | None | None | None | 42.26% | 0 | 0% | 15.83 | 6.6 | 41.69% | 0 | 0% | 15.83 | 6.61 | 41.76% | 0 | 0% | 15.83 | 6.61 | 41.76% | 0 | 0% | 15.83 | 6.66 | 42.07% | 0 | 0% | 15.83 | 6.69 | 42.26% | 0 | 0%
GNA_024160402_Capacity | Bay Area | Peninsula | REDWOOD CITY 0402 | 24160402 | Feeder | None | None | None | 49.12% | 0 | 0% | 2.85 | 1.4 | 49.12% | 0 | 0% | 2.85 | 1.4 | 49.12% | 0 | 0% | 2.85 | 1.39 | 48.77% | 0 | 0% | 2.85 | 1.39 | 48.77% | 0 | 0% | 2.85 | 1.39 | 48.77% | 0 | 0%
GNA_024160403_Capacity | Bay Area | Peninsula | REDWOOD CITY 0403 | 24160403 | Feeder | None | None | None | 75.46% | 0 | 0% | 2.73 | 2.03 | 74.36% | 0 | 0% | 2.73 | 2.04 | 74.73% | 0 | 0% | 2.73 | 2.05 | 75.09% | 0 | 0% | 2.73 | 2.05 | 75.09% | 0 | 0% | 2.73 | 2.06 | 75.46% | 0 | 0%
GNA_024160404_Capacity | Bay Area | Peninsula | REDWOOD CITY 0404 | 24160404 | Feeder | None | None | None | 46.38% | 0 | 0% | 2.35 | 1.09 | 46.38% | 0 | 0% | 2.35 | 1.08 | 45.96% | 0 | 0% | 2.35 | 1.08 | 45.96% | 0 | 0% | 2.35 | 1.07 | 45.53% | 0 | 0% | 2.35 | 1.07 | 45.53% | 0 | 0%
GNA_024160405_Capacity | Bay Area | Peninsula | REDWOOD CITY 0405 | 24160405 | Feeder | None | None | None | 74.07% | 0 | 0% | 2.7 | 1.94 | 71.85% | 0 | 0% | 2.7 | 1.94 | 71.85% | 0 | 0% | 2.7 | 1.95 | 72.22% | 0 | 0% | 2.7 | 1.99 | 73.7% | 0 | 0% | 2.7 | 2 | 74.07% | 0 | 0%
GNA_0241604_Capacity | Bay Area | Peninsula | REDWOOD CITY BANK 4 | 241604 | Bank | Demand Growth | Capacity | 2023 | 110.5% | 0.99 | 10.53% | 9.4 | 10.11 | 107.6% | 0.71 | 7.553% | 9.4 | 10.19 | 108.4% | 0.79 | 8.404% | 9.4 | 10.27 | 109.3% | 0.87 | 9.255% | 9.4 | 10.33 | 109.9% | 0.93 | 9.894% | 9.4 | 10.39 | 110.5% | 0.99 | 10.53%
GNA_024161103_Capacity | Bay Area | Peninsula | REDWOOD CITY 1103 | 24161103 | Feeder | None | None | None | 88.11% | 0 | 0% | 12.19 | 10.45 | 85.73% | 0 | 0% | 12.19 | 10.54 | 86.46% | 0 | 0% | 12.19 | 10.62 | 87.12% | 0 | 0% | 12.19 | 10.68 | 87.61% | 0 | 0% | 12.19 | 10.74 | 88.11% | 0 | 0%
GNA_0241605_Capacity | Bay Area | Peninsula | REDWOOD CITY BANK 5 | 241605 | Bank | Demand Growth | Capacity | 2023 | 127.1% | 8.05 | 27.1% | 29.7 | 31.62 | 106.5% | 1.92 | 6.465% | 29.7 | 34.49 | 116.1% | 4.79 | 16.13% | 29.7 | 36.17 | 121.8% | 6.47 | 21.78% | 29.7 | 37.63 | 126.7% | 7.93 | 26.7% | 29.7 | 37.75 | 127.1% | 8.05 | 27.1%
GNA_0241603_Capacity | Bay Area | Peninsula | REDWOOD CITY BANK 3 (12/4KV) | 241603 | Bank | None | None | None | 78.15% | 0 | 0% | 12.4 | 9.52 | 76.77% | 0 | 0% | 12.4 | 9.54 | 76.94% | 0 | 0% | 12.4 | 9.56 | 77.1% | 0 | 0% | 12.4 | 9.61 | 77.5% | 0 | 0% | 12.4 | 9.69 | 78.15% | 0 | 0%
GNA_024160406_Capacity | Bay Area | Peninsula | REDWOOD CITY 0406 | 24160406 | Feeder | None | None | None | 87.91% | 0 | 0% | 2.73 | 2.36 | 86.45% | 0 | 0% | 2.73 | 2.36 | 86.45% | 0 | 0% | 2.73 | 2.36 | 86.45% | 0 | 0% | 2.73 | 2.38 | 87.18% | 0 | 0% | 2.73 | 2.4 | 87.91% | 0 | 0%
GNA_024160408_Capacity | Bay Area | Peninsula | REDWOOD CITY 0408 | 24160408 | Feeder | None | None | None | 59.33% | 0 | 0% | 3.27 | 1.89 | 57.8% | 0 | 0% | 3.27 | 1.89 | 57.8% | 0 | 0% | 3.27 | 1.89 | 57.8% | 0 | 0% | 3.27 | 1.91 | 58.41% | 0 | 0% | 3.27 | 1.94 | 59.33% | 0 | 0%
GNA_024160409_Capacity | Bay Area | Peninsula | REDWOOD CITY 0409 | 24160409 | Feeder | None | None | None | 75.82% | 0 | 0% | 2.73 | 2.03 | 74.36% | 0 | 0% | 2.73 | 2.03 | 74.36% | 0 | 0% | 2.73 | 2.04 | 74.73% | 0 | 0% | 2.73 | 2.05 | 75.09% | 0 | 0% | 2.73 | 2.07 | 75.82% | 0 | 0%
GNA_024160410_Capacity | Bay Area | Peninsula | REDWOOD CITY 0410 | 24160410 | Feeder | None | None | None | 78.72% | 0 | 0% | 2.35 | 1.84 | 78.3% | 0 | 0% | 2.35 | 1.84 | 78.3% | 0 | 0% | 2.35 | 1.84 | 78.3% | 0 | 0% | 2.35 | 1.84 | 78.3% | 0 | 0% | 2.35 | 1.85 | 78.72% | 0 | 0%
GNA_024161104_Capacity | Bay Area | Peninsula | REDWOOD CITY 1104 | 24161104 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024161105_Capacity | Bay Area | Peninsula | REDWOOD CITY 1105 | 24161105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0241303_Capacity | Bay Area | Peninsula | MENLO BANK 3 | 241303 | Bank | None | None | None | 99.68% | 0 | 0% | 15.8 | 15.75 | 99.68% | 0 | 0% | 15.8 | 15.3 | 96.84% | 0 | 0% | 15.8 | 14.76 | 93.42% | 0 | 0% | 15.8 | 14.97 | 94.75% | 0 | 0% | 15.8 | 15.34 | 97.09% | 0 | 0%
GNA_024131101_Capacity | Bay Area | Peninsula | MENLO 1101 | 24131101 | Feeder | None | None | None | 74.8% | 0 | 0% | 10.16 | 7.6 | 74.8% | 0 | 0% | 10.16 | 7.52 | 74.02% | 0 | 0% | 10.16 | 7.47 | 73.52% | 0 | 0% | 10.16 | 7.42 | 73.03% | 0 | 0% | 10.16 | 7.46 | 73.43% | 0 | 0%
GNA_024131102_Capacity | Bay Area | Peninsula | MENLO 1102 | 24131102 | Feeder | None | None | None | 66.44% | 0 | 0% | 10.28 | 6.79 | 66.05% | 0 | 0% | 10.28 | 6.42 | 62.45% | 0 | 0% | 10.28 | 6.41 | 62.35% | 0 | 0% | 10.28 | 6.61 | 64.3% | 0 | 0% | 10.28 | 6.83 | 66.44% | 0 | 0%
GNA_0241304_Capacity | Bay Area | Peninsula | MENLO BANK 4 | 241304 | Bank | Demand Growth | Capacity | 2023 | 104.6% | 0.72 | 4.557% | 15.8 | 16.05 | 101.6% | 0.25 | 1.582% | 15.8 | 16.26 | 102.9% | 0.46 | 2.911% | 15.8 | 16.52 | 104.6% | 0.72 | 4.557% | 15.8 | 14.12 | 89.37% | 0 | 0% | 15.8 | 14.5 | 91.77% | 0 | 0%
GNA_024131103_Capacity | Bay Area | Peninsula | MENLO 1103 | 24131103 | Feeder | None | None | None | 69.88% | 0 | 0% | 10.16 | 6.27 | 61.71% | 0 | 0% | 10.16 | 6.51 | 64.07% | 0 | 0% | 10.16 | 6.7 | 65.94% | 0 | 0% | 10.16 | 6.88 | 67.72% | 0 | 0% | 10.16 | 7.1 | 69.88% | 0 | 0%
GNA_024131104_Capacity | Bay Area | Peninsula | MENLO 1104 | 24131104 | Feeder | None | None | None | 98.23% | 0 | 0% | 10.16 | 9.98 | 98.23% | 0 | 0% | 10.16 | 9.9 | 97.44% | 0 | 0% | 10.16 | 9.89 | 97.34% | 0 | 0% | 10.16 | 7.3 | 71.85% | 0 | 0% | 10.16 | 7.42 | 73.03% | 0 | 0%
GNA_0241802_Capacity | Bay Area | Peninsula | SAN CARLOS BANK 2 | 241802 | Bank | Demand Growth | Capacity | 2023 | 121.1% | 3.33 | 21.08% | 15.8 | 18.67 | 118.2% | 2.87 | 18.16% | 15.8 | 19.13 | 121.1% | 3.33 | 21.08% | 15.8 | 19.02 | 120.4% | 3.22 | 20.38% | 15.8 | 18.93 | 119.8% | 3.13 | 19.81% | 15.8 | 18.84 | 119.2% | 3.04 | 19.24%
GNA_024181102_Capacity | Bay Area | Peninsula | SAN CARLOS 1102 | 24181102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024181104_Capacity | Bay Area | Peninsula | SAN CARLOS 1104 | 24181104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0241803_Capacity | Bay Area | Peninsula | SAN CARLOS BANK 3 | 241803 | Bank | Demand Growth | Capacity | 2023 | 130.6% | 3.8 | 30.65% | 12.4 | 14.57 | 117.5% | 2.17 | 17.5% | 12.4 | 14.39 | 116% | 1.99 | 16.05% | 12.4 | 16.2 | 130.6% | 3.8 | 30.65% | 12.4 | 16.15 | 130.2% | 3.75 | 30.24% | 12.4 | 16.17 | 130.4% | 3.77 | 30.4%
GNA_024181101_Capacity | Bay Area | Peninsula | SAN CARLOS 1101 | 24181101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024181103_Capacity | Bay Area | Peninsula | SAN CARLOS 1103 | 24181103 | Feeder | None | None | None | 88.11% | 0 | 0% | 12.19 | 10.74 | 88.11% | 0 | 0% | 12.19 | 10.62 | 87.12% | 0 | 0% | 12.19 | 10.52 | 86.3% | 0 | 0% | 12.19 | 10.54 | 86.46% | 0 | 0% | 12.19 | 10.61 | 87.04% | 0 | 0%
GNA_0242501_Capacity | Bay Area | Peninsula | WOODSIDE BANK 1 | 242501 | Bank | None | None | None | 69.35% | 0 | 0% | 29.69 | 17.42 | 58.67% | 0 | 0% | 29.69 | 17.47 | 58.84% | 0 | 0% | 29.69 | 17.48 | 58.88% | 0 | 0% | 29.69 | 20.35 | 68.54% | 0 | 0% | 29.69 | 20.59 | 69.35% | 0 | 0%
GNA_024251101_Capacity | Bay Area | Peninsula | WOODSIDE 1101 | 24251101 | Feeder | None | None | None | 65.41% | 0 | 0% | 11.65 | 7.38 | 63.35% | 0 | 0% | 11.65 | 7.41 | 63.61% | 0 | 0% | 11.65 | 7.43 | 63.78% | 0 | 0% | 11.65 | 7.52 | 64.55% | 0 | 0% | 11.65 | 7.62 | 65.41% | 0 | 0%
GNA_024251102_Capacity | Bay Area | Peninsula | WOODSIDE 1102 | 24251102 | Feeder | None | None | None | 99.45% | 0 | 0% | 12.83 | 10.05 | 78.33% | 0 | 0% | 12.83 | 10 | 77.94% | 0 | 0% | 12.83 | 9.91 | 77.24% | 0 | 0% | 12.83 | 12.65 | 98.6% | 0 | 0% | 12.83 | 12.76 | 99.45% | 0 | 0%
GNA_0242502_Capacity | Bay Area | Peninsula | WOODSIDE BANK 2 | 242502 | Bank | None | None | None | 60.88% | 0 | 0% | 29.7 | 17.77 | 59.83% | 0 | 0% | 29.7 | 17.79 | 59.9% | 0 | 0% | 29.7 | 17.81 | 59.97% | 0 | 0% | 29.7 | 17.93 | 60.37% | 0 | 0% | 29.7 | 18.08 | 60.88% | 0 | 0%
GNA_024251104_Capacity | Bay Area | Peninsula | WOODSIDE 1104 | 24251104 | Feeder | None | None | None | 92.96% | 0 | 0% | 11.65 | 10.63 | 91.24% | 0 | 0% | 11.65 | 10.64 | 91.33% | 0 | 0% | 11.65 | 10.62 | 91.16% | 0 | 0% | 11.65 | 10.72 | 92.02% | 0 | 0% | 11.65 | 10.83 | 92.96% | 0 | 0%
GNA_024251105_Capacity | Bay Area | Peninsula | WOODSIDE 1105 | 24251105 | Feeder | None | None | None | 55.18% | 0 | 0% | 11.4 | 6.29 | 55.18% | 0 | 0% | 11.4 | 6.22 | 54.56% | 0 | 0% | 11.4 | 6.18 | 54.21% | 0 | 0% | 11.4 | 6.16 | 54.04% | 0 | 0% | 11.4 | 6.16 | 54.04% | 0 | 0%
GNA_0240201_Capacity | Bay Area | Peninsula | BELLE HAVEN BANK 1 | 240201 | Bank | Demand Growth | Capacity | 2027 | 100.6% | 0.04 | 0.5682% | 7.04 | 6.35 | 90.2% | 0 | 0% | 7.04 | 6.65 | 94.46% | 0 | 0% | 7.04 | 6.46 | 91.76% | 0 | 0% | 7.04 | 6.78 | 96.31% | 0 | 0% | 7.04 | 7.08 | 100.6% | 0.04 | 0.5682%
GNA_024020401_Capacity | Bay Area | Peninsula | BELLE HAVEN 0401 | 24020401 | Feeder | Demand Growth | Capacity | 2026 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024020402_Capacity | Bay Area | Peninsula | BELLE HAVEN 0402 | 24020402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024020403_Capacity | Bay Area | Peninsula | BELLE HAVEN 0403 | 24020403 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024020404_Capacity | Bay Area | Peninsula | BELLE HAVEN 0404 | 24020404 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0240202_Capacity | Bay Area | Peninsula | BELLE HAVEN BANK 2 | 240202 | Bank | Demand Growth | Capacity | 2023 | 130.5% | 2.15 | 30.5% | 7.05 | 8.36 | 118.6% | 1.31 | 18.58% | 7.05 | 8.57 | 121.6% | 1.52 | 21.56% | 7.05 | 8.77 | 124.4% | 1.72 | 24.4% | 7.05 | 8.98 | 127.4% | 1.93 | 27.38% | 7.05 | 9.2 | 130.5% | 2.15 | 30.5%
GNA_024020405_Capacity | Bay Area | Peninsula | BELLE HAVEN 0405 | 24020405 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024020406_Capacity | Bay Area | Peninsula | BELLE HAVEN 0406 | 24020406 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024020407_Capacity | Bay Area | Peninsula | BELLE HAVEN 0407 | 24020407 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024020408_Capacity | Bay Area | Peninsula | BELLE HAVEN 0408 | 24020408 | Feeder | None | None | None | 73.08% | 0 | 0% | 2.34 | 1.59 | 67.95% | 0 | 0% | 2.34 | 1.61 | 68.8% | 0 | 0% | 2.34 | 1.64 | 70.09% | 0 | 0% | 2.34 | 1.67 | 71.37% | 0 | 0% | 2.34 | 1.71 | 73.08% | 0 | 0%
GNA_024020409_Capacity | Bay Area | Peninsula | BELLE HAVEN 0409 | 24020409 | Feeder | None | None | None | 93.59% | 0 | 0% | 2.34 | 1.93 | 82.48% | 0 | 0% | 2.34 | 2.01 | 85.9% | 0 | 0% | 2.34 | 2.09 | 89.32% | 0 | 0% | 2.34 | 2.14 | 91.45% | 0 | 0% | 2.34 | 2.19 | 93.59% | 0 | 0%
GNA_0240801_Capacity | Bay Area | Peninsula | EMERALD LAKE BANK 1 | 240801 | Bank | None | None | None | 61.45% | 0 | 0% | 6.9 | 4.09 | 59.28% | 0 | 0% | 6.9 | 4.1 | 59.42% | 0 | 0% | 6.9 | 4.13 | 59.86% | 0 | 0% | 6.9 | 4.18 | 60.58% | 0 | 0% | 6.9 | 4.24 | 61.45% | 0 | 0%
GNA_024080401_Capacity | Bay Area | Peninsula | EMERALD LAKE 0401 | 24080401 | Feeder | Demand Growth | Capacity | 2023 | 109.2% | 0.21 | 9.211% | 2.28 | 2.4 | 105.3% | 0.12 | 5.263% | 2.28 | 2.41 | 105.7% | 0.13 | 5.702% | 2.28 | 2.42 | 106.1% | 0.14 | 6.14% | 2.28 | 2.44 | 107% | 0.16 | 7.018% | 2.28 | 2.49 | 109.2% | 0.21 | 9.211%
GNA_024080402_Capacity | Bay Area | Peninsula | EMERALD LAKE 0402 | 24080402 | Feeder | None | None | None | 77.63% | 0 | 0% | 2.28 | 1.7 | 74.56% | 0 | 0% | 2.28 | 1.71 | 75% | 0 | 0% | 2.28 | 1.73 | 75.88% | 0 | 0% | 2.28 | 1.75 | 76.75% | 0 | 0% | 2.28 | 1.77 | 77.63% | 0 | 0%
GNA_0240902_Capacity | Bay Area | Peninsula | GLENWOOD BANK 2 | 240902 | Bank | None | None | None | 96.97% | 0 | 0% | 6.93 | 6.72 | 96.97% | 0 | 0% | 6.93 | 6.46 | 93.22% | 0 | 0% | 6.93 | 6.34 | 91.49% | 0 | 0% | 6.93 | 6.43 | 92.78% | 0 | 0% | 6.93 | 6.53 | 94.23% | 0 | 0%
GNA_024090404_Capacity | Bay Area | Peninsula | GLENWOOD 0404 | 24090404 | Feeder | None | None | None | 90.65% | 0 | 0% | 2.78 | 2.52 | 90.65% | 0 | 0% | 2.78 | 2.4 | 86.33% | 0 | 0% | 2.78 | 2.42 | 87.05% | 0 | 0% | 2.78 | 2.45 | 88.13% | 0 | 0% | 2.78 | 2.5 | 89.93% | 0 | 0%
GNA_024090405_Capacity | Bay Area | Peninsula | GLENWOOD 0405 | 24090405 | Feeder | None | None | None | 97.84% | 0 | 0% | 2.78 | 2.61 | 93.88% | 0 | 0% | 2.78 | 2.62 | 94.24% | 0 | 0% | 2.78 | 2.66 | 95.68% | 0 | 0% | 2.78 | 2.69 | 96.76% | 0 | 0% | 2.78 | 2.72 | 97.84% | 0 | 0%
GNA_024090406_Capacity | Bay Area | Peninsula | GLENWOOD 0406 | 24090406 | Feeder | None | None | None | 51.82% | 0 | 0% | 3.3 | 1.63 | 49.39% | 0 | 0% | 3.3 | 1.66 | 50.3% | 0 | 0% | 3.3 | 1.67 | 50.61% | 0 | 0% | 3.3 | 1.7 | 51.52% | 0 | 0% | 3.3 | 1.71 | 51.82% | 0 | 0%
GNA_0241201_Capacity | Bay Area | Peninsula | LAS PULGAS BANK 1 | 241201 | Bank | None | None | None | 80.87% | 0 | 0% | 6.9 | 5.48 | 79.42% | 0 | 0% | 6.9 | 5.5 | 79.71% | 0 | 0% | 6.9 | 5.5 | 79.71% | 0 | 0% | 6.9 | 5.53 | 80.14% | 0 | 0% | 6.9 | 5.58 | 80.87% | 0 | 0%
GNA_024120401_Capacity | Bay Area | Peninsula | LAS PULGAS 0401 | 24120401 | Feeder | Demand Growth | Capacity | 2023 | 107% | 0.23 | 7.034% | 3.27 | 3.42 | 104.6% | 0.15 | 4.587% | 3.27 | 3.44 | 105.2% | 0.17 | 5.199% | 3.27 | 3.44 | 105.2% | 0.17 | 5.199% | 3.27 | 3.46 | 105.8% | 0.19 | 5.81% | 3.27 | 3.5 | 107% | 0.23 | 7.034%
GNA_024120402_Capacity | Bay Area | Peninsula | LAS PULGAS 0402 | 24120402 | Feeder | None | None | None | 56.48% | 0 | 0% | 3.24 | 1.8 | 55.56% | 0 | 0% | 3.24 | 1.81 | 55.86% | 0 | 0% | 3.24 | 1.81 | 55.86% | 0 | 0% | 3.24 | 1.82 | 56.17% | 0 | 0% | 3.24 | 1.83 | 56.48% | 0 | 0%
GNA_0241202_Capacity | Bay Area | Peninsula | LAS PULGAS BANK 2 | 241202 | Bank | None | None | None | 86.09% | 0 | 0% | 6.9 | 5.81 | 84.2% | 0 | 0% | 6.9 | 5.83 | 84.49% | 0 | 0% | 6.9 | 5.85 | 84.78% | 0 | 0% | 6.9 | 5.88 | 85.22% | 0 | 0% | 6.9 | 5.94 | 86.09% | 0 | 0%
GNA_024120403_Capacity | Bay Area | Peninsula | LAS PULGAS 0403 | 24120403 | Feeder | None | None | None | 99.38% | 0 | 0% | 3.24 | 3.14 | 96.91% | 0 | 0% | 3.24 | 3.14 | 96.91% | 0 | 0% | 3.24 | 3.15 | 97.22% | 0 | 0% | 3.24 | 3.18 | 98.15% | 0 | 0% | 3.24 | 3.22 | 99.38% | 0 | 0%
GNA_024120404_Capacity | Bay Area | Peninsula | LAS PULGAS 0404 | 24120404 | Feeder | None | None | None | 69.54% | 0 | 0% | 3.48 | 2.37 | 68.1% | 0 | 0% | 3.48 | 2.38 | 68.39% | 0 | 0% | 3.48 | 2.39 | 68.68% | 0 | 0% | 3.48 | 2.39 | 68.68% | 0 | 0% | 3.48 | 2.42 | 69.54% | 0 | 0%
GNA_0241301_Capacity | Bay Area | Peninsula | MENLO BANK 1 | 241301 | Bank | None | None | None | 54.16% | 0 | 0% | 12.37 | 6.3 | 50.93% | 0 | 0% | 12.37 | 6.4 | 51.74% | 0 | 0% | 12.37 | 6.47 | 52.3% | 0 | 0% | 12.37 | 6.58 | 53.19% | 0 | 0% | 12.37 | 6.7 | 54.16% | 0 | 0%
GNA_024130401_Capacity | Bay Area | Peninsula | MENLO 0401 | 24130401 | Feeder | None | None | None | 73.57% | 0 | 0% | 3.33 | 2.26 | 67.87% | 0 | 0% | 3.33 | 2.32 | 69.67% | 0 | 0% | 3.33 | 2.34 | 70.27% | 0 | 0% | 3.33 | 2.41 | 72.37% | 0 | 0% | 3.33 | 2.45 | 73.57% | 0 | 0%
GNA_024130403_Capacity | Bay Area | Peninsula | MENLO 0403 | 24130403 | Feeder | Demand Growth | Capacity | 2027 | 100.6% | 0.02 | 0.6369% | 3.14 | 2.96 | 94.27% | 0 | 0% | 3.14 | 3 | 95.54% | 0 | 0% | 3.14 | 3.05 | 97.13% | 0 | 0% | 3.14 | 3.09 | 98.41% | 0 | 0% | 3.14 | 3.16 | 100.6% | 0.02 | 0.6369%
GNA_0241302_Capacity | Bay Area | Peninsula | MENLO BANK 2 | 241302 | Bank | None | None | None | 93.72% | 0 | 0% | 4.94 | 4.39 | 88.87% | 0 | 0% | 4.94 | 4.45 | 90.08% | 0 | 0% | 4.94 | 4.5 | 91.09% | 0 | 0% | 4.94 | 4.57 | 92.51% | 0 | 0% | 4.94 | 4.63 | 93.72% | 0 | 0%
GNA_024130402_Capacity | Bay Area | Peninsula | MENLO 0402 | 24130402 | Feeder | None | None | None | 75.38% | 0 | 0% | 3.33 | 2.44 | 73.27% | 0 | 0% | 3.33 | 2.46 | 73.87% | 0 | 0% | 3.33 | 2.48 | 74.47% | 0 | 0% | 3.33 | 2.49 | 74.77% | 0 | 0% | 3.33 | 2.51 | 75.38% | 0 | 0%
GNA_024130404_Capacity | Bay Area | Peninsula | MENLO 0404 | 24130404 | Feeder | None | None | None | 94.42% | 0 | 0% | 3.94 | 3.55 | 90.1% | 0 | 0% | 3.94 | 3.58 | 90.86% | 0 | 0% | 3.94 | 3.62 | 91.88% | 0 | 0% | 3.94 | 3.67 | 93.15% | 0 | 0% | 3.94 | 3.72 | 94.42% | 0 | 0%
GNA_0241801_Capacity | Bay Area | Peninsula | SAN CARLOS BANK 1 | 241801 | Bank | Demand Growth | Capacity | 2023 | 103.5% | 0.41 | 3.463% | 11.84 | 12.25 | 103.5% | 0.41 | 3.463% | 11.84 | 12.04 | 101.7% | 0.2 | 1.689% | 11.84 | 11.83 | 99.92% | 0 | 0% | 11.84 | 11.64 | 98.31% | 0 | 0% | 11.84 | 11.39 | 96.2% | 0 | 0%
GNA_024180401_Capacity | Bay Area | Peninsula | SAN CARLOS 0401 | 24180401 | Feeder | None | None | None | 59.57% | 0 | 0% | 2.35 | 1.4 | 59.57% | 0 | 0% | 2.35 | 1.39 | 59.15% | 0 | 0% | 2.35 | 1.39 | 59.15% | 0 | 0% | 2.35 | 1.39 | 59.15% | 0 | 0% | 2.35 | 1.39 | 59.15% | 0 | 0%
GNA_024180402_Capacity | Bay Area | Peninsula | SAN CARLOS 0402 | 24180402 | Feeder | None | None | None | 88.09% | 0 | 0% | 2.35 | 2.07 | 88.09% | 0 | 0% | 2.35 | 2.06 | 87.66% | 0 | 0% | 2.35 | 2.06 | 87.66% | 0 | 0% | 2.35 | 2.05 | 87.23% | 0 | 0% | 2.35 | 2.05 | 87.23% | 0 | 0%
GNA_024180403_Capacity | Bay Area | Peninsula | SAN CARLOS 0403 | 24180403 | Feeder | None | None | None | 89.12% | 0 | 0% | 2.85 | 2.54 | 89.12% | 0 | 0% | 2.85 | 2.51 | 88.07% | 0 | 0% | 2.85 | 2.5 | 87.72% | 0 | 0% | 2.85 | 2.45 | 85.96% | 0 | 0% | 2.85 | 2.4 | 84.21% | 0 | 0%
GNA_024180404_Capacity | Bay Area | Peninsula | SAN CARLOS 0404 | 24180404 | Feeder | None | None | None | 92.93% | 0 | 0% | 2.97 | 2.74 | 92.26% | 0 | 0% | 2.97 | 2.74 | 92.26% | 0 | 0% | 2.97 | 2.74 | 92.26% | 0 | 0% | 2.97 | 2.76 | 92.93% | 0 | 0% | 2.97 | 2.76 | 92.93% | 0 | 0%
GNA_024180405_Capacity | Bay Area | Peninsula | SAN CARLOS 0405 | 24180405 | Feeder | Demand Growth | Capacity | 2023 | 102.6% | 0.06 | 2.632% | 2.28 | 2.34 | 102.6% | 0.06 | 2.632% | 2.28 | 2.25 | 98.68% | 0 | 0% | 2.28 | 2.21 | 96.93% | 0 | 0% | 2.28 | 2.2 | 96.49% | 0 | 0% | 2.28 | 2.23 | 97.81% | 0 | 0%
GNA_024180406_Capacity | Bay Area | Peninsula | SAN CARLOS 0406 | 24180406 | Feeder | None | None | None | 95.74% | 0 | 0% | 2.35 | 2.25 | 95.74% | 0 | 0% | 2.35 | 2.2 | 93.62% | 0 | 0% | 2.35 | 2.12 | 90.21% | 0 | 0% | 2.35 | 2.07 | 88.09% | 0 | 0% | 2.35 | 2.07 | 88.09% | 0 | 0%
GNA_0242401_Capacity | Bay Area | Peninsula | WATERSHED BANK 1 | 242401 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_024240402_Capacity | Bay Area | Peninsula | WATERSHED 0402 | 24240402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0241001_Capacity | Bay Area | Peninsula | HALF MOON BAY BANK 1 | 241001 | Bank | None | None | None | 29.54% | 0 | 0% | 29.69 | 7.26 | 24.45% | 0 | 0% | 29.69 | 7.54 | 25.4% | 0 | 0% | 29.69 | 7.82 | 26.34% | 0 | 0% | 29.69 | 8.26 | 27.82% | 0 | 0% | 29.69 | 8.77 | 29.54% | 0 | 0%
GNA_024101102_Capacity | Bay Area | Peninsula | HALF MOON BAY 1102 | 24101102 | Feeder | None | None | None | 73.01% | 0 | 0% | 12.19 | 7.4 | 60.71% | 0 | 0% | 12.19 | 7.67 | 62.92% | 0 | 0% | 12.19 | 7.96 | 65.3% | 0 | 0% | 12.19 | 8.39 | 68.83% | 0 | 0% | 12.19 | 8.9 | 73.01% | 0 | 0%
GNA_0241002_Capacity | Bay Area | Peninsula | HALF MOON BAY BANK 2 | 241002 | Bank | None | None | None | 59.81% | 0 | 0% | 10.4 | 5.43 | 52.21% | 0 | 0% | 10.4 | 5.73 | 55.1% | 0 | 0% | 10.4 | 5.84 | 56.15% | 0 | 0% | 10.4 | 5.99 | 57.6% | 0 | 0% | 10.4 | 6.22 | 59.81% | 0 | 0%
GNA_024101101_Capacity | Bay Area | Peninsula | HALF MOON BAY 1101 | 24101101 | Feeder | None | None | None | 51.76% | 0 | 0% | 12.19 | 5.51 | 45.2% | 0 | 0% | 12.19 | 5.82 | 47.74% | 0 | 0% | 12.19 | 5.93 | 48.65% | 0 | 0% | 12.19 | 6.08 | 49.88% | 0 | 0% | 12.19 | 6.31 | 51.76% | 0 | 0%
GNA_0241003_Capacity | Bay Area | Peninsula | HALF MOON BAY BANK 3 | 241003 | Bank | None | None | None | 25.46% | 0 | 0% | 29.69 | 7.13 | 24.01% | 0 | 0% | 29.69 | 7.19 | 24.22% | 0 | 0% | 29.69 | 7.25 | 24.42% | 0 | 0% | 29.69 | 7.43 | 25.03% | 0 | 0% | 29.69 | 7.56 | 25.46% | 0 | 0%
GNA_024101103_Capacity | Bay Area | Peninsula | HALF MOON BAY 1103 | 24101103 | Feeder | None | None | None | 58.3% | 0 | 0% | 12.83 | 7.05 | 54.95% | 0 | 0% | 12.83 | 7.11 | 55.42% | 0 | 0% | 12.83 | 7.17 | 55.88% | 0 | 0% | 12.83 | 7.35 | 57.29% | 0 | 0% | 12.83 | 7.48 | 58.3% | 0 | 0%
GNA_0620401_Capacity | North Valley and Sierra | Sacramento | DAVIS BANK 1 | 620401 | Bank | None | None | None | 95.71% | 0 | 0% | 44.53 | 42.62 | 95.71% | 0 | 0% | 44.53 | 42.32 | 95.04% | 0 | 0% | 44.53 | 42.1 | 94.54% | 0 | 0% | 44.53 | 42.08 | 94.5% | 0 | 0% | 44.53 | 42.39 | 95.19% | 0 | 0%
GNA_062041101_Capacity | North Valley and Sierra | Sacramento | DAVIS 1101 | 62041101 | Feeder | None | None | None | 79.13% | 0 | 0% | 12.36 | 9.62 | 77.83% | 0 | 0% | 12.36 | 9.62 | 77.83% | 0 | 0% | 12.36 | 9.63 | 77.91% | 0 | 0% | 12.36 | 9.68 | 78.32% | 0 | 0% | 12.36 | 9.78 | 79.13% | 0 | 0%
GNA_062041102_Capacity | North Valley and Sierra | Sacramento | DAVIS 1102 | 62041102 | Feeder | None | None | None | 93.11% | 0 | 0% | 12.19 | 11.35 | 93.11% | 0 | 0% | 12.19 | 11.27 | 92.45% | 0 | 0% | 12.19 | 11.13 | 91.3% | 0 | 0% | 12.19 | 11.07 | 90.81% | 0 | 0% | 12.19 | 11.18 | 91.71% | 0 | 0%
GNA_062041103_Capacity | North Valley and Sierra | Sacramento | DAVIS 1103 | 62041103 | Feeder | None | None | None | 92.66% | 0 | 0% | 10.76 | 9.91 | 92.1% | 0 | 0% | 10.76 | 9.84 | 91.45% | 0 | 0% | 10.76 | 9.83 | 91.36% | 0 | 0% | 10.76 | 9.85 | 91.54% | 0 | 0% | 10.76 | 9.97 | 92.66% | 0 | 0%
GNA_062041104_Capacity | North Valley and Sierra | Sacramento | DAVIS 1104 | 62041104 | Feeder | None | None | None | 98.01% | 0 | 0% | 11.55 | 11.3 | 97.84% | 0 | 0% | 11.55 | 11.25 | 97.4% | 0 | 0% | 11.55 | 11.22 | 97.14% | 0 | 0% | 11.55 | 11.26 | 97.49% | 0 | 0% | 11.55 | 11.32 | 98.01% | 0 | 0%
GNA_0620402_Capacity | North Valley and Sierra | Sacramento | DAVIS BANK 2 | 620402 | Bank | None | None | None | 87.96% | 0 | 0% | 44.6 | 37.16 | 83.32% | 0 | 0% | 44.6 | 38.89 | 87.2% | 0 | 0% | 44.6 | 38.28 | 85.83% | 0 | 0% | 44.6 | 38.68 | 86.73% | 0 | 0% | 44.6 | 39.23 | 87.96% | 0 | 0%
GNA_062041105_Capacity | North Valley and Sierra | Sacramento | DAVIS 1105 | 62041105 | Feeder | None | None | None | 99.75% | 0 | 0% | 12.19 | 12.16 | 99.75% | 0 | 0% | 12.19 | 12.13 | 99.51% | 0 | 0% | 12.19 | 12.1 | 99.26% | 0 | 0% | 12.19 | 12.11 | 99.34% | 0 | 0% | 12.19 | 12.16 | 99.75% | 0 | 0%
GNA_062041106_Capacity | North Valley and Sierra | Sacramento | DAVIS 1106 | 62041106 | Feeder | None | None | None | 96.96% | 0 | 0% | 12.19 | 10.26 | 84.17% | 0 | 0% | 12.19 | 11.82 | 96.96% | 0 | 0% | 12.19 | 11.04 | 90.57% | 0 | 0% | 12.19 | 11.09 | 90.98% | 0 | 0% | 12.19 | 11.21 | 91.96% | 0 | 0%
GNA_062041107_Capacity | North Valley and Sierra | Sacramento | DAVIS 1107 | 62041107 | Feeder | Demand Growth | Capacity | 2027 | 101.4% | 0.17 | 1.375% | 12.36 | 12.11 | 97.98% | 0 | 0% | 12.36 | 12.2 | 98.71% | 0 | 0% | 12.36 | 12.27 | 99.27% | 0 | 0% | 12.36 | 12.39 | 100.2% | 0.03 | 0.2427% | 12.36 | 12.53 | 101.4% | 0.17 | 1.375%
GNA_062041108_Capacity | North Valley and Sierra | Sacramento | DAVIS 1108 | 62041108 | Feeder | None | None | None | 81.72% | 0 | 0% | 12.36 | 9.55 | 77.27% | 0 | 0% | 12.36 | 9.61 | 77.75% | 0 | 0% | 12.36 | 9.72 | 78.64% | 0 | 0% | 12.36 | 9.91 | 80.18% | 0 | 0% | 12.36 | 10.1 | 81.72% | 0 | 0%
GNA_0620403_Capacity | North Valley and Sierra | Sacramento | DAVIS BANK 3 | 620403 | Bank | None | None | None | 97.44% | 0 | 0% | 44.6 | 37.7 | 84.53% | 0 | 0% | 44.6 | 41.37 | 92.76% | 0 | 0% | 44.6 | 41.81 | 93.74% | 0 | 0% | 44.6 | 42.88 | 96.14% | 0 | 0% | 44.6 | 43.46 | 97.44% | 0 | 0%
GNA_062041109_Capacity | North Valley and Sierra | Sacramento | DAVIS 1109 | 62041109 | Feeder | None | None | None | 97.29% | 0 | 0% | 12.19 | 11.32 | 92.86% | 0 | 0% | 12.19 | 11.44 | 93.85% | 0 | 0% | 12.19 | 11.55 | 94.75% | 0 | 0% | 12.19 | 11.66 | 95.65% | 0 | 0% | 12.19 | 11.86 | 97.29% | 0 | 0%
GNA_062041110_Capacity | North Valley and Sierra | Sacramento | DAVIS 1110 | 62041110 | Feeder | None | None | None | 79.66% | 0 | 0% | 12.19 | 9.3 | 76.29% | 0 | 0% | 12.19 | 9.4 | 77.11% | 0 | 0% | 12.19 | 9.5 | 77.93% | 0 | 0% | 12.19 | 9.61 | 78.84% | 0 | 0% | 12.19 | 9.71 | 79.66% | 0 | 0%
GNA_062041111_Capacity | North Valley and Sierra | Sacramento | DAVIS 1111 | 62041111 | Feeder | None | None | None | 56.69% | 0 | 0% | 10.76 | 5.7 | 52.97% | 0 | 0% | 10.76 | 5.77 | 53.62% | 0 | 0% | 10.76 | 5.84 | 54.28% | 0 | 0% | 10.76 | 5.96 | 55.39% | 0 | 0% | 10.76 | 6.1 | 56.69% | 0 | 0%
GNA_062041112_Capacity | North Valley and Sierra | Sacramento | DAVIS 1112 | 62041112 | Feeder | Demand Growth | Capacity | 2024 | 109.4% | 0.98 | 9.369% | 10.46 | 8.05 | 76.96% | 0 | 0% | 10.46 | 10.55 | 100.9% | 0.09 | 0.8604% | 10.46 | 10.66 | 101.9% | 0.2 | 1.912% | 10.46 | 11.33 | 108.3% | 0.87 | 8.317% | 10.46 | 11.44 | 109.4% | 0.98 | 9.369%
GNA_0624601_Capacity | North Valley and Sierra | Sacramento | GRAND ISLAND BANK 1 | 624601 | Bank | None | None | None | 28.07% | 0 | 0% | 17.81 | 5 | 28.07% | 0 | 0% | 17.81 | 4.97 | 27.91% | 0 | 0% | 17.81 | 4.94 | 27.74% | 0 | 0% | 17.81 | 4.91 | 27.57% | 0 | 0% | 17.81 | 4.9 | 27.51% | 0 | 0%
GNA_062462223_Capacity | North Valley and Sierra | Sacramento | GRAND ISLAND 2223 | 62462223 | Feeder | None | None | None | 41.48% | 0 | 0% | 12.44 | 5.16 | 41.48% | 0 | 0% | 12.44 | 5.13 | 41.24% | 0 | 0% | 12.44 | 5.1 | 41% | 0 | 0% | 12.44 | 5.07 | 40.76% | 0 | 0% | 12.44 | 5.06 | 40.68% | 0 | 0%
GNA_0624602_Capacity | North Valley and Sierra | Sacramento | GRAND ISLAND BANK 2 | 624602 | Bank | None | None | None | 70.19% | 0 | 0% | 17.81 | 12.5 | 70.19% | 0 | 0% | 17.81 | 12.44 | 69.85% | 0 | 0% | 17.81 | 12.37 | 69.46% | 0 | 0% | 17.81 | 12.33 | 69.23% | 0 | 0% | 17.81 | 12.32 | 69.17% | 0 | 0%
GNA_062462224_Capacity | North Valley and Sierra | Sacramento | GRAND ISLAND 2224 | 62462224 | Feeder | None | None | None | 68.87% | 0 | 0% | 4.85 | 3.34 | 68.87% | 0 | 0% | 4.85 | 3.33 | 68.66% | 0 | 0% | 4.85 | 3.31 | 68.25% | 0 | 0% | 4.85 | 3.3 | 68.04% | 0 | 0% | 4.85 | 3.28 | 67.63% | 0 | 0%
GNA_062462225_Capacity | North Valley and Sierra | Sacramento | GRAND ISLAND 2225 | 62462225 | Feeder | None | None | None | 71.64% | 0 | 0% | 13.33 | 9.55 | 71.64% | 0 | 0% | 13.33 | 9.5 | 71.27% | 0 | 0% | 13.33 | 9.45 | 70.89% | 0 | 0% | 13.33 | 9.42 | 70.67% | 0 | 0% | 13.33 | 9.43 | 70.74% | 0 | 0%
GNA_0624603_Capacity | North Valley and Sierra | Sacramento | GRAND ISLAND BANK 3 | 624603 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062462226_Capacity | North Valley and Sierra | Sacramento | GRAND ISLAND 2226 | 62462226 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062462227_Capacity | North Valley and Sierra | Sacramento | GRAND ISLAND 2227 | 62462227 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0620201_Capacity | North Valley and Sierra | Sacramento | COLUSA BANK 1 | 620201 | Bank | None | None | None | 28.55% | 0 | 0% | 28.9 | 8.01 | 27.72% | 0 | 0% | 28.9 | 7.99 | 27.65% | 0 | 0% | 28.9 | 8.01 | 27.72% | 0 | 0% | 28.9 | 8.1 | 28.03% | 0 | 0% | 28.9 | 8.25 | 28.55% | 0 | 0%
GNA_062021101_Capacity | North Valley and Sierra | Sacramento | COLUSA 1101 | 62021101 | Feeder | None | None | None | 51.66% | 0 | 0% | 8.13 | 3.96 | 48.71% | 0 | 0% | 8.13 | 3.95 | 48.59% | 0 | 0% | 8.13 | 3.97 | 48.83% | 0 | 0% | 8.13 | 4.06 | 49.94% | 0 | 0% | 8.13 | 4.2 | 51.66% | 0 | 0%
GNA_062021103_Capacity | North Valley and Sierra | Sacramento | COLUSA 1103 | 62021103 | Feeder | None | None | None | 43.83% | 0 | 0% | 8.92 | 3.91 | 43.83% | 0 | 0% | 8.92 | 3.91 | 43.83% | 0 | 0% | 8.92 | 3.91 | 43.83% | 0 | 0% | 8.92 | 3.91 | 43.83% | 0 | 0% | 8.92 | 3.91 | 43.83% | 0 | 0%
GNA_0620202_Capacity | North Valley and Sierra | Sacramento | COLUSA BANK 2 | 620202 | Bank | None | None | None | 31.76% | 0 | 0% | 29.69 | 7.88 | 26.54% | 0 | 0% | 29.69 | 9.42 | 31.73% | 0 | 0% | 29.69 | 9.42 | 31.73% | 0 | 0% | 29.69 | 9.42 | 31.73% | 0 | 0% | 29.69 | 9.43 | 31.76% | 0 | 0%
GNA_062021104_Capacity | North Valley and Sierra | Sacramento | COLUSA 1104 | 62021104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062021105_Capacity | North Valley and Sierra | Sacramento | COLUSA 1105 | 62021105 | Feeder | None | None | None | 16.37% | 0 | 0% | 10.69 | 1.75 | 16.37% | 0 | 0% | 10.69 | 1.75 | 16.37% | 0 | 0% | 10.69 | 1.75 | 16.37% | 0 | 0% | 10.69 | 1.75 | 16.37% | 0 | 0% | 10.69 | 1.75 | 16.37% | 0 | 0%
GNA_0620701_Capacity | North Valley and Sierra | Sacramento | COLUSA JUNCTION BANK 1 | 620701 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062071101_Capacity | North Valley and Sierra | Sacramento | COLUSA JUNCTION 1101 | 62071101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0628801_Capacity | North Valley and Sierra | Sacramento | MAXWELL BANK 1 | 628801 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062881102_Capacity | North Valley and Sierra | Sacramento | MAXWELL 1102 | 62881102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0628802_Capacity | North Valley and Sierra | Sacramento | MAXWELL BANK 2 | 628802 | Bank | None | None | None | 15.52% | 0 | 0% | 29.7 | 4.61 | 15.52% | 0 | 0% | 29.7 | 4.59 | 15.45% | 0 | 0% | 29.7 | 4.57 | 15.39% | 0 | 0% | 29.7 | 4.57 | 15.39% | 0 | 0% | 29.7 | 4.55 | 15.32% | 0 | 0%
GNA_062881105_Capacity | North Valley and Sierra | Sacramento | MAXWELL 1105 | 62881105 | Feeder | None | None | None | 45.2% | 0 | 0% | 8.23 | 3.72 | 45.2% | 0 | 0% | 8.23 | 3.71 | 45.08% | 0 | 0% | 8.23 | 3.7 | 44.96% | 0 | 0% | 8.23 | 3.69 | 44.84% | 0 | 0% | 8.23 | 3.68 | 44.71% | 0 | 0%
GNA_062881106_Capacity | North Valley and Sierra | Sacramento | MAXWELL 1106 | 62881106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0628301_Capacity | North Valley and Sierra | Sacramento | RICE BANK 1 | 628301 | Bank | None | None | None | 50.25% | 0 | 0% | 15.84 | 7.96 | 50.25% | 0 | 0% | 15.84 | 7.95 | 50.19% | 0 | 0% | 15.84 | 7.94 | 50.13% | 0 | 0% | 15.84 | 7.95 | 50.19% | 0 | 0% | 15.84 | 7.96 | 50.25% | 0 | 0%
GNA_062831101_Capacity | North Valley and Sierra | Sacramento | RICE 1101 | 62831101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062831102_Capacity | North Valley and Sierra | Sacramento | RICE 1102 | 62831102 | Feeder | None | None | None | 34.79% | 0 | 0% | 11.01 | 3.82 | 34.7% | 0 | 0% | 11.01 | 3.82 | 34.7% | 0 | 0% | 11.01 | 3.81 | 34.6% | 0 | 0% | 11.01 | 3.82 | 34.7% | 0 | 0% | 11.01 | 3.83 | 34.79% | 0 | 0%
GNA_0628302_Capacity | North Valley and Sierra | Sacramento | RICE BANK 2 | 628302 | Bank | None | None | None | 50.38% | 0 | 0% | 15.84 | 7.98 | 50.38% | 0 | 0% | 15.84 | 7.98 | 50.38% | 0 | 0% | 15.84 | 7.97 | 50.32% | 0 | 0% | 15.84 | 7.95 | 50.19% | 0 | 0% | 15.84 | 7.97 | 50.32% | 0 | 0%
GNA_062831103_Capacity | North Valley and Sierra | Sacramento | RICE 1103 | 62831103 | Feeder | None | None | None | 57.28% | 0 | 0% | 12.36 | 7.08 | 57.28% | 0 | 0% | 12.36 | 7.08 | 57.28% | 0 | 0% | 12.36 | 7.07 | 57.2% | 0 | 0% | 12.36 | 7.07 | 57.2% | 0 | 0% | 12.36 | 7.08 | 57.28% | 0 | 0%
GNA_062831104_Capacity | North Valley and Sierra | Sacramento | RICE 1104 | 62831104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0636401_Capacity | North Valley and Sierra | Sacramento | PEABODY BANK 1 | 636401 | Bank | None | None | None | 95.62% | 0 | 0% | 59.4 | 53.56 | 90.17% | 0 | 0% | 59.4 | 55.47 | 93.38% | 0 | 0% | 59.4 | 55.77 | 93.89% | 0 | 0% | 59.4 | 56.25 | 94.7% | 0 | 0% | 59.4 | 56.8 | 95.62% | 0 | 0%
GNA_063642102_Capacity | North Valley and Sierra | Sacramento | PEABODY 2102 | 63642102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063642104_Capacity | North Valley and Sierra | Sacramento | PEABODY 2104 | 63642104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063642105_Capacity | North Valley and Sierra | Sacramento | PEABODY 2105 | 63642105 | Feeder | Demand Growth | Capacity | 2023 | 128.4% | 6.84 | 28.42% | 24.07 | 28.65 | 119% | 4.58 | 19.03% | 24.07 | 30.33 | 126% | 6.26 | 26.01% | 24.07 | 30.44 | 126.5% | 6.37 | 26.46% | 24.07 | 30.65 | 127.3% | 6.58 | 27.34% | 24.07 | 30.91 | 128.4% | 6.84 | 28.42%
GNA_0636402_Capacity | North Valley and Sierra | Sacramento | PEABODY BANK 2 | 636402 | Bank | None | None | None | 94.88% | 0 | 0% | 59.4 | 54.49 | 91.73% | 0 | 0% | 59.4 | 54.78 | 92.22% | 0 | 0% | 59.4 | 55.12 | 92.79% | 0 | 0% | 59.4 | 55.67 | 93.72% | 0 | 0% | 59.4 | 56.36 | 94.88% | 0 | 0%
GNA_063642106_Capacity | North Valley and Sierra | Sacramento | PEABODY 2106 | 63642106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063642107_Capacity | North Valley and Sierra | Sacramento | PEABODY 2107 | 63642107 | Feeder | None | None | None | 80.89% | 0 | 0% | 24.07 | 18.9 | 78.52% | 0 | 0% | 24.07 | 18.98 | 78.85% | 0 | 0% | 24.07 | 19.07 | 79.23% | 0 | 0% | 24.07 | 19.27 | 80.06% | 0 | 0% | 24.07 | 19.47 | 80.89% | 0 | 0%
GNA_063642108_Capacity | North Valley and Sierra | Sacramento | PEABODY 2108 | 63642108 | Feeder | None | None | None | 91.19% | 0 | 0% | 21.11 | 18.56 | 87.92% | 0 | 0% | 21.11 | 18.67 | 88.44% | 0 | 0% | 21.11 | 18.81 | 89.1% | 0 | 0% | 21.11 | 18.98 | 89.91% | 0 | 0% | 21.11 | 19.25 | 91.19% | 0 | 0%
GNA_0636403_Capacity | North Valley and Sierra | Sacramento | PEABODY BANK 3 | 636403 | Bank | None | None | None | 91.1% | 0 | 0% | 44.6 | 39.07 | 87.6% | 0 | 0% | 44.6 | 39.62 | 88.83% | 0 | 0% | 44.6 | 39.82 | 89.28% | 0 | 0% | 44.6 | 40.2 | 90.13% | 0 | 0% | 44.6 | 40.63 | 91.1% | 0 | 0%
GNA_063642112_Capacity | North Valley and Sierra | Sacramento | PEABODY 2112 | 63642112 | Feeder | None | None | None | 94.04% | 0 | 0% | 26.19 | 23.53 | 89.84% | 0 | 0% | 26.19 | 24.01 | 91.68% | 0 | 0% | 26.19 | 24.13 | 92.13% | 0 | 0% | 26.19 | 24.35 | 92.97% | 0 | 0% | 26.19 | 24.63 | 94.04% | 0 | 0%
GNA_063642113_Capacity | North Valley and Sierra | Sacramento | PEABODY 2113 | 63642113 | Feeder | None | None | None | 98.91% | 0 | 0% | 21.11 | 20.44 | 96.83% | 0 | 0% | 21.11 | 20.51 | 97.16% | 0 | 0% | 21.11 | 20.58 | 97.49% | 0 | 0% | 21.11 | 20.72 | 98.15% | 0 | 0% | 21.11 | 20.88 | 98.91% | 0 | 0%
GNA_0620801_Capacity | North Valley and Sierra | Sacramento | ARBUCKLE BANK 1 | 620801 | Bank | Demand Growth | Capacity | 2023 | 118.1% | 2.23 | 18.1% | 12.32 | 14.55 | 118.1% | 2.23 | 18.1% | 12.32 | 14.54 | 118% | 2.22 | 18.02% | 12.32 | 14.5 | 117.7% | 2.18 | 17.69% | 12.32 | 14.49 | 117.6% | 2.17 | 17.61% | 12.32 | 14.49 | 117.6% | 2.17 | 17.61%
GNA_062081101_Capacity | North Valley and Sierra | Sacramento | ARBUCKLE 1101 | 62081101 | Feeder | None | None | None | 79.01% | 0 | 0% | 11.67 | 9.22 | 79.01% | 0 | 0% | 11.67 | 9.21 | 78.92% | 0 | 0% | 11.67 | 9.19 | 78.75% | 0 | 0% | 11.67 | 9.19 | 78.75% | 0 | 0% | 11.67 | 9.19 | 78.75% | 0 | 0%
GNA_062081102_Capacity | North Valley and Sierra | Sacramento | ARBUCKLE 1102 | 62081102 | Feeder | None | None | None | 60.76% | 0 | 0% | 8.13 | 4.94 | 60.76% | 0 | 0% | 8.13 | 4.94 | 60.76% | 0 | 0% | 8.13 | 4.92 | 60.52% | 0 | 0% | 8.13 | 4.91 | 60.39% | 0 | 0% | 8.13 | 4.91 | 60.39% | 0 | 0%
GNA_0620802_Capacity | North Valley and Sierra | Sacramento | ARBUCKLE BANK 2 | 620802 | Bank | None | None | None | 74.03% | 0 | 0% | 12.36 | 9.15 | 74.03% | 0 | 0% | 12.36 | 9.14 | 73.95% | 0 | 0% | 12.36 | 9.12 | 73.79% | 0 | 0% | 12.36 | 9.14 | 73.95% | 0 | 0% | 12.36 | 9.15 | 74.03% | 0 | 0%
GNA_062081104_Capacity | North Valley and Sierra | Sacramento | ARBUCKLE 1104 | 62081104 | Feeder | None | None | None | 67.79% | 0 | 0% | 13.6 | 9.22 | 67.79% | 0 | 0% | 13.6 | 9.22 | 67.79% | 0 | 0% | 13.6 | 9.2 | 67.65% | 0 | 0% | 13.6 | 9.22 | 67.79% | 0 | 0% | 13.6 | 9.22 | 67.79% | 0 | 0%
GNA_0631203_Capacity | North Valley and Sierra | Sacramento | CORTINA BANK 3 | 631203 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063121101_Capacity | North Valley and Sierra | Sacramento | CORTINA 1101 | 63121101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0638101_Capacity | North Valley and Sierra | Sacramento | DUNNIGAN BANK 1 | 638101 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063811101_Capacity | North Valley and Sierra | Sacramento | DUNNIGAN 1101 | 63811101 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063811102_Capacity | North Valley and Sierra | Sacramento | DUNNIGAN 1102 (Mobile TX Outlet) | 63811102 | Feeder | None | None | None | 57.42% | 0 | 0% | 12.19 | 7 | 57.42% | 0 | 0% | 12.19 | 7 | 57.42% | 0 | 0% | 12.19 | 7 | 57.42% | 0 | 0% | 12.19 | 7 | 57.42% | 0 | 0% | 12.19 | 7 | 57.42% | 0 | 0%
GNA_0620501_Capacity | North Valley and Sierra | Sacramento | WILLIAMS BANK 1 | 620501 | Bank | None | None | None | 92.55% | 0 | 0% | 15.84 | 13.38 | 84.47% | 0 | 0% | 15.84 | 14.28 | 90.15% | 0 | 0% | 15.84 | 14.4 | 90.91% | 0 | 0% | 15.84 | 14.52 | 91.67% | 0 | 0% | 15.84 | 14.66 | 92.55% | 0 | 0%
GNA_062051102_Capacity | North Valley and Sierra | Sacramento | WILLIAMS 1102 | 62051102 | Feeder | None | None | None | 98.06% | 0 | 0% | 14.97 | 13.4 | 89.51% | 0 | 0% | 14.97 | 14.3 | 95.52% | 0 | 0% | 14.97 | 14.42 | 96.33% | 0 | 0% | 14.97 | 14.54 | 97.13% | 0 | 0% | 14.97 | 14.68 | 98.06% | 0 | 0%
GNA_0620502_Capacity | North Valley and Sierra | Sacramento | WILLIAMS BANK 2 | 620502 | Bank | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062051101_Capacity | North Valley and Sierra | Sacramento | WILLIAMS 1101 | 62051101 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0627003_Capacity | North Valley and Sierra | Sacramento | CORDELIA BANK 3 | 627003 | Bank | None | None | None | 67.08% | 0 | 0% | 43.1 | 28.91 | 67.08% | 0 | 0% | 43.1 | 28.43 | 65.96% | 0 | 0% | 43.1 | 28.23 | 65.5% | 0 | 0% | 43.1 | 28.24 | 65.52% | 0 | 0% | 43.1 | 28.26 | 65.57% | 0 | 0%
GNA_062701104_Capacity | North Valley and Sierra | Sacramento | CORDELIA 1104 | 62701104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062701110_Capacity | North Valley and Sierra | Sacramento | CORDELIA 1110 (old 1103) | 62701110 | Feeder | None | None | None | 80.79% | 0 | 0% | 14.26 | 11.52 | 80.79% | 0 | 0% | 14.26 | 11.42 | 80.08% | 0 | 0% | 14.26 | 11.35 | 79.59% | 0 | 0% | 14.26 | 11.43 | 80.15% | 0 | 0% | 14.26 | 11.52 | 80.79% | 0 | 0%
GNA_062701112_Capacity | North Valley and Sierra | Sacramento | CORDELIA 1112 (old 1101) | 62701112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0638001_Capacity | North Valley and Sierra | Sacramento | JAMESON BANK 1 | 638001 | Bank | None | None | None | 79.24% | 0 | 0% | 44.6 | 33.07 | 74.15% | 0 | 0% | 44.6 | 33.56 | 75.25% | 0 | 0% | 44.6 | 33.97 | 76.17% | 0 | 0% | 44.6 | 34.61 | 77.6% | 0 | 0% | 44.6 | 35.34 | 79.24% | 0 | 0%
GNA_063801101_Capacity | North Valley and Sierra | Sacramento | JAMESON 1101 | 63801101 | Feeder | None | None | None | 81.58% | 0 | 0% | 10.86 | 8.33 | 76.7% | 0 | 0% | 10.86 | 8.43 | 77.62% | 0 | 0% | 10.86 | 8.56 | 78.82% | 0 | 0% | 10.86 | 8.71 | 80.2% | 0 | 0% | 10.86 | 8.86 | 81.58% | 0 | 0%
GNA_063801102_Capacity | North Valley and Sierra | Sacramento | JAMESON 1102 | 63801102 | Feeder | None | None | None | 88.76% | 0 | 0% | 12.19 | 10.1 | 82.85% | 0 | 0% | 12.19 | 10.24 | 84% | 0 | 0% | 12.19 | 10.36 | 84.99% | 0 | 0% | 12.19 | 10.57 | 86.71% | 0 | 0% | 12.19 | 10.82 | 88.76% | 0 | 0%
GNA_063801103_Capacity | North Valley and Sierra | Sacramento | JAMESON 1103 | 63801103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063801104_Capacity | North Valley and Sierra | Sacramento | JAMESON 1104 | 63801104 | Feeder | None | None | None | 73.58% | 0 | 0% | 12.49 | 8.31 | 66.53% | 0 | 0% | 12.49 | 8.56 | 68.53% | 0 | 0% | 12.49 | 8.72 | 69.82% | 0 | 0% | 12.49 | 8.93 | 71.5% | 0 | 0% | 12.49 | 9.19 | 73.58% | 0 | 0%
GNA_0638002_Capacity | North Valley and Sierra | Sacramento | JAMESON BANK 2 | 638002 | Bank | None | None | None | 28.92% | 0 | 0% | 44.5 | 12.79 | 28.74% | 0 | 0% | 44.5 | 12.7 | 28.54% | 0 | 0% | 44.5 | 12.71 | 28.56% | 0 | 0% | 44.5 | 12.79 | 28.74% | 0 | 0% | 44.5 | 12.87 | 28.92% | 0 | 0%
GNA_063801105_Capacity | North Valley and Sierra | Sacramento | JAMESON 1105 | 63801105 | Feeder | None | None | None | 90.55% | 0 | 0% | 12.49 | 11.19 | 89.59% | 0 | 0% | 12.49 | 11.14 | 89.19% | 0 | 0% | 12.49 | 11.15 | 89.27% | 0 | 0% | 12.49 | 11.23 | 89.91% | 0 | 0% | 12.49 | 11.31 | 90.55% | 0 | 0%
GNA_0621301_Capacity | North Valley and Sierra | Sacramento | SUISUN BANK 1 | 621301 | Bank | None | None | None | 87.51% | 0 | 0% | 44.6 | 38.9 | 87.22% | 0 | 0% | 44.6 | 38.82 | 87.04% | 0 | 0% | 44.6 | 38.74 | 86.86% | 0 | 0% | 44.6 | 38.8 | 87% | 0 | 0% | 44.6 | 39.03 | 87.51% | 0 | 0%
GNA_062131101_Capacity | North Valley and Sierra | Sacramento | SUISUN 1101 | 62131101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062131102_Capacity | North Valley and Sierra | Sacramento | SUISUN 1102 | 62131102 | Feeder | None | None | None | 86.22% | 0 | 0% | 12.19 | 10.51 | 86.22% | 0 | 0% | 12.19 | 10.47 | 85.89% | 0 | 0% | 12.19 | 10.43 | 85.56% | 0 | 0% | 12.19 | 10.4 | 85.32% | 0 | 0% | 12.19 | 10.37 | 85.07% | 0 | 0%
GNA_062131103_Capacity | North Valley and Sierra | Sacramento | SUISUN 1103 | 62131103 | Feeder | None | None | None | 97.86% | 0 | 0% | 10.76 | 10.28 | 95.54% | 0 | 0% | 10.76 | 10.26 | 95.35% | 0 | 0% | 10.76 | 10.24 | 95.17% | 0 | 0% | 10.76 | 10.4 | 96.65% | 0 | 0% | 10.76 | 10.53 | 97.86% | 0 | 0%
GNA_062131104_Capacity | North Valley and Sierra | Sacramento | SUISUN 1104 | 62131104 | Feeder | Demand Growth | Capacity | 2023 | 101.1% | 0.13 | 1.066% | 12.19 | 12.32 | 101.1% | 0.13 | 1.066% | 12.19 | 12.2 | 100.1% | 0.01 | 0.08203% | 12.19 | 12.1 | 99.26% | 0 | 0% | 12.19 | 12.06 | 98.93% | 0 | 0% | 12.19 | 12.08 | 99.1% | 0 | 0%
GNA_0621302_Capacity | North Valley and Sierra | Sacramento | SUISUN BANK 2 | 621302 | Bank | None | None | None | 76.37% | 0 | 0% | 44.6 | 34.06 | 76.37% | 0 | 0% | 44.6 | 33.93 | 76.08% | 0 | 0% | 44.6 | 33.7 | 75.56% | 0 | 0% | 44.6 | 33.79 | 75.76% | 0 | 0% | 44.6 | 34 | 76.23% | 0 | 0%
GNA_062131105_Capacity | North Valley and Sierra | Sacramento | SUISUN 1105 | 62131105 | Feeder | None | None | None | 72.77% | 0 | 0% | 10.76 | 7.49 | 69.61% | 0 | 0% | 10.76 | 7.57 | 70.35% | 0 | 0% | 10.76 | 7.6 | 70.63% | 0 | 0% | 10.76 | 7.71 | 71.65% | 0 | 0% | 10.76 | 7.83 | 72.77% | 0 | 0%
GNA_062131106_Capacity | North Valley and Sierra | Sacramento | SUISUN 1106 | 62131106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062131107_Capacity | North Valley and Sierra | Sacramento | SUISUN 1107 | 62131107 | Feeder | None | None | None | 96.93% | 0 | 0% | 10.76 | 10.43 | 96.93% | 0 | 0% | 10.76 | 10.37 | 96.38% | 0 | 0% | 10.76 | 10.28 | 95.54% | 0 | 0% | 10.76 | 10.18 | 94.61% | 0 | 0% | 10.76 | 10.2 | 94.8% | 0 | 0%
GNA_062131108_Capacity | North Valley and Sierra | Sacramento | SUISUN 1108 | 62131108 | Feeder | None | None | None | 86.17% | 0 | 0% | 12.36 | 10.63 | 86% | 0 | 0% | 12.36 | 10.53 | 85.19% | 0 | 0% | 12.36 | 10.53 | 85.19% | 0 | 0% | 12.36 | 10.56 | 85.44% | 0 | 0% | 12.36 | 10.65 | 86.17% | 0 | 0%
GNA_0621303_Capacity | North Valley and Sierra | Sacramento | SUISUN BANK 3 | 621303 | Bank | None | None | None | 95.49% | 0 | 0% | 29.7 | 27.92 | 94.01% | 0 | 0% | 29.7 | 27.96 | 94.14% | 0 | 0% | 29.7 | 28.02 | 94.34% | 0 | 0% | 29.7 | 28.1 | 94.61% | 0 | 0% | 29.7 | 28.36 | 95.49% | 0 | 0%
GNA_062131109_Capacity | North Valley and Sierra | Sacramento | SUISUN 1109 | 62131109 | Feeder | Demand Growth | Capacity | 2023 | 107.4% | 0.8 | 7.435% | 10.76 | 11.56 | 107.4% | 0.8 | 7.435% | 10.76 | 11.41 | 106% | 0.65 | 6.041% | 10.76 | 11.39 | 105.9% | 0.63 | 5.855% | 10.76 | 11.43 | 106.2% | 0.67 | 6.227% | 10.76 | 11.51 | 107% | 0.75 | 6.97%
GNA_062131110_Capacity | North Valley and Sierra | Sacramento | SUISUN 1110 | 62131110 | Feeder | None | None | None | 34.39% | 0 | 0% | 10.76 | 3.3 | 30.67% | 0 | 0% | 10.76 | 3.41 | 31.69% | 0 | 0% | 10.76 | 3.52 | 32.71% | 0 | 0% | 10.76 | 3.61 | 33.55% | 0 | 0% | 10.76 | 3.7 | 34.39% | 0 | 0%
GNA_062131111_Capacity | North Valley and Sierra | Sacramento | SUISUN 1111 | 62131111 | Feeder | None | None | None | 70.88% | 0 | 0% | 12.19 | 8.28 | 67.92% | 0 | 0% | 12.19 | 8.36 | 68.58% | 0 | 0% | 12.19 | 8.46 | 69.4% | 0 | 0% | 12.19 | 8.54 | 70.06% | 0 | 0% | 12.19 | 8.64 | 70.88% | 0 | 0%
GNA_062131112_Capacity | North Valley and Sierra | Sacramento | SUISUN 1112 | 62131112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0620601_Capacity | North Valley and Sierra | Sacramento | DIXON BANK 1 | 620601 | Bank | None | None | None | 50.35% | 0 | 0% | 44.53 | 21.76 | 48.87% | 0 | 0% | 44.53 | 21.92 | 49.23% | 0 | 0% | 44.53 | 22.08 | 49.58% | 0 | 0% | 44.53 | 22.24 | 49.94% | 0 | 0% | 44.53 | 22.42 | 50.35% | 0 | 0%
GNA_062061104_Capacity | North Valley and Sierra | Sacramento | DIXON 1104 | 62061104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062061103_Capacity | North Valley and Sierra | Sacramento | DIXON 1103 | 62061103 | Feeder | None | None | None | 83.99% | 0 | 0% | 12.49 | 10.49 | 83.99% | 0 | 0% | 12.49 | 10.48 | 83.91% | 0 | 0% | 12.49 | 10.47 | 83.83% | 0 | 0% | 12.49 | 10.44 | 83.59% | 0 | 0% | 12.49 | 10.42 | 83.43% | 0 | 0%
GNA_062061102_Capacity | North Valley and Sierra | Sacramento | DIXON 1102 | 62061102 | Feeder | Demand Growth | Capacity | 2023 | 115.9% | 1.4 | 15.89% | 8.81 | 9.8 | 111.2% | 0.99 | 11.24% | 8.81 | 9.9 | 112.4% | 1.09 | 12.37% | 8.81 | 9.99 | 113.4% | 1.18 | 13.39% | 8.81 | 10.09 | 114.5% | 1.28 | 14.53% | 8.81 | 10.21 | 115.9% | 1.4 | 15.89%
GNA_0620602_Capacity | North Valley and Sierra | Sacramento | DIXON BANK 2 | 620602 | Bank | None | None | None | 83.87% | 0 | 0% | 29.7 | 24.28 | 81.75% | 0 | 0% | 29.7 | 24.43 | 82.26% | 0 | 0% | 29.7 | 24.55 | 82.66% | 0 | 0% | 29.7 | 24.72 | 83.23% | 0 | 0% | 29.7 | 24.91 | 83.87% | 0 | 0%
GNA_062061105_Capacity | North Valley and Sierra | Sacramento | DIXON 1105 | 62061105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062061106_Capacity | North Valley and Sierra | Sacramento | DIXON 1106 | 62061106 | Feeder | None | None | None | 98.11% | 0 | 0% | 13.73 | 13.1 | 95.41% | 0 | 0% | 13.73 | 13.17 | 95.92% | 0 | 0% | 13.73 | 13.26 | 96.58% | 0 | 0% | 13.73 | 13.37 | 97.38% | 0 | 0% | 13.73 | 13.47 | 98.11% | 0 | 0%
GNA_0635906_Capacity | North Valley and Sierra | Sacramento | VACA DIXON BANK 6 | 635906 | Bank | None | None | None | 55.44% | 0 | 0% | 44.5 | 21.28 | 47.82% | 0 | 0% | 44.5 | 22.15 | 49.78% | 0 | 0% | 44.5 | 24.33 | 54.67% | 0 | 0% | 44.5 | 24.49 | 55.03% | 0 | 0% | 44.5 | 24.67 | 55.44% | 0 | 0%
GNA_063591101_Capacity | North Valley and Sierra | Sacramento | VACA DIXON 1101 | 63591101 | Feeder | None | None | None | 86.57% | 0 | 0% | 15.12 | 13.07 | 86.44% | 0 | 0% | 15.12 | 13.01 | 86.04% | 0 | 0% | 15.12 | 13 | 85.98% | 0 | 0% | 15.12 | 13.03 | 86.18% | 0 | 0% | 15.12 | 13.09 | 86.57% | 0 | 0%
GNA_063591109_Capacity | North Valley and Sierra | Sacramento | VACA DIXON 1109 | 63591109 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0635907_Capacity | North Valley and Sierra | Sacramento | VACA DIXON BANK 7 | 635907 | Bank | None | None | None | 96.73% | 0 | 0% | 29.7 | 27.19 | 91.55% | 0 | 0% | 29.7 | 27.72 | 93.33% | 0 | 0% | 29.7 | 27.79 | 93.57% | 0 | 0% | 29.7 | 28.4 | 95.62% | 0 | 0% | 29.7 | 28.73 | 96.73% | 0 | 0%
GNA_063591102_Capacity | North Valley and Sierra | Sacramento | VACA DIXON 1102 | 63591102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063591103_Capacity | North Valley and Sierra | Sacramento | VACA DIXON 1103 | 63591103 | Feeder | None | None | None | 71.45% | 0 | 0% | 12.19 | 7.87 | 64.56% | 0 | 0% | 12.19 | 8.06 | 66.12% | 0 | 0% | 12.19 | 8.25 | 67.68% | 0 | 0% | 12.19 | 8.71 | 71.45% | 0 | 0% | 12.19 | 8.63 | 70.8% | 0 | 0%
GNA_063591104_Capacity | North Valley and Sierra | Sacramento | VACA DIXON 1104 | 63591104 | Feeder | None | None | None | 77.45% | 0 | 0% | 15.12 | 11.68 | 77.25% | 0 | 0% | 15.12 | 11.65 | 77.05% | 0 | 0% | 15.12 | 11.54 | 76.32% | 0 | 0% | 15.12 | 11.56 | 76.46% | 0 | 0% | 15.12 | 11.71 | 77.45% | 0 | 0%
GNA_0635908_Capacity | North Valley and Sierra | Sacramento | VACA DIXON BANK 8 | 635908 | Bank | Demand Growth | Capacity | 2027 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063591105_Capacity | North Valley and Sierra | Sacramento | VACA DIXON 1105 | 63591105 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063591106_Capacity | North Valley and Sierra | Sacramento | VACA DIXON 1106 | 63591106 | Feeder | None | None | None | 82.05% | 0 | 0% | 14.26 | 11.08 | 77.7% | 0 | 0% | 14.26 | 11.19 | 78.47% | 0 | 0% | 14.26 | 11.32 | 79.38% | 0 | 0% | 14.26 | 11.48 | 80.5% | 0 | 0% | 14.26 | 11.7 | 82.05% | 0 | 0%
GNA_063591107_Capacity | North Valley and Sierra | Sacramento | VACA DIXON 1107 | 63591107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0636001_Capacity | North Valley and Sierra | Sacramento | VACAVILLE BANK 1 | 636001 | Bank | None | None | None | 92.76% | 0 | 0% | 29.7 | 26.52 | 89.29% | 0 | 0% | 29.7 | 27.1 | 91.25% | 0 | 0% | 29.7 | 27.2 | 91.58% | 0 | 0% | 29.7 | 27.36 | 92.12% | 0 | 0% | 29.7 | 27.55 | 92.76% | 0 | 0%
GNA_063601102_Capacity | North Valley and Sierra | Sacramento | VACAVILLE 1102 | 63601102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063601103_Capacity | North Valley and Sierra | Sacramento | VACAVILLE 1103 | 63601103 | Feeder | None | None | None | 93.36% | 0 | 0% | 12.19 | 11.38 | 93.36% | 0 | 0% | 12.19 | 11.19 | 91.8% | 0 | 0% | 12.19 | 11.18 | 91.71% | 0 | 0% | 12.19 | 11.21 | 91.96% | 0 | 0% | 12.19 | 11.24 | 92.21% | 0 | 0%
GNA_063601104_Capacity | North Valley and Sierra | Sacramento | VACAVILLE 1104 | 63601104 | Feeder | None | None | None | 96.64% | 0 | 0% | 12.49 | 10.8 | 86.47% | 0 | 0% | 12.49 | 11.68 | 93.51% | 0 | 0% | 12.49 | 11.79 | 94.4% | 0 | 0% | 12.49 | 11.93 | 95.52% | 0 | 0% | 12.49 | 12.07 | 96.64% | 0 | 0%
GNA_0636002_Capacity | North Valley and Sierra | Sacramento | VACAVILLE BANK 2 | 636002 | Bank | None | None | None | 93.3% | 0 | 0% | 44.6 | 41.51 | 93.07% | 0 | 0% | 44.6 | 41.61 | 93.3% | 0 | 0% | 44.6 | 41.32 | 92.65% | 0 | 0% | 44.6 | 41.45 | 92.94% | 0 | 0% | 44.6 | 41.56 | 93.18% | 0 | 0%
GNA_063601105_Capacity | North Valley and Sierra | Sacramento | VACAVILLE 1105 | 63601105 | Feeder | None | None | None | 92.06% | 0 | 0% | 11.08 | 9.5 | 85.74% | 0 | 0% | 11.08 | 10.2 | 92.06% | 0 | 0% | 11.08 | 10.07 | 90.88% | 0 | 0% | 11.08 | 10 | 90.25% | 0 | 0% | 11.08 | 10.01 | 90.34% | 0 | 0%
GNA_063601106_Capacity | North Valley and Sierra | Sacramento | VACAVILLE 1106 | 63601106 | Feeder | None | None | None | 92.42% | 0 | 0% | 11.08 | 10.24 | 92.42% | 0 | 0% | 11.08 | 10.07 | 90.88% | 0 | 0% | 11.08 | 10.07 | 90.88% | 0 | 0% | 11.08 | 10.12 | 91.34% | 0 | 0% | 11.08 | 10.17 | 91.79% | 0 | 0%
GNA_063601107_Capacity | North Valley and Sierra | Sacramento | VACAVILLE 1107 | 63601107 | Feeder | None | None | None | 100.4% | 0.04 | 0.3676% | 10.88 | 10.92 | 100.4% | 0.04 | 0.3676% | 10.88 | 10.83 | 99.54% | 0 | 0% | 10.88 | 10.8 | 99.26% | 0 | 0% | 10.88 | 10.86 | 99.82% | 0 | 0% | 10.88 | 10.9 | 100.2% | 0.02 | 0.1838%
GNA_063601108_Capacity | North Valley and Sierra | Sacramento | VACAVILLE 1108 | 63601108 | Feeder | None | None | None | 85.64% | 0 | 0% | 12.19 | 10.44 | 85.64% | 0 | 0% | 12.19 | 10.25 | 84.09% | 0 | 0% | 12.19 | 10.05 | 82.44% | 0 | 0% | 12.19 | 10.06 | 82.53% | 0 | 0% | 12.19 | 10.08 | 82.69% | 0 | 0%
GNA_0636003_Capacity | North Valley and Sierra | Sacramento | VACAVILLE BANK 3 | 636003 | Bank | None | None | None | 91.64% | 0 | 0% | 44.6 | 39.92 | 89.51% | 0 | 0% | 44.6 | 40.25 | 90.25% | 0 | 0% | 44.6 | 40.32 | 90.4% | 0 | 0% | 44.6 | 40.53 | 90.87% | 0 | 0% | 44.6 | 40.87 | 91.64% | 0 | 0%
GNA_063601109_Capacity | North Valley and Sierra | Sacramento | VACAVILLE 1109 | 63601109 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063601110_Capacity | North Valley and Sierra | Sacramento | VACAVILLE 1110 | 63601110 | Feeder | None | None | None | 80.5% | 0 | 0% | 12.1 | 9.48 | 78.35% | 0 | 0% | 12.1 | 9.67 | 79.92% | 0 | 0% | 12.1 | 9.66 | 79.83% | 0 | 0% | 12.1 | 9.69 | 80.08% | 0 | 0% | 12.1 | 9.74 | 80.5% | 0 | 0%
GNA_063601111_Capacity | North Valley and Sierra | Sacramento | VACAVILLE 1111 | 63601111 | Feeder | None | None | None | 93.38% | 0 | 0% | 10.88 | 9.62 | 88.42% | 0 | 0% | 10.88 | 9.72 | 89.34% | 0 | 0% | 10.88 | 9.82 | 90.26% | 0 | 0% | 10.88 | 9.97 | 91.64% | 0 | 0% | 10.88 | 10.16 | 93.38% | 0 | 0%
GNA_063601112_Capacity | North Valley and Sierra | Sacramento | VACAVILLE 1112 | 63601112 | Feeder | None | None | None | 93.52% | 0 | 0% | 12.19 | 11.29 | 92.62% | 0 | 0% | 12.19 | 11.29 | 92.62% | 0 | 0% | 12.19 | 11.29 | 92.62% | 0 | 0% | 12.19 | 11.33 | 92.95% | 0 | 0% | 12.19 | 11.4 | 93.52% | 0 | 0%
GNA_0636202_Capacity | North Valley and Sierra | Sacramento | DEEPWATER BANK 2 | 636202 | Bank | None | None | None | 85.92% | 0 | 0% | 44.6 | 37.65 | 84.42% | 0 | 0% | 44.6 | 37.68 | 84.48% | 0 | 0% | 44.6 | 37.74 | 84.62% | 0 | 0% | 44.6 | 37.94 | 85.07% | 0 | 0% | 44.6 | 38.32 | 85.92% | 0 | 0%
GNA_063621105_Capacity | North Valley and Sierra | Sacramento | DEEPWATER 1105 | 63621105 | Feeder | None | None | None | 74.78% | 0 | 0% | 12.49 | 9.33 | 74.7% | 0 | 0% | 12.49 | 9.32 | 74.62% | 0 | 0% | 12.49 | 9.31 | 74.54% | 0 | 0% | 12.49 | 9.31 | 74.54% | 0 | 0% | 12.49 | 9.34 | 74.78% | 0 | 0%
GNA_063621106_Capacity | North Valley and Sierra | Sacramento | DEEPWATER 1106 | 63621106 | Feeder | Demand Growth | Capacity | 2023 | 109.4% | 1.18 | 9.448% | 12.49 | 12.93 | 103.5% | 0.44 | 3.523% | 12.49 | 13.17 | 105.4% | 0.68 | 5.444% | 12.49 | 13.4 | 107.3% | 0.91 | 7.286% | 12.49 | 13.53 | 108.3% | 1.04 | 8.327% | 12.49 | 13.67 | 109.4% | 1.18 | 9.448%
GNA_063621107_Capacity | North Valley and Sierra | Sacramento | DEEPWATER 1107 | 63621107 | Feeder | Demand Growth | Capacity | 2023 | 116.5% | 2.24 | 16.47% | 13.6 | 15.71 | 115.5% | 2.11 | 15.51% | 13.6 | 15.64 | 115% | 2.04 | 15% | 13.6 | 15.61 | 114.8% | 2.01 | 14.78% | 13.6 | 15.7 | 115.4% | 2.1 | 15.44% | 13.6 | 15.84 | 116.5% | 2.24 | 16.47%
GNA_0636203_Capacity | North Valley and Sierra | Sacramento | DEEPWATER BANK 3 | 636203 | Bank | None | None | None | 53.74% | 0 | 0% | 44.6 | 23.48 | 52.65% | 0 | 0% | 44.6 | 23.5 | 52.69% | 0 | 0% | 44.6 | 23.52 | 52.74% | 0 | 0% | 44.6 | 23.7 | 53.14% | 0 | 0% | 44.6 | 23.97 | 53.74% | 0 | 0%
GNA_063621108_Capacity | North Valley and Sierra | Sacramento | DEEPWATER 1108 | 63621108 | Feeder | Demand Growth | Capacity | 2023 | 111.7% | 1.32 | 11.65% | 11.33 | 12.64 | 111.6% | 1.31 | 11.56% | 11.33 | 12.59 | 111.1% | 1.26 | 11.12% | 11.33 | 12.56 | 110.9% | 1.23 | 10.86% | 11.33 | 12.61 | 111.3% | 1.28 | 11.3% | 11.33 | 12.65 | 111.7% | 1.32 | 11.65%
GNA_063621109_Capacity | North Valley and Sierra | Sacramento | DEEPWATER 1109 | 63621109 | Feeder | Demand Growth | Capacity | 2023 | 108.8% | 1 | 8.826% | 11.33 | 11.99 | 105.8% | 0.66 | 5.825% | 11.33 | 12.02 | 106.1% | 0.69 | 6.09% | 11.33 | 12.03 | 106.2% | 0.7 | 6.178% | 11.33 | 12.13 | 107.1% | 0.8 | 7.061% | 11.33 | 12.33 | 108.8% | 1 | 8.826%
GNA_0631301_Capacity | North Valley and Sierra | Sacramento | WEST SACRAMENTO BANK 1 | 631301 | Bank | Demand Growth | Capacity | 2023 | 106.6% | 1.95 | 6.566% | 29.7 | 31.65 | 106.6% | 1.95 | 6.566% | 29.7 | 31.6 | 106.4% | 1.9 | 6.397% | 29.7 | 31.56 | 106.3% | 1.86 | 6.263% | 29.7 | 31.58 | 106.3% | 1.88 | 6.33% | 29.7 | 31.6 | 106.4% | 1.9 | 6.397%
GNA_063131104_Capacity | North Valley and Sierra | Sacramento | WEST SACRAMENTO 1104 | 63131104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063131105_Capacity | North Valley and Sierra | Sacramento | WEST SACRAMENTO 1105 | 63131105 | Feeder | None | None | None | 94% | 0 | 0% | 11.33 | 10.65 | 94% | 0 | 0% | 11.33 | 10.61 | 93.65% | 0 | 0% | 11.33 | 10.59 | 93.47% | 0 | 0% | 11.33 | 10.59 | 93.47% | 0 | 0% | 11.33 | 10.62 | 93.73% | 0 | 0%
GNA_063131106_Capacity | North Valley and Sierra | Sacramento | WEST SACRAMENTO 1106 | 63131106 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0631302_Capacity | North Valley and Sierra | Sacramento | WEST SACRAMENTO BANK 2 | 631302 | Bank | None | None | None | 76.5% | 0 | 0% | 29.7 | 22.72 | 76.5% | 0 | 0% | 29.7 | 22.61 | 76.13% | 0 | 0% | 29.7 | 22.52 | 75.82% | 0 | 0% | 29.7 | 22.53 | 75.86% | 0 | 0% | 29.7 | 22.58 | 76.03% | 0 | 0%
GNA_063131107_Capacity | North Valley and Sierra | Sacramento | WEST SACRAMENTO 1107 | 63131107 | Feeder | None | None | None | 92.01% | 0 | 0% | 15.14 | 13.93 | 92.01% | 0 | 0% | 15.14 | 13.84 | 91.41% | 0 | 0% | 15.14 | 13.79 | 91.08% | 0 | 0% | 15.14 | 13.81 | 91.22% | 0 | 0% | 15.14 | 13.88 | 91.68% | 0 | 0%
GNA_063131108_Capacity | North Valley and Sierra | Sacramento | WEST SACRAMENTO 1108 | 63131108 | Feeder | None | None | None | 78.01% | 0 | 0% | 12.19 | 9.51 | 78.01% | 0 | 0% | 12.19 | 9.5 | 77.93% | 0 | 0% | 12.19 | 9.46 | 77.6% | 0 | 0% | 12.19 | 9.44 | 77.44% | 0 | 0% | 12.19 | 9.43 | 77.36% | 0 | 0%
GNA_0631303_Capacity | North Valley and Sierra | Sacramento | WEST SACRAMENTO BANK 3 | 631303 | Bank | Demand Growth | Capacity | 2027 | 100.6% | 0.28 | 0.6285% | 44.55 | 41.86 | 93.96% | 0 | 0% | 44.55 | 44.67 | 100.3% | 0.12 | 0.2694% | 44.55 | 44.65 | 100.2% | 0.1 | 0.2245% | 44.55 | 44.72 | 100.4% | 0.17 | 0.3816% | 44.55 | 44.83 | 100.6% | 0.28 | 0.6285%
GNA_063131109_Capacity | North Valley and Sierra | Sacramento | WEST SACRAMENTO 1109 | 63131109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063131110_Capacity | North Valley and Sierra | Sacramento | WEST SACRAMENTO 1110 | 63131110 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063131111_Capacity | North Valley and Sierra | Sacramento | WEST SACRAMENTO 1111 | 63131111 | Feeder | None | None | None | 99.92% | 0 | 0% | 12.19 | 11.9 | 97.62% | 0 | 0% | 12.19 | 12.18 | 99.92% | 0 | 0% | 12.19 | 12.18 | 99.92% | 0 | 0% | 12.19 | 12.18 | 99.92% | 0 | 0% | 12.19 | 12.17 | 99.84% | 0 | 0%
GNA_0634401_Capacity | North Valley and Sierra | Sacramento | PLAINFIELD BANK 1 | 634401 | Bank | None | None | None | 96.52% | 0 | 0% | 9.2 | 8.81 | 95.76% | 0 | 0% | 9.2 | 8.81 | 95.76% | 0 | 0% | 9.2 | 8.82 | 95.87% | 0 | 0% | 9.2 | 8.83 | 95.98% | 0 | 0% | 9.2 | 8.88 | 96.52% | 0 | 0%
GNA_063441101_Capacity | North Valley and Sierra | Sacramento | PLAINFIELD 1101 | 63441101 | Feeder | None | None | None | 83.16% | 0 | 0% | 10.69 | 8.82 | 82.51% | 0 | 0% | 10.69 | 8.82 | 82.51% | 0 | 0% | 10.69 | 8.83 | 82.6% | 0 | 0% | 10.69 | 8.84 | 82.69% | 0 | 0% | 10.69 | 8.89 | 83.16% | 0 | 0%
GNA_0634402_Capacity | North Valley and Sierra | Sacramento | PLAINFIELD BANK 2 | 634402 | Bank | None | None | None | 75.42% | 0 | 0% | 29.7 | 20.24 | 68.15% | 0 | 0% | 29.7 | 20.26 | 68.22% | 0 | 0% | 29.7 | 22.08 | 74.34% | 0 | 0% | 29.7 | 22.22 | 74.81% | 0 | 0% | 29.7 | 22.4 | 75.42% | 0 | 0%
GNA_063441105_Capacity | North Valley and Sierra | Sacramento | PLAINFIELD 1105 | 63441105 | Feeder | None | None | None | 81.15% | 0 | 0% | 13.26 | 8.92 | 67.27% | 0 | 0% | 13.26 | 8.91 | 67.19% | 0 | 0% | 13.26 | 10.7 | 80.69% | 0 | 0% | 13.26 | 10.73 | 80.92% | 0 | 0% | 13.26 | 10.76 | 81.15% | 0 | 0%
GNA_063441106_Capacity | North Valley and Sierra | Sacramento | PLAINFIELD 1106 | 63441106 | Feeder | None | None | None | 89.89% | 0 | 0% | 13.26 | 11.62 | 87.63% | 0 | 0% | 13.26 | 11.64 | 87.78% | 0 | 0% | 13.26 | 11.67 | 88.01% | 0 | 0% | 13.26 | 11.78 | 88.84% | 0 | 0% | 13.26 | 11.92 | 89.89% | 0 | 0%
GNA_0620301_Capacity | North Valley and Sierra | Sacramento | WOODLAND BANK 1 | 620301 | Bank | None | None | None | 86.17% | 0 | 0% | 44.6 | 36.51 | 81.86% | 0 | 0% | 44.6 | 37.63 | 84.37% | 0 | 0% | 44.6 | 38.07 | 85.36% | 0 | 0% | 44.6 | 38.2 | 85.65% | 0 | 0% | 44.6 | 38.43 | 86.17% | 0 | 0%
GNA_062031101_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1101 | 62031101 | Feeder | None | None | None | 94.26% | 0 | 0% | 12.19 | 11.1 | 91.06% | 0 | 0% | 12.19 | 11.18 | 91.71% | 0 | 0% | 12.19 | 11.26 | 92.37% | 0 | 0% | 12.19 | 11.36 | 93.19% | 0 | 0% | 12.19 | 11.49 | 94.26% | 0 | 0%
GNA_062031102_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1102 | 62031102 | Feeder | None | None | None | 99.91% | 0 | 0% | 10.76 | 9.32 | 86.62% | 0 | 0% | 10.76 | 10.39 | 96.56% | 0 | 0% | 10.76 | 10.75 | 99.91% | 0 | 0% | 10.76 | 10.75 | 99.91% | 0 | 0% | 10.76 | 10.75 | 99.91% | 0 | 0%
GNA_062031103_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1103 | 62031103 | Feeder | None | None | None | 87.37% | 0 | 0% | 12.19 | 10.52 | 86.3% | 0 | 0% | 12.19 | 10.52 | 86.3% | 0 | 0% | 12.19 | 10.53 | 86.38% | 0 | 0% | 12.19 | 10.57 | 86.71% | 0 | 0% | 12.19 | 10.65 | 87.37% | 0 | 0%
GNA_062031113_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1113 | 62031113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0620302_Capacity | North Valley and Sierra | Sacramento | WOODLAND BANK 2 | 620302 | Bank | None | None | None | 100.2% | 0.07 | 0.157% | 44.6 | 44.26 | 99.24% | 0 | 0% | 44.6 | 44.09 | 98.86% | 0 | 0% | 44.6 | 44.24 | 99.19% | 0 | 0% | 44.6 | 44.45 | 99.66% | 0 | 0% | 44.6 | 44.67 | 100.2% | 0.07 | 0.157%
GNA_062031104_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1104 | 62031104 | Feeder | None | None | None | 83.92% | 0 | 0% | 10.76 | 9.03 | 83.92% | 0 | 0% | 10.76 | 9.01 | 83.74% | 0 | 0% | 10.76 | 9 | 83.64% | 0 | 0% | 10.76 | 9.03 | 83.92% | 0 | 0% | 10.76 | 9.03 | 83.92% | 0 | 0%
GNA_062031105_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1105 | 62031105 | Feeder | Demand Growth | Capacity | 2026 | 101.8% | 0.23 | 1.793% | 12.83 | 12.1 | 94.31% | 0 | 0% | 12.83 | 12.7 | 98.99% | 0 | 0% | 12.83 | 12.8 | 99.77% | 0 | 0% | 12.83 | 12.94 | 100.9% | 0.11 | 0.8574% | 12.83 | 13.06 | 101.8% | 0.23 | 1.793%
GNA_062031106_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1106 | 62031106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062031107_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1107 | 62031107 | Feeder | None | None | None | 88.48% | 0 | 0% | 10.76 | 9.44 | 87.73% | 0 | 0% | 10.76 | 9.44 | 87.73% | 0 | 0% | 10.76 | 9.44 | 87.73% | 0 | 0% | 10.76 | 9.47 | 88.01% | 0 | 0% | 10.76 | 9.52 | 88.48% | 0 | 0%
GNA_062031108_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1108 | 62031108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0620303_Capacity | North Valley and Sierra | Sacramento | WOODLAND BANK 3 | 620303 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062031109_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1109 | 62031109 | Feeder | None | None | None | 99.67% | 0 | 0% | 12.19 | 12.15 | 99.67% | 0 | 0% | 12.19 | 12.12 | 99.43% | 0 | 0% | 12.19 | 12.1 | 99.26% | 0 | 0% | 12.19 | 12.08 | 99.1% | 0 | 0% | 12.19 | 12.1 | 99.26% | 0 | 0%
GNA_062031110_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1110 | 62031110 | Feeder | None | None | None | 98.76% | 0 | 0% | 12.1 | 11.39 | 94.13% | 0 | 0% | 12.1 | 11.94 | 98.68% | 0 | 0% | 12.1 | 11.93 | 98.6% | 0 | 0% | 12.1 | 11.94 | 98.68% | 0 | 0% | 12.1 | 11.95 | 98.76% | 0 | 0%
GNA_062031111_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1111 | 62031111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062031112_Capacity | North Valley and Sierra | Sacramento | WOODLAND 1112 | 62031112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0627201_Capacity | North Valley and Sierra | Sacramento | KNIGHTS LANDING BANK 1 | 627201 | Bank | None | None | None | 36.84% | 0 | 0% | 29.7 | 10.58 | 35.62% | 0 | 0% | 29.7 | 10.65 | 35.86% | 0 | 0% | 29.7 | 10.75 | 36.2% | 0 | 0% | 29.7 | 10.84 | 36.5% | 0 | 0% | 29.7 | 10.94 | 36.84% | 0 | 0%
GNA_062721101_Capacity | North Valley and Sierra | Sacramento | KNIGHTS LANDING 1101 | 62721101 | Feeder | None | None | None | 35.74% | 0 | 0% | 10.8 | 3.49 | 32.31% | 0 | 0% | 10.8 | 3.58 | 33.15% | 0 | 0% | 10.8 | 3.67 | 33.98% | 0 | 0% | 10.8 | 3.76 | 34.81% | 0 | 0% | 10.8 | 3.86 | 35.74% | 0 | 0%
GNA_062721102_Capacity | North Valley and Sierra | Sacramento | KNIGHTS LANDING 1102 | 62721102 | Feeder | None | None | None | 66.3% | 0 | 0% | 10.8 | 7.15 | 66.2% | 0 | 0% | 10.8 | 7.14 | 66.11% | 0 | 0% | 10.8 | 7.15 | 66.2% | 0 | 0% | 10.8 | 7.15 | 66.2% | 0 | 0% | 10.8 | 7.16 | 66.3% | 0 | 0%
GNA_0631901_Capacity | North Valley and Sierra | Sacramento | ZAMORA BANK 1 | 631901 | Bank | Demand Growth | Capacity | 2023 | 119.2% | 1.79 | 19.25% | 9.3 | 11.09 | 119.2% | 1.79 | 19.25% | 9.3 | 11.07 | 119% | 1.77 | 19.03% | 9.3 | 11.01 | 118.4% | 1.71 | 18.39% | 9.3 | 10.98 | 118.1% | 1.68 | 18.06% | 9.3 | 10.92 | 117.4% | 1.62 | 17.42%
GNA_063191105_Capacity | North Valley and Sierra | Sacramento | ZAMORA 1105 | 63191105 | Feeder | None | None | None | 53.54% | 0 | 0% | 10.46 | 5.6 | 53.54% | 0 | 0% | 10.46 | 5.6 | 53.54% | 0 | 0% | 10.46 | 5.59 | 53.44% | 0 | 0% | 10.46 | 5.58 | 53.35% | 0 | 0% | 10.46 | 5.57 | 53.25% | 0 | 0%
GNA_063191106_Capacity | North Valley and Sierra | Sacramento | ZAMORA 1106 | 63191106 | Feeder | None | None | None | 60.13% | 0 | 0% | 10.46 | 6.29 | 60.13% | 0 | 0% | 10.46 | 6.26 | 59.85% | 0 | 0% | 10.46 | 6.24 | 59.66% | 0 | 0% | 10.46 | 6.22 | 59.46% | 0 | 0% | 10.46 | 6.2 | 59.27% | 0 | 0%
GNA_0631902_Capacity | North Valley and Sierra | Sacramento | ZAMORA BANK 2 | 631902 | Bank | None | None | None | 60.73% | 0 | 0% | 15.84 | 9.07 | 57.26% | 0 | 0% | 15.84 | 9.62 | 60.73% | 0 | 0% | 15.84 | 9.59 | 60.54% | 0 | 0% | 15.84 | 9.53 | 60.16% | 0 | 0% | 15.84 | 9.45 | 59.66% | 0 | 0%
GNA_063191107_Capacity | North Valley and Sierra | Sacramento | ZAMORA 1107 | 63191107 | Feeder | None | None | None | 77.55% | 0 | 0% | 12.83 | 9.4 | 73.27% | 0 | 0% | 12.83 | 9.95 | 77.55% | 0 | 0% | 12.83 | 9.93 | 77.4% | 0 | 0% | 12.83 | 9.86 | 76.85% | 0 | 0% | 12.83 | 9.79 | 76.31% | 0 | 0%
GNA_0631701_Capacity | North Valley and Sierra | Sacramento | MADISON BANK 1 | 631701 | Bank | Demand Growth | Capacity | 2023 | 111% | 1.14 | 10.96% | 10.4 | 11.54 | 111% | 1.14 | 10.96% | 10.4 | 11.5 | 110.6% | 1.1 | 10.58% | 10.4 | 11.45 | 110.1% | 1.05 | 10.1% | 10.4 | 11.43 | 109.9% | 1.03 | 9.904% | 10.4 | 11.44 | 110% | 1.04 | 10%
GNA_063171103_Capacity | North Valley and Sierra | Sacramento | MADISON 1103 | 63171103 | Feeder | Demand Growth | Capacity | 2023 | 116.6% | 1.71 | 16.63% | 10.28 | 11.99 | 116.6% | 1.71 | 16.63% | 10.28 | 11.94 | 116.1% | 1.66 | 16.15% | 10.28 | 11.89 | 115.7% | 1.61 | 15.66% | 10.28 | 11.88 | 115.6% | 1.6 | 15.56% | 10.28 | 11.88 | 115.6% | 1.6 | 15.56%
GNA_0631702_Capacity | North Valley and Sierra | Sacramento | MADISON BANK 2 | 631702 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063171105_Capacity | North Valley and Sierra | Sacramento | MADISON 1105 | 63171105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0631703_Capacity | North Valley and Sierra | Sacramento | MADISON BANK 3 | 631703 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063172101_Capacity | North Valley and Sierra | Sacramento | MADISON 2101 | 63172101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0636801_Capacity | North Valley and Sierra | Sacramento | PUTAH CREEK BANK 1 | 636801 | Bank | None | None | None | 99.05% | 0 | 0% | 15.8 | 14.88 | 94.18% | 0 | 0% | 15.8 | 14.99 | 94.87% | 0 | 0% | 15.8 | 15.26 | 96.58% | 0 | 0% | 15.8 | 15.47 | 97.91% | 0 | 0% | 15.8 | 15.65 | 99.05% | 0 | 0%
GNA_063681102_Capacity | North Valley and Sierra | Sacramento | PUTAH CREEK 1102 | 63681102 | Feeder | None | None | None | 53.92% | 0 | 0% | 10.46 | 5.64 | 53.92% | 0 | 0% | 10.46 | 5.57 | 53.25% | 0 | 0% | 10.46 | 5.48 | 52.39% | 0 | 0% | 10.46 | 5.43 | 51.91% | 0 | 0% | 10.46 | 5.37 | 51.34% | 0 | 0%
GNA_063681103_Capacity | North Valley and Sierra | Sacramento | PUTAH CREEK 1103 | 63681103 | Feeder | None | None | None | 87.53% | 0 | 0% | 12.83 | 10.52 | 82% | 0 | 0% | 12.83 | 10.6 | 82.62% | 0 | 0% | 12.83 | 10.88 | 84.8% | 0 | 0% | 12.83 | 11.07 | 86.28% | 0 | 0% | 12.83 | 11.23 | 87.53% | 0 | 0%
GNA_0636802_Capacity | North Valley and Sierra | Sacramento | PUTAH CREEK BANK 2 | 636802 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_063681105_Capacity | North Valley and Sierra | Sacramento | PUTAH CREEK 1105 | 63681105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0633201_Capacity | North Valley and Sierra | Sacramento | WINTERS BANK 1 | 633201 | Bank | None | None | None | 48.3% | 0 | 0% | 12.36 | 5.97 | 48.3% | 0 | 0% | 12.36 | 5.97 | 48.3% | 0 | 0% | 12.36 | 5.95 | 48.14% | 0 | 0% | 12.36 | 5.95 | 48.14% | 0 | 0% | 12.36 | 5.94 | 48.06% | 0 | 0%
GNA_063321101_Capacity | North Valley and Sierra | Sacramento | WINTERS 1101 | 63321101 | Feeder | None | None | None | 36.84% | 0 | 0% | 8.55 | 3.15 | 36.84% | 0 | 0% | 8.55 | 3.15 | 36.84% | 0 | 0% | 8.55 | 3.14 | 36.73% | 0 | 0% | 8.55 | 3.14 | 36.73% | 0 | 0% | 8.55 | 3.14 | 36.73% | 0 | 0%
GNA_063321102_Capacity | North Valley and Sierra | Sacramento | WINTERS 1102 | 63321102 | Feeder | None | None | None | 39.3% | 0 | 0% | 8.55 | 3.36 | 39.3% | 0 | 0% | 8.55 | 3.35 | 39.18% | 0 | 0% | 8.55 | 3.34 | 39.06% | 0 | 0% | 8.55 | 3.34 | 39.06% | 0 | 0% | 8.55 | 3.33 | 38.95% | 0 | 0%
GNA_0625401_Capacity | North Valley and Sierra | Sacramento | MERIDIAN BANK 1 | 625401 | Bank | None | None | None | 45.22% | 0 | 0% | 19.75 | 8.93 | 45.22% | 0 | 0% | 19.75 | 8.91 | 45.11% | 0 | 0% | 19.75 | 8.91 | 45.11% | 0 | 0% | 19.75 | 8.9 | 45.06% | 0 | 0% | 19.75 | 8.9 | 45.06% | 0 | 0%
GNA_062541101_Capacity | North Valley and Sierra | Sacramento | MERIDIAN 1101 | 62541101 | Feeder | None | None | None | 47.27% | 0 | 0% | 6.41 | 3.03 | 47.27% | 0 | 0% | 6.41 | 3.02 | 47.11% | 0 | 0% | 6.41 | 3.02 | 47.11% | 0 | 0% | 6.41 | 3.01 | 46.96% | 0 | 0% | 6.41 | 3.01 | 46.96% | 0 | 0%
GNA_062541102_Capacity | North Valley and Sierra | Sacramento | MERIDIAN 1102 | 62541102 | Feeder | None | None | None | 70.34% | 0 | 0% | 8.53 | 6 | 70.34% | 0 | 0% | 8.53 | 5.99 | 70.22% | 0 | 0% | 8.53 | 5.99 | 70.22% | 0 | 0% | 8.53 | 5.99 | 70.22% | 0 | 0% | 8.53 | 5.99 | 70.22% | 0 | 0%
GNA_0627701_Capacity | North Valley and Sierra | Sacramento | WILKINS SLOUGH BANK 1 | 627701 | Bank | None | None | None | 83.98% | 0 | 0% | 8.8 | 7.39 | 83.98% | 0 | 0% | 8.8 | 7.38 | 83.86% | 0 | 0% | 8.8 | 7.38 | 83.86% | 0 | 0% | 8.8 | 7.37 | 83.75% | 0 | 0% | 8.8 | 7.36 | 83.64% | 0 | 0%
GNA_062771101_Capacity | North Valley and Sierra | Sacramento | WILKINS SLOUGH 1101 | 62771101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_062771102_Capacity | North Valley and Sierra | Sacramento | WILKINS SLOUGH 1102 | 62771102 | Feeder | None | None | None | 62.09% | 0 | 0% | 6.41 | 3.98 | 62.09% | 0 | 0% | 6.41 | 3.98 | 62.09% | 0 | 0% | 6.41 | 3.97 | 61.93% | 0 | 0% | 6.41 | 3.97 | 61.93% | 0 | 0% | 6.41 | 3.96 | 61.78% | 0 | 0%
GNA_062771103_Capacity | North Valley and Sierra | Sacramento | WILKINS SLOUGH 1103 | 62771103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022871113_Capacity | Bay Area | San Francisco | EMBARCADERO (SF Z) 1113 | 22871113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022871114_Capacity | Bay Area | San Francisco | EMBARCADERO (SF Z) 1114 | 22871114 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022871115_Capacity | Bay Area | San Francisco | EMBARCADERO (SF Z) 1115 | 22871115 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022871117_Capacity | Bay Area | San Francisco | EMBARCADERO (SF Z) 1117 | 22871117 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022871118_Capacity | Bay Area | San Francisco | EMBARCADERO (SF Z) 1118 | 22871118 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022871121_Capacity | Bay Area | San Francisco | EMBARCADERO (SF Z) 1121 | 22871121 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022871123_Capacity | Bay Area | San Francisco | EMBARCADERO (SF Z) 1123 | 22871123 | Feeder | None | None | None | 87.92% | 0 | 0% | 8.36 | 7.32 | 87.56% | 0 | 0% | 8.36 | 7.22 | 86.36% | 0 | 0% | 8.36 | 7.15 | 85.53% | 0 | 0% | 8.36 | 7.21 | 86.24% | 0 | 0% | 8.36 | 7.35 | 87.92% | 0 | 0%
GNA_022221108_Capacity | Bay Area | San Francisco | SF J 1108 | 22221108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0222201_Capacity | Bay Area | San Francisco | SF J BANK 1 | 222201 | Bank | None | None | None | 15.87% | 0 | 0% | 10.4 | 1.55 | 14.9% | 0 | 0% | 10.4 | 1.56 | 15% | 0 | 0% | 10.4 | 1.58 | 15.19% | 0 | 0% | 10.4 | 1.6 | 15.38% | 0 | 0% | 10.4 | 1.65 | 15.87% | 0 | 0%
GNA_022220403_Capacity | Bay Area | San Francisco | SF J 0403 | 22220403 | Feeder | None | None | None | 37.2% | 0 | 0% | 2.5 | 0.91 | 36.4% | 0 | 0% | 2.5 | 0.9 | 36% | 0 | 0% | 2.5 | 0.89 | 35.6% | 0 | 0% | 2.5 | 0.89 | 35.6% | 0 | 0% | 2.5 | 0.93 | 37.2% | 0 | 0%
GNA_022220407_Capacity | Bay Area | San Francisco | SF J 0407 | 22220407 | Feeder | None | None | None | 21.75% | 0 | 0% | 2.85 | 0.58 | 20.35% | 0 | 0% | 2.85 | 0.58 | 20.35% | 0 | 0% | 2.85 | 0.59 | 20.7% | 0 | 0% | 2.85 | 0.61 | 21.4% | 0 | 0% | 2.85 | 0.62 | 21.75% | 0 | 0%
GNA_022220409_Capacity | Bay Area | San Francisco | SF J 0409 | 22220409 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0222202_Capacity | Bay Area | San Francisco | SF J BANK 2 | 222202 | Bank | None | None | None | 31.01% | 0 | 0% | 11.9 | 3.42 | 28.74% | 0 | 0% | 11.9 | 3.44 | 28.91% | 0 | 0% | 11.9 | 3.5 | 29.41% | 0 | 0% | 11.9 | 3.59 | 30.17% | 0 | 0% | 11.9 | 3.69 | 31.01% | 0 | 0%
GNA_022220402_Capacity | Bay Area | San Francisco | SF J 0402 | 22220402 | Feeder | None | None | None | 57.45% | 0 | 0% | 2.82 | 1.44 | 51.06% | 0 | 0% | 2.82 | 1.45 | 51.42% | 0 | 0% | 2.82 | 1.49 | 52.84% | 0 | 0% | 2.82 | 1.55 | 54.96% | 0 | 0% | 2.82 | 1.62 | 57.45% | 0 | 0%
GNA_022220404_Capacity | Bay Area | San Francisco | SF J 0404 | 22220404 | Feeder | None | None | None | 29.23% | 0 | 0% | 2.6 | 0.67 | 25.77% | 0 | 0% | 2.6 | 0.67 | 25.77% | 0 | 0% | 2.6 | 0.69 | 26.54% | 0 | 0% | 2.6 | 0.72 | 27.69% | 0 | 0% | 2.6 | 0.76 | 29.23% | 0 | 0%
GNA_022220406_Capacity | Bay Area | San Francisco | SF J 0406 | 22220406 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022871112_Capacity | Bay Area | San Francisco | EMBARCADERO (SF Z) 1112 | 22871112 | Feeder | None | None | None | 69.86% | 0 | 0% | 8.36 | 5.84 | 69.86% | 0 | 0% | 8.36 | 5.84 | 69.86% | 0 | 0% | 8.36 | 5.84 | 69.86% | 0 | 0% | 8.36 | 5.82 | 69.62% | 0 | 0% | 8.36 | 5.83 | 69.74% | 0 | 0%
GNA_022871116_Capacity | Bay Area | San Francisco | EMBARCADERO (SF Z) 1116 | 22871116 | Feeder | None | None | None | 92.79% | 0 | 0% | 10.54 | 9.52 | 90.32% | 0 | 0% | 10.54 | 9.44 | 89.56% | 0 | 0% | 10.54 | 9.46 | 89.75% | 0 | 0% | 10.54 | 9.59 | 90.99% | 0 | 0% | 10.54 | 9.78 | 92.79% | 0 | 0%
GNA_022871119_Capacity | Bay Area | San Francisco | EMBARCADERO (SF Z) 1119 | 22871119 | Feeder | None | None | None | 72.56% | 0 | 0% | 12.83 | 8.79 | 68.51% | 0 | 0% | 12.83 | 9.31 | 72.56% | 0 | 0% | 12.83 | 9.25 | 72.1% | 0 | 0% | 12.83 | 9.22 | 71.86% | 0 | 0% | 12.83 | 9.24 | 72.02% | 0 | 0%
GNA_022871120_Capacity | Bay Area | San Francisco | EMBARCADERO (SF Z) 1120 | 22871120 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022871122_Capacity | Bay Area | San Francisco | EMBARCADERO (SF Z) 1122 | 22871122 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0223301_Capacity | Bay Area | San Francisco | HUNTERS POINT P BANK 1 | 223301 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022331103_Capacity | Bay Area | San Francisco | HUNTERS POINT (SF P) 1103 | 22331103 | Feeder | None | None | None | 87.99% | 0 | 0% | 11.57 | 7.99 | 69.06% | 0 | 0% | 11.57 | 9.35 | 80.81% | 0 | 0% | 11.57 | 9.54 | 82.45% | 0 | 0% | 11.57 | 9.86 | 85.22% | 0 | 0% | 11.57 | 10.18 | 87.99% | 0 | 0%
GNA_0224901_Capacity | Bay Area | San Francisco | YOSEMITE BANK 1 | 224901 | Bank | None | None | None | 79.55% | 0 | 0% | 3.96 | 2.6 | 65.66% | 0 | 0% | 3.96 | 2.71 | 68.43% | 0 | 0% | 3.96 | 2.84 | 71.72% | 0 | 0% | 3.96 | 2.99 | 75.51% | 0 | 0% | 3.96 | 3.15 | 79.55% | 0 | 0%
GNA_022490401_Capacity | Bay Area | San Francisco | YOSEMITE 0401 | 22490401 | Feeder | None | None | None | 68.77% | 0 | 0% | 2.85 | 1.49 | 52.28% | 0 | 0% | 2.85 | 1.6 | 56.14% | 0 | 0% | 2.85 | 1.72 | 60.35% | 0 | 0% | 2.85 | 1.83 | 64.21% | 0 | 0% | 2.85 | 1.96 | 68.77% | 0 | 0%
GNA_022490402_Capacity | Bay Area | San Francisco | YOSEMITE 0402 | 22490402 | Feeder | None | None | None | 40.7% | 0 | 0% | 2.85 | 1.07 | 37.54% | 0 | 0% | 2.85 | 1.09 | 38.25% | 0 | 0% | 2.85 | 1.1 | 38.6% | 0 | 0% | 2.85 | 1.13 | 39.65% | 0 | 0% | 2.85 | 1.16 | 40.7% | 0 | 0%
GNA_022331104_Capacity | Bay Area | San Francisco | HUNTERS POINT (SF P) 1104 | 22331104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022331105_Capacity | Bay Area | San Francisco | HUNTERS POINT (SF P) 1105 | 22331105 | Feeder | None | None | None | 87.22% | 0 | 0% | 12.83 | 11.19 | 87.22% | 0 | 0% | 12.83 | 11.08 | 86.36% | 0 | 0% | 12.83 | 10.59 | 82.54% | 0 | 0% | 12.83 | 10.57 | 82.39% | 0 | 0% | 12.83 | 10.6 | 82.62% | 0 | 0%
GNA_022331106_Capacity | Bay Area | San Francisco | HUNTERS POINT (SF P) 1106 | 22331106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0223306_Capacity | Bay Area | San Francisco | HUNTERS POINT P BANK 6 | 223306 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022331101_Capacity | Bay Area | San Francisco | HUNTERS POINT (SF P) 1101 | 22331101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022331102_Capacity | Bay Area | San Francisco | HUNTERS POINT (SF P) 1102 | 22331102 | Feeder | None | None | None | 94.68% | 0 | 0% | 10.28 | 9.14 | 88.91% | 0 | 0% | 11.65 | 11.03 | 94.68% | 0 | 0% | 11.65 | 10.93 | 93.82% | 0 | 0% | 11.65 | 10.94 | 93.91% | 0 | 0% | 11.65 | 11.02 | 94.59% | 0 | 0%
GNA_022331107_Capacity | Bay Area | San Francisco | HUNTERS POINT (SF P) 1107 | 22331107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022331108_Capacity | Bay Area | San Francisco | HUNTERS POINT (SF P) 1108 | 22331108 | Feeder | None | None | None | 82.8% | 0 | 0% | 11.57 | 8.64 | 74.68% | 0 | 0% | 11.57 | 8.99 | 77.7% | 0 | 0% | 11.57 | 9.07 | 78.39% | 0 | 0% | 11.57 | 9.3 | 80.38% | 0 | 0% | 11.57 | 9.58 | 82.8% | 0 | 0%
GNA_022331109_Capacity | Bay Area | San Francisco | HUNTERS POINT (SF P) 1109 | 22331109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022801120_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1120 | 22801120 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022801127_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1127 | 22801127 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022801128_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1128 | 22801128 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022801135_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1135 | 22801135 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022801136_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1136 | 22801136 | Feeder | None | None | None | 81.65% | 0 | 0% | 8.34 | 6.77 | 81.18% | 0 | 0% | 8.34 | 6.75 | 80.94% | 0 | 0% | 8.34 | 6.75 | 80.94% | 0 | 0% | 8.34 | 6.77 | 81.18% | 0 | 0% | 8.34 | 6.81 | 81.65% | 0 | 0%
GNA_022801140_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1140 (Doyle Drive Back Up) | 22801140 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0227841_Capacity | Bay Area | San Francisco | MARINA BANK 1 | 227841 | Bank | None | None | None | 29.42% | 0 | 0% | 9.28 | 2.47 | 26.62% | 0 | 0% | 9.28 | 2.52 | 27.16% | 0 | 0% | 9.28 | 2.58 | 27.8% | 0 | 0% | 9.28 | 2.64 | 28.45% | 0 | 0% | 9.28 | 2.73 | 29.42% | 0 | 0%
GNA_022780402_Capacity | Bay Area | San Francisco | MARINA (SF F) 0402 | 22780402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022780403_Capacity | Bay Area | San Francisco | MARINA (SF F) 0403 | 22780403 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022780404_Capacity | Bay Area | San Francisco | MARINA (SF F) 0404 | 22780404 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022780407_Capacity | Bay Area | San Francisco | MARINA (SF F) 0407 | 22780407 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0227842_Capacity | Bay Area | San Francisco | MARINA BANK 2 | 227842 | Bank | None | None | None | 28.34% | 0 | 0% | 9.28 | 2.46 | 26.51% | 0 | 0% | 9.28 | 2.47 | 26.62% | 0 | 0% | 9.28 | 2.51 | 27.05% | 0 | 0% | 9.28 | 2.57 | 27.69% | 0 | 0% | 9.28 | 2.63 | 28.34% | 0 | 0%
GNA_022780401_Capacity | Bay Area | San Francisco | MARINA (SF F) 0401 | 22780401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022780405_Capacity | Bay Area | San Francisco | MARINA (SF F) 0405 | 22780405 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022780408_Capacity | Bay Area | San Francisco | MARINA (SF F) 0408 | 22780408 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022781101_Capacity | Bay Area | San Francisco | MARINA (SF F) 1101 | 22781101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022781102_Capacity | Bay Area | San Francisco | MARINA (SF F) 1102 | 22781102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022781103_Capacity | Bay Area | San Francisco | MARINA (SF F) 1103 | 22781103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0223402_Capacity | Bay Area | San Francisco | BEACH Q BANK 2 | 223402 | Bank | None | None | None | 40.4% | 0 | 0% | 1.98 | 0.68 | 34.34% | 0 | 0% | 1.98 | 0.7 | 35.35% | 0 | 0% | 1.98 | 0.72 | 36.36% | 0 | 0% | 1.98 | 0.77 | 38.89% | 0 | 0% | 1.98 | 0.8 | 40.4% | 0 | 0%
GNA_022340402_Capacity | Bay Area | San Francisco | BEACH Q 0402 | 22340402 | Feeder | None | None | None | 36.24% | 0 | 0% | 2.18 | 0.68 | 31.19% | 0 | 0% | 2.18 | 0.69 | 31.65% | 0 | 0% | 2.18 | 0.72 | 33.03% | 0 | 0% | 2.18 | 0.76 | 34.86% | 0 | 0% | 2.18 | 0.79 | 36.24% | 0 | 0%
GNA_022801107_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1107 | 22801107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022801108_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1108C | 22801108 | Feeder | None | None | None | 73.63% | 0 | 0% | 9.52 | 7.01 | 73.63% | 0 | 0% | 9.52 | 6.96 | 73.11% | 0 | 0% | 9.52 | 6.91 | 72.58% | 0 | 0% | 9.52 | 6.92 | 72.69% | 0 | 0% | 9.52 | 6.98 | 73.32% | 0 | 0%
GNA_022801109_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1109 | 22801109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022801110_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1110 | 22801110 | Feeder | None | None | None | 72.19% | 0 | 0% | 7.55 | 5.1 | 67.55% | 0 | 0% | 7.55 | 5.06 | 67.02% | 0 | 0% | 7.55 | 5.11 | 67.68% | 0 | 0% | 7.55 | 5.28 | 69.93% | 0 | 0% | 7.55 | 5.45 | 72.19% | 0 | 0%
GNA_022801111_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1111 | 22801111 | Feeder | None | None | None | 86.33% | 0 | 0% | 8.34 | 7.2 | 86.33% | 0 | 0% | 8.34 | 7.14 | 85.61% | 0 | 0% | 8.34 | 7.09 | 85.01% | 0 | 0% | 8.34 | 7.1 | 85.13% | 0 | 0% | 8.34 | 7.15 | 85.73% | 0 | 0%
GNA_022801119_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1119 | 22801119 | Feeder | None | None | None | 91.5% | 0 | 0% | 7.06 | 6.29 | 89.09% | 0 | 0% | 7.06 | 6.27 | 88.81% | 0 | 0% | 7.06 | 6.26 | 88.67% | 0 | 0% | 7.06 | 6.37 | 90.23% | 0 | 0% | 7.06 | 6.46 | 91.5% | 0 | 0%
GNA_022801137_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1137 | 22801137 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022801138_Capacity | Bay Area | San Francisco | LARKIN (SF Y) 1138 | 22801138 | Feeder | None | None | None | 62.28% | 0 | 0% | 9.73 | 5.81 | 59.71% | 0 | 0% | 9.73 | 5.83 | 59.92% | 0 | 0% | 9.73 | 5.88 | 60.43% | 0 | 0% | 9.73 | 5.94 | 61.05% | 0 | 0% | 9.73 | 6.06 | 62.28% | 0 | 0%
GNA_0225301_Capacity | Bay Area | San Francisco | 6TH AVENUE BANK 1 | 225301 | Bank | None | None | None | 52.02% | 0 | 0% | 1.98 | 0.95 | 47.98% | 0 | 0% | 1.98 | 0.96 | 48.48% | 0 | 0% | 1.98 | 0.97 | 48.99% | 0 | 0% | 1.98 | 0.99 | 50% | 0 | 0% | 1.98 | 1.03 | 52.02% | 0 | 0%
GNA_022530401_Capacity | Bay Area | San Francisco | 6TH AVENUE 0401 | 22530401 | Feeder | None | None | None | 47.25% | 0 | 0% | 2.18 | 0.96 | 44.04% | 0 | 0% | 2.18 | 0.96 | 44.04% | 0 | 0% | 2.18 | 0.97 | 44.5% | 0 | 0% | 2.18 | 0.99 | 45.41% | 0 | 0% | 2.18 | 1.03 | 47.25% | 0 | 0%
GNA_0225303_Capacity | Bay Area | San Francisco | 6TH AVENUE BANK 3 | 225303 | Bank | None | None | None | 61.62% | 0 | 0% | 1.98 | 1.1 | 55.56% | 0 | 0% | 1.98 | 1.12 | 56.57% | 0 | 0% | 1.98 | 1.13 | 57.07% | 0 | 0% | 1.98 | 1.16 | 58.59% | 0 | 0% | 1.98 | 1.22 | 61.62% | 0 | 0%
GNA_022530403_Capacity | Bay Area | San Francisco | 6TH AVENUE 0403 | 22530403 | Feeder | None | None | None | 55.96% | 0 | 0% | 2.18 | 1.1 | 50.46% | 0 | 0% | 2.18 | 1.12 | 51.38% | 0 | 0% | 2.18 | 1.13 | 51.83% | 0 | 0% | 2.18 | 1.16 | 53.21% | 0 | 0% | 2.18 | 1.22 | 55.96% | 0 | 0%
GNA_0221001_Capacity | Bay Area | San Francisco | SF H BANK 1 (MARTIN) | 221001 | Bank | Demand Growth | Capacity | 2024 | 122.7% | 10.11 | 22.67% | 44.6 | 41.38 | 92.78% | 0 | 0% | 44.6 | 51.3 | 115% | 6.7 | 15.02% | 44.6 | 53.48 | 119.9% | 8.88 | 19.91% | 44.6 | 54 | 121.1% | 9.4 | 21.08% | 44.6 | 54.71 | 122.7% | 10.11 | 22.67%
GNA_022101101_Capacity | Bay Area | San Francisco | MARTIN (SF H) 1101 | 22101101 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022101102_Capacity | Bay Area | San Francisco | MARTIN (SF H) 1102 | 22101102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022101103_Capacity | Bay Area | San Francisco | MARTIN (SF H) 1103 | 22101103 | Feeder | None | None | None | 93.64% | 0 | 0% | 10.22 | 9.24 | 90.41% | 0 | 0% | 10.22 | 9.57 | 93.64% | 0 | 0% | 10.22 | 9.32 | 91.19% | 0 | 0% | 10.22 | 9.23 | 90.31% | 0 | 0% | 10.22 | 9.18 | 89.82% | 0 | 0%
GNA_022101104_Capacity | Bay Area | San Francisco | MARTIN (SF H) 1104 | 22101104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022101106_Capacity | Bay Area | San Francisco | MARTIN (SF H) 1106 | 22101106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022101107_Capacity | Bay Area | San Francisco | MARTIN (SF H) 1107 | 22101107 | Feeder | None | None | None | 64.13% | 0 | 0% | 10.76 | 6.42 | 59.67% | 0 | 0% | 10.76 | 6.48 | 60.22% | 0 | 0% | 10.76 | 6.56 | 60.97% | 0 | 0% | 10.76 | 6.71 | 62.36% | 0 | 0% | 10.76 | 6.9 | 64.13% | 0 | 0%
GNA_0224701_Capacity | Bay Area | San Francisco | ACTON BANK 1 | 224701 | Bank | None | None | None | 74.24% | 0 | 0% | 1.98 | 1.38 | 69.7% | 0 | 0% | 1.98 | 1.39 | 70.2% | 0 | 0% | 1.98 | 1.41 | 71.21% | 0 | 0% | 1.98 | 1.44 | 72.73% | 0 | 0% | 1.98 | 1.47 | 74.24% | 0 | 0%
GNA_022470401_Capacity | Bay Area | San Francisco | ACTON 0401 | 22470401 | Feeder | None | None | None | 64.19% | 0 | 0% | 2.29 | 1.38 | 60.26% | 0 | 0% | 2.29 | 1.38 | 60.26% | 0 | 0% | 2.29 | 1.4 | 61.14% | 0 | 0% | 2.29 | 1.44 | 62.88% | 0 | 0% | 2.29 | 1.47 | 64.19% | 0 | 0%
GNA_0224702_Capacity | Bay Area | San Francisco | ACTON BANK 2 | 224702 | Bank | None | None | None | 73.28% | 0 | 0% | 2.47 | 1.69 | 68.42% | 0 | 0% | 2.47 | 1.7 | 68.83% | 0 | 0% | 2.47 | 1.72 | 69.64% | 0 | 0% | 2.47 | 1.76 | 71.26% | 0 | 0% | 2.47 | 1.81 | 73.28% | 0 | 0%
GNA_022470402_Capacity | Bay Area | San Francisco | ACTON 0402 | 22470402 | Feeder | None | None | None | 62.81% | 0 | 0% | 2.85 | 1.67 | 58.6% | 0 | 0% | 2.85 | 1.68 | 58.95% | 0 | 0% | 2.85 | 1.7 | 59.65% | 0 | 0% | 2.85 | 1.74 | 61.05% | 0 | 0% | 2.85 | 1.79 | 62.81% | 0 | 0%
GNA_022101110_Capacity | Bay Area | San Francisco | MARTIN (SF H) 1110 | 22101110 | Feeder | None | None | None | 97.91% | 0 | 0% | 11.01 | 9.07 | 82.38% | 0 | 0% | 11.01 | 10.78 | 97.91% | 0 | 0% | 11.01 | 10.78 | 97.91% | 0 | 0% | 11.01 | 10.73 | 97.46% | 0 | 0% | 11.01 | 10.7 | 97.18% | 0 | 0%
GNA_0221002_Capacity | Bay Area | San Francisco | SF H BANK 2 (MARTIN) | 221002 | Bank | None | None | None | 44.82% | 0 | 0% | 44.6 | 16.25 | 36.43% | 0 | 0% | 44.6 | 17.49 | 39.22% | 0 | 0% | 44.6 | 18.63 | 41.77% | 0 | 0% | 44.6 | 19.22 | 43.09% | 0 | 0% | 44.6 | 19.99 | 44.82% | 0 | 0%
GNA_0221003_Capacity | Bay Area | San Francisco | SF H BANK 3 (MARTIN) | 221003 | Bank | None | None | None | 23.86% | 0 | 0% | 9.89 | 2.23 | 22.55% | 0 | 0% | 9.89 | 2.2 | 22.24% | 0 | 0% | 9.89 | 2.21 | 22.35% | 0 | 0% | 9.89 | 2.26 | 22.85% | 0 | 0% | 9.89 | 2.36 | 23.86% | 0 | 0%
GNA_022100402_Capacity | Bay Area | San Francisco | MARTIN (SF H) 0402 | 22100402 | Feeder | None | None | None | 51.85% | 0 | 0% | 2.97 | 1.4 | 47.14% | 0 | 0% | 2.97 | 1.38 | 46.46% | 0 | 0% | 2.97 | 1.4 | 47.14% | 0 | 0% | 2.97 | 1.46 | 49.16% | 0 | 0% | 2.97 | 1.54 | 51.85% | 0 | 0%
GNA_022100404_Capacity | Bay Area | San Francisco | MARTIN (SF H) 0404 | 22100404 | Feeder | None | None | None | 31.62% | 0 | 0% | 2.53 | 0.78 | 30.83% | 0 | 0% | 2.53 | 0.79 | 31.23% | 0 | 0% | 2.53 | 0.79 | 31.23% | 0 | 0% | 2.53 | 0.8 | 31.62% | 0 | 0% | 2.53 | 0.8 | 31.62% | 0 | 0%
GNA_022101105_Capacity | Bay Area | San Francisco | MARTIN (SF H) 1105 | 22101105 | Feeder | None | None | None | 99.24% | 0 | 0% | 10.52 | 9.11 | 86.6% | 0 | 0% | 10.52 | 9.68 | 92.02% | 0 | 0% | 10.52 | 9.86 | 93.73% | 0 | 0% | 10.52 | 10.12 | 96.2% | 0 | 0% | 10.52 | 10.44 | 99.24% | 0 | 0%
GNA_022101108_Capacity | Bay Area | San Francisco | MARTIN (SF H) 1108 | 22101108 | Feeder | None | None | None | 78.65% | 0 | 0% | 11.57 | 7.05 | 60.93% | 0 | 0% | 11.57 | 7.83 | 67.68% | 0 | 0% | 11.57 | 8.66 | 74.85% | 0 | 0% | 11.57 | 8.83 | 76.32% | 0 | 0% | 11.57 | 9.1 | 78.65% | 0 | 0%
GNA_0226701_Capacity | Bay Area | San Francisco | SILVER BANK 1 | 226701 | Bank | None | None | None | 61.84% | 0 | 0% | 2.28 | 1.33 | 58.33% | 0 | 0% | 2.28 | 1.33 | 58.33% | 0 | 0% | 2.28 | 1.35 | 59.21% | 0 | 0% | 2.28 | 1.38 | 60.53% | 0 | 0% | 2.28 | 1.41 | 61.84% | 0 | 0%
GNA_022670401_Capacity | Bay Area | San Francisco | SILVER 0401 | 22670401 | Feeder | None | None | None | 51.29% | 0 | 0% | 2.71 | 1.31 | 48.34% | 0 | 0% | 2.71 | 1.32 | 48.71% | 0 | 0% | 2.71 | 1.34 | 49.45% | 0 | 0% | 2.71 | 1.36 | 50.18% | 0 | 0% | 2.71 | 1.39 | 51.29% | 0 | 0%
GNA_0221004_Capacity | Bay Area | San Francisco | SF H BANK 4 (MARTIN) | 221004 | Bank | None | None | None | 80.87% | 0 | 0% | 44.6 | 12.78 | 28.65% | 0 | 0% | 44.6 | 14.51 | 32.53% | 0 | 0% | 44.6 | 31.54 | 70.72% | 0 | 0% | 44.6 | 33.7 | 75.56% | 0 | 0% | 44.6 | 36.07 | 80.87% | 0 | 0%
GNA_022101109_Capacity | Bay Area | San Francisco | MARTIN (SF H) 1109 | 22101109 | Feeder | None | None | None | 53.89% | 0 | 0% | 9.39 | 4.98 | 53.04% | 0 | 0% | 9.39 | 5.06 | 53.89% | 0 | 0% | 9.39 | 4.65 | 49.52% | 0 | 0% | 9.39 | 4.81 | 51.22% | 0 | 0% | 9.39 | 5.05 | 53.78% | 0 | 0%
GNA_0222741_Capacity | Bay Area | San Francisco | SF M BANK 41 | 222741 | Bank | None | None | None | 25.69% | 0 | 0% | 15.84 | 3.58 | 22.6% | 0 | 0% | 15.84 | 3.64 | 22.98% | 0 | 0% | 15.84 | 3.71 | 23.42% | 0 | 0% | 15.84 | 3.87 | 24.43% | 0 | 0% | 15.84 | 4.07 | 25.69% | 0 | 0%
GNA_022270401_Capacity | Bay Area | San Francisco | SF M 0401 (M1) | 22270401 | Feeder | None | None | None | 74.65% | 0 | 0% | 2.17 | 1.48 | 68.2% | 0 | 0% | 2.17 | 1.49 | 68.66% | 0 | 0% | 2.17 | 1.5 | 69.12% | 0 | 0% | 2.17 | 1.55 | 71.43% | 0 | 0% | 2.17 | 1.62 | 74.65% | 0 | 0%
GNA_022270402_Capacity | Bay Area | San Francisco | SF M 0402 (M2) | 22270402 | Feeder | None | None | None | 47.64% | 0 | 0% | 2.54 | 1.08 | 42.52% | 0 | 0% | 2.54 | 1.1 | 43.31% | 0 | 0% | 2.54 | 1.12 | 44.09% | 0 | 0% | 2.54 | 1.16 | 45.67% | 0 | 0% | 2.54 | 1.21 | 47.64% | 0 | 0%
GNA_022270403_Capacity | Bay Area | San Francisco | SF M 0403 (M3) | 22270403 | Feeder | None | None | None | 53.7% | 0 | 0% | 2.7 | 1.2 | 44.44% | 0 | 0% | 2.7 | 1.23 | 45.56% | 0 | 0% | 2.7 | 1.26 | 46.67% | 0 | 0% | 2.7 | 1.35 | 50% | 0 | 0% | 2.7 | 1.45 | 53.7% | 0 | 0%
GNA_0222742_Capacity | Bay Area | San Francisco | SF M BANK 42 | 222742 | Bank | None | None | None | 30.62% | 0 | 0% | 15.84 | 4.36 | 27.53% | 0 | 0% | 15.84 | 4.44 | 28.03% | 0 | 0% | 15.84 | 4.5 | 28.41% | 0 | 0% | 15.84 | 4.64 | 29.29% | 0 | 0% | 15.84 | 4.85 | 30.62% | 0 | 0%
GNA_022270404_Capacity | Bay Area | San Francisco | SF M 0404 (M4) | 22270404 | Feeder | None | None | None | 56.67% | 0 | 0% | 2.7 | 1.35 | 50% | 0 | 0% | 2.7 | 1.39 | 51.48% | 0 | 0% | 2.7 | 1.41 | 52.22% | 0 | 0% | 2.7 | 1.46 | 54.07% | 0 | 0% | 2.7 | 1.53 | 56.67% | 0 | 0%
GNA_022270405_Capacity | Bay Area | San Francisco | SF M 0405 (M5) | 22270405 | Feeder | None | None | None | 59.06% | 0 | 0% | 2.54 | 1.33 | 52.36% | 0 | 0% | 2.54 | 1.35 | 53.15% | 0 | 0% | 2.54 | 1.39 | 54.72% | 0 | 0% | 2.54 | 1.44 | 56.69% | 0 | 0% | 2.54 | 1.5 | 59.06% | 0 | 0%
GNA_022270406_Capacity | Bay Area | San Francisco | SF M 0406 (M6) | 22270406 | Feeder | None | None | None | 72.22% | 0 | 0% | 2.7 | 1.8 | 66.67% | 0 | 0% | 2.7 | 1.82 | 67.41% | 0 | 0% | 2.7 | 1.84 | 68.15% | 0 | 0% | 2.7 | 1.88 | 69.63% | 0 | 0% | 2.7 | 1.95 | 72.22% | 0 | 0%
GNA_0221009_Capacity | Bay Area | San Francisco | SF H BANK 9 (MARTIN) | 221009 | Bank | None | None | None | 80.22% | 0 | 0% | 44.6 | 32.41 | 72.67% | 0 | 0% | 44.6 | 33.06 | 74.13% | 0 | 0% | 44.6 | 33.71 | 75.58% | 0 | 0% | 44.6 | 34.64 | 77.67% | 0 | 0% | 44.6 | 35.78 | 80.22% | 0 | 0%
GNA_022261101_Capacity | Bay Area | San Francisco | SF L 1101 | 22261101 | Feeder | None | None | None | 60.1% | 0 | 0% | 8.42 | 4.24 | 50.36% | 0 | 0% | 8.42 | 4.34 | 51.54% | 0 | 0% | 8.42 | 4.46 | 52.97% | 0 | 0% | 8.42 | 4.75 | 56.41% | 0 | 0% | 8.42 | 5.06 | 60.1% | 0 | 0%
GNA_0225001_Capacity | Bay Area | San Francisco | TARAVAL BANK 1 | 225001 | Bank | None | None | None | 37.72% | 0 | 0% | 2.28 | 0.75 | 32.89% | 0 | 0% | 2.28 | 0.76 | 33.33% | 0 | 0% | 2.28 | 0.78 | 34.21% | 0 | 0% | 2.28 | 0.82 | 35.96% | 0 | 0% | 2.28 | 0.86 | 37.72% | 0 | 0%
GNA_022500401_Capacity | Bay Area | San Francisco | TARAVAL 0401 | 22500401 | Feeder | None | None | None | 35.42% | 0 | 0% | 2.4 | 0.74 | 30.83% | 0 | 0% | 2.4 | 0.75 | 31.25% | 0 | 0% | 2.4 | 0.77 | 32.08% | 0 | 0% | 2.4 | 0.82 | 34.17% | 0 | 0% | 2.4 | 0.85 | 35.42% | 0 | 0%
GNA_0225002_Capacity | Bay Area | San Francisco | TARAVAL BANK 2 | 225002 | Bank | None | None | None | 64.14% | 0 | 0% | 1.98 | 1.12 | 56.57% | 0 | 0% | 1.98 | 1.13 | 57.07% | 0 | 0% | 1.98 | 1.15 | 58.08% | 0 | 0% | 1.98 | 1.2 | 60.61% | 0 | 0% | 1.98 | 1.27 | 64.14% | 0 | 0%
GNA_022500402_Capacity | Bay Area | San Francisco | TARAVAL 0402 | 22500402 | Feeder | None | None | None | 60.29% | 0 | 0% | 2.09 | 1.11 | 53.11% | 0 | 0% | 2.09 | 1.12 | 53.59% | 0 | 0% | 2.09 | 1.14 | 54.55% | 0 | 0% | 2.09 | 1.19 | 56.94% | 0 | 0% | 2.09 | 1.26 | 60.29% | 0 | 0%
GNA_0225003_Capacity | Bay Area | San Francisco | TARAVAL BANK 3 | 225003 | Bank | None | None | None | 68.15% | 0 | 0% | 2.48 | 1.43 | 57.66% | 0 | 0% | 2.48 | 1.46 | 58.87% | 0 | 0% | 2.48 | 1.49 | 60.08% | 0 | 0% | 2.48 | 1.58 | 63.71% | 0 | 0% | 2.48 | 1.69 | 68.15% | 0 | 0%
GNA_022500403_Capacity | Bay Area | San Francisco | TARAVAL 0403 | 22500403 | Feeder | None | None | None | 63.74% | 0 | 0% | 2.62 | 1.42 | 54.2% | 0 | 0% | 2.62 | 1.45 | 55.34% | 0 | 0% | 2.62 | 1.48 | 56.49% | 0 | 0% | 2.62 | 1.57 | 59.92% | 0 | 0% | 2.62 | 1.67 | 63.74% | 0 | 0%
GNA_022261102_Capacity | Bay Area | San Francisco | SF L 1102 | 22261102 | Feeder | Demand Growth | Capacity | 2026 | 106.3% | 0.6 | 6.303% | 9.52 | 9.18 | 96.43% | 0 | 0% | 9.52 | 9.32 | 97.9% | 0 | 0% | 9.52 | 9.43 | 99.05% | 0 | 0% | 9.52 | 9.74 | 102.3% | 0.22 | 2.311% | 9.52 | 10.12 | 106.3% | 0.6 | 6.303%
GNA_0225501_Capacity | Bay Area | San Francisco | 21ST AVENUE BANK 1 | 225501 | Bank | None | None | None | 61.84% | 0 | 0% | 2.28 | 1.25 | 54.82% | 0 | 0% | 2.28 | 1.28 | 56.14% | 0 | 0% | 2.28 | 1.3 | 57.02% | 0 | 0% | 2.28 | 1.33 | 58.33% | 0 | 0% | 2.28 | 1.41 | 61.84% | 0 | 0%
GNA_022550401_Capacity | Bay Area | San Francisco | 21ST AVENUE 0401 | 22550401 | Feeder | None | None | None | 58.75% | 0 | 0% | 2.4 | 1.24 | 51.67% | 0 | 0% | 2.4 | 1.27 | 52.92% | 0 | 0% | 2.4 | 1.29 | 53.75% | 0 | 0% | 2.4 | 1.33 | 55.42% | 0 | 0% | 2.4 | 1.41 | 58.75% | 0 | 0%
GNA_0225503_Capacity | Bay Area | San Francisco | 21ST AVENUE BANK 3 | 225503 | Bank | None | None | None | 58.77% | 0 | 0% | 2.28 | 1.19 | 52.19% | 0 | 0% | 2.28 | 1.23 | 53.95% | 0 | 0% | 2.28 | 1.24 | 54.39% | 0 | 0% | 2.28 | 1.29 | 56.58% | 0 | 0% | 2.28 | 1.34 | 58.77% | 0 | 0%
GNA_022550403_Capacity | Bay Area | San Francisco | 21ST AVENUE 0403 | 22550403 | Feeder | None | None | None | 55.42% | 0 | 0% | 2.4 | 1.19 | 49.58% | 0 | 0% | 2.4 | 1.22 | 50.83% | 0 | 0% | 2.4 | 1.23 | 51.25% | 0 | 0% | 2.4 | 1.28 | 53.33% | 0 | 0% | 2.4 | 1.33 | 55.42% | 0 | 0%
GNA_0225101_Capacity | Bay Area | San Francisco | NORIEGA BANK 1 | 225101 | Bank | None | None | None | 32.02% | 0 | 0% | 2.28 | 0.64 | 28.07% | 0 | 0% | 2.28 | 0.65 | 28.51% | 0 | 0% | 2.28 | 0.66 | 28.95% | 0 | 0% | 2.28 | 0.69 | 30.26% | 0 | 0% | 2.28 | 0.73 | 32.02% | 0 | 0%
GNA_022510401_Capacity | Bay Area | San Francisco | NORIEGA 0401 | 22510401 | Feeder | None | None | None | 26.57% | 0 | 0% | 2.71 | 0.63 | 23.25% | 0 | 0% | 2.71 | 0.64 | 23.62% | 0 | 0% | 2.71 | 0.65 | 23.99% | 0 | 0% | 2.71 | 0.68 | 25.09% | 0 | 0% | 2.71 | 0.72 | 26.57% | 0 | 0%
GNA_022261103_Capacity | Bay Area | San Francisco | SF L 1103 | 22261103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0225801_Capacity | Bay Area | San Francisco | OCEAN BANK 1 | 225801 | Bank | None | None | None | 78.51% | 0 | 0% | 2.28 | 1.57 | 68.86% | 0 | 0% | 2.28 | 1.6 | 70.18% | 0 | 0% | 2.28 | 1.63 | 71.49% | 0 | 0% | 2.28 | 1.69 | 74.12% | 0 | 0% | 2.28 | 1.79 | 78.51% | 0 | 0%
GNA_022580401_Capacity | Bay Area | San Francisco | OCEAN 0401 | 22580401 | Feeder | None | None | None | 71.77% | 0 | 0% | 2.48 | 1.55 | 62.5% | 0 | 0% | 2.48 | 1.59 | 64.11% | 0 | 0% | 2.48 | 1.62 | 65.32% | 0 | 0% | 2.48 | 1.68 | 67.74% | 0 | 0% | 2.48 | 1.78 | 71.77% | 0 | 0%
GNA_0225802_Capacity | Bay Area | San Francisco | OCEAN BANK 2 | 225802 | Bank | None | None | None | 67.98% | 0 | 0% | 2.28 | 1.34 | 58.77% | 0 | 0% | 2.28 | 1.39 | 60.96% | 0 | 0% | 2.28 | 1.42 | 62.28% | 0 | 0% | 2.28 | 1.48 | 64.91% | 0 | 0% | 2.28 | 1.55 | 67.98% | 0 | 0%
GNA_022580402_Capacity | Bay Area | San Francisco | OCEAN 0402 | 22580402 | Feeder | None | None | None | 54.8% | 0 | 0% | 2.81 | 1.33 | 47.33% | 0 | 0% | 2.81 | 1.37 | 48.75% | 0 | 0% | 2.81 | 1.41 | 50.18% | 0 | 0% | 2.81 | 1.47 | 52.31% | 0 | 0% | 2.81 | 1.54 | 54.8% | 0 | 0%
GNA_0222601_Capacity | Bay Area | San Francisco | SF L BANK 1 | 222601 | Bank | None | None | None | 29.81% | 0 | 0% | 12.38 | 3.21 | 25.93% | 0 | 0% | 12.38 | 3.29 | 26.58% | 0 | 0% | 12.38 | 3.38 | 27.3% | 0 | 0% | 12.38 | 3.52 | 28.43% | 0 | 0% | 12.38 | 3.69 | 29.81% | 0 | 0%
GNA_022260401_Capacity | Bay Area | San Francisco | SF L 0401 | 22260401 | Feeder | None | None | None | 44.96% | 0 | 0% | 2.58 | 0.93 | 36.05% | 0 | 0% | 2.58 | 0.97 | 37.6% | 0 | 0% | 2.58 | 1.01 | 39.15% | 0 | 0% | 2.58 | 1.08 | 41.86% | 0 | 0% | 2.58 | 1.16 | 44.96% | 0 | 0%
GNA_022260403_Capacity | Bay Area | San Francisco | SF L 0403 | 22260403 | Feeder | None | None | None | 34.36% | 0 | 0% | 1.63 | 0.49 | 30.06% | 0 | 0% | 1.63 | 0.5 | 30.67% | 0 | 0% | 1.63 | 0.52 | 31.9% | 0 | 0% | 1.63 | 0.53 | 32.52% | 0 | 0% | 1.63 | 0.56 | 34.36% | 0 | 0%
GNA_022260405_Capacity | Bay Area | San Francisco | SF L 0405 | 22260405 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022260407_Capacity | Bay Area | San Francisco | SF L 0407 | 22260407 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022260409_Capacity | Bay Area | San Francisco | SF L 0409 | 22260409 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0222602_Capacity | Bay Area | San Francisco | SF L BANK 2 | 222602 | Bank | None | None | None | 29.97% | 0 | 0% | 12.38 | 3.38 | 27.3% | 0 | 0% | 12.38 | 3.43 | 27.71% | 0 | 0% | 12.38 | 3.49 | 28.19% | 0 | 0% | 12.38 | 3.61 | 29.16% | 0 | 0% | 12.38 | 3.71 | 29.97% | 0 | 0%
GNA_022260402_Capacity | Bay Area | San Francisco | SF L 0402 | 22260402 | Feeder | None | None | None | 30.62% | 0 | 0% | 2.58 | 0.78 | 30.23% | 0 | 0% | 2.58 | 0.79 | 30.62% | 0 | 0% | 2.58 | 0.79 | 30.62% | 0 | 0% | 2.58 | 0.79 | 30.62% | 0 | 0% | 2.58 | 0.79 | 30.62% | 0 | 0%
GNA_022260404_Capacity | Bay Area | San Francisco | SF L 0404 | 22260404 | Feeder | None | None | None | 25.58% | 0 | 0% | 2.58 | 0.56 | 21.71% | 0 | 0% | 2.58 | 0.57 | 22.09% | 0 | 0% | 2.58 | 0.6 | 23.26% | 0 | 0% | 2.58 | 0.64 | 24.81% | 0 | 0% | 2.58 | 0.66 | 25.58% | 0 | 0%
GNA_022260406_Capacity | Bay Area | San Francisco | SF L 0406 | 22260406 | Feeder | None | None | None | 52.4% | 0 | 0% | 2.5 | 1.19 | 47.6% | 0 | 0% | 2.5 | 1.21 | 48.4% | 0 | 0% | 2.5 | 1.22 | 48.8% | 0 | 0% | 2.5 | 1.25 | 50% | 0 | 0% | 2.5 | 1.31 | 52.4% | 0 | 0%
GNA_022260408_Capacity | Bay Area | San Francisco | SF L 0408 | 22260408 | Feeder | None | None | None | 57.2% | 0 | 0% | 2.5 | 1.29 | 51.6% | 0 | 0% | 2.5 | 1.31 | 52.4% | 0 | 0% | 2.5 | 1.34 | 53.6% | 0 | 0% | 2.5 | 1.4 | 56% | 0 | 0% | 2.5 | 1.43 | 57.2% | 0 | 0%
GNA_0221005_Capacity | Bay Area | San Francisco | SF H BANK 5 (MARTIN) | 221005 | Bank | None | None | None | 43.17% | 0 | 0% | 9.89 | 3.62 | 36.6% | 0 | 0% | 9.89 | 3.84 | 38.83% | 0 | 0% | 9.89 | 4.08 | 41.25% | 0 | 0% | 9.89 | 4.16 | 42.06% | 0 | 0% | 9.89 | 4.27 | 43.17% | 0 | 0%
GNA_022100401_Capacity | Bay Area | San Francisco | MARTIN (SF H) 0401 | 22100401 | Feeder | None | None | None | 81.16% | 0 | 0% | 3.45 | 2.17 | 62.9% | 0 | 0% | 3.45 | 2.39 | 69.28% | 0 | 0% | 3.45 | 2.62 | 75.94% | 0 | 0% | 3.45 | 2.71 | 78.55% | 0 | 0% | 3.45 | 2.8 | 81.16% | 0 | 0%
GNA_022100403_Capacity | Bay Area | San Francisco | MARTIN (SF H) 0403 | 22100403 | Feeder | None | None | None | 11.51% | 0 | 0% | 3.04 | 0.34 | 11.18% | 0 | 0% | 3.04 | 0.34 | 11.18% | 0 | 0% | 3.04 | 0.34 | 11.18% | 0 | 0% | 3.04 | 0.34 | 11.18% | 0 | 0% | 3.04 | 0.35 | 11.51% | 0 | 0%
GNA_022100405_Capacity | Bay Area | San Francisco | MARTIN (SF H) 0405 | 22100405 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022011101_Capacity | Bay Area | San Francisco | MISSION (SF X) 1101 | 22011101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022011102_Capacity | Bay Area | San Francisco | MISSION (SF X) 1102 | 22011102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022011104_Capacity | Bay Area | San Francisco | MISSION (SF X) 1104 | 22011104 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022011107_Capacity | Bay Area | San Francisco | MISSION (SF X) 1107 | 22011107 | Feeder | None | None | None | 60.12% | 0 | 0% | 9.73 | 5.58 | 57.35% | 0 | 0% | 9.73 | 5.64 | 57.97% | 0 | 0% | 9.73 | 5.7 | 58.58% | 0 | 0% | 9.73 | 5.76 | 59.2% | 0 | 0% | 9.73 | 5.85 | 60.12% | 0 | 0%
GNA_022011108_Capacity | Bay Area | San Francisco | MISSION (SF X) 1108 | 22011108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022011109_Capacity | Bay Area | San Francisco | MISSION (SF X) 1109 | 22011109 | Feeder | Demand Growth | Capacity | 2023 | 106.5% | 0.72 | 6.516% | 11.05 | 11.55 | 104.5% | 0.5 | 4.525% | 11.05 | 11.59 | 104.9% | 0.54 | 4.887% | 11.05 | 11.63 | 105.2% | 0.58 | 5.249% | 11.05 | 11.69 | 105.8% | 0.64 | 5.792% | 11.05 | 11.77 | 106.5% | 0.72 | 6.516%
GNA_022011110_Capacity | Bay Area | San Francisco | MISSION (SF X) 1110 | 22011110 | Feeder | None | None | None | 87.18% | 0 | 0% | 8.66 | 7.49 | 86.49% | 0 | 0% | 8.66 | 7.55 | 87.18% | 0 | 0% | 8.66 | 6.93 | 80.02% | 0 | 0% | 8.66 | 7.11 | 82.1% | 0 | 0% | 8.66 | 7.29 | 84.18% | 0 | 0%
GNA_022011111_Capacity | Bay Area | San Francisco | MISSION (SF X) 1111 | 22011111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022011113_Capacity | Bay Area | San Francisco | MISSION (SF X) 1113 | 22011113 | Feeder | Demand Growth | Capacity | 2023 | 149.7% | 3.4 | 49.71% | 6.84 | 7.74 | 113.2% | 0.9 | 13.16% | 6.84 | 9.41 | 137.6% | 2.57 | 37.57% | 6.84 | 9.63 | 140.8% | 2.79 | 40.79% | 6.84 | 9.89 | 144.6% | 3.05 | 44.59% | 6.84 | 10.24 | 149.7% | 3.4 | 49.71%
GNA_022011116_Capacity | Bay Area | San Francisco | MISSION (SF X) 1116 | 22011116 | Feeder | None | None | None | 82.22% | 0 | 0% | 9.73 | 7.75 | 79.65% | 0 | 0% | 9.73 | 7.78 | 79.96% | 0 | 0% | 9.73 | 7.83 | 80.47% | 0 | 0% | 9.73 | 7.92 | 81.4% | 0 | 0% | 9.73 | 8 | 82.22% | 0 | 0%
GNA_022011118_Capacity | Bay Area | San Francisco | MISSION (SF X) 1118 | 22011118 | Feeder | Demand Growth | Capacity | 2026 | 101.3% | 0.11 | 1.319% | 8.34 | 7.98 | 95.68% | 0 | 0% | 8.34 | 8.1 | 97.12% | 0 | 0% | 8.34 | 8.23 | 98.68% | 0 | 0% | 8.34 | 8.45 | 101.3% | 0.11 | 1.319% | 8.34 | 8.33 | 99.88% | 0 | 0%
GNA_0225502_Capacity | Bay Area | San Francisco | 21ST AVENUE BANK 2 | 225502 | Bank | None | None | None | 64.52% | 0 | 0% | 2.48 | 1.36 | 54.84% | 0 | 0% | 2.48 | 1.39 | 56.05% | 0 | 0% | 2.48 | 1.43 | 57.66% | 0 | 0% | 2.48 | 1.49 | 60.08% | 0 | 0% | 2.48 | 1.6 | 64.52% | 0 | 0%
GNA_022550402_Capacity | Bay Area | San Francisco | 21ST AVENUE 0402 | 22550402 | Feeder | None | None | None | 62.65% | 0 | 0% | 2.57 | 1.36 | 52.92% | 0 | 0% | 2.57 | 1.4 | 54.47% | 0 | 0% | 2.57 | 1.43 | 55.64% | 0 | 0% | 2.57 | 1.49 | 57.98% | 0 | 0% | 2.57 | 1.61 | 62.65% | 0 | 0%
GNA_0224001_Capacity | Bay Area | San Francisco | JUDAH BANK 1 | 224001 | Bank | None | None | None | 96.97% | 0 | 0% | 1.98 | 1.75 | 88.38% | 0 | 0% | 1.98 | 1.8 | 90.91% | 0 | 0% | 1.98 | 1.85 | 93.43% | 0 | 0% | 1.98 | 1.92 | 96.97% | 0 | 0% | 1.98 | 1.59 | 80.3% | 0 | 0%
GNA_022400401_Capacity | Bay Area | San Francisco | JUDAH 0401 | 22400401 | Feeder | None | None | None | 91.87% | 0 | 0% | 2.09 | 1.75 | 83.73% | 0 | 0% | 2.09 | 1.8 | 86.12% | 0 | 0% | 2.09 | 1.85 | 88.52% | 0 | 0% | 2.09 | 1.92 | 91.87% | 0 | 0% | 2.09 | 1.59 | 76.08% | 0 | 0%
GNA_0224002_Capacity | Bay Area | San Francisco | JUDAH BANK 2 | 224002 | Bank | None | None | None | 73.23% | 0 | 0% | 1.98 | 1.29 | 65.15% | 0 | 0% | 1.98 | 1.3 | 65.66% | 0 | 0% | 1.98 | 1.34 | 67.68% | 0 | 0% | 1.98 | 1.38 | 69.7% | 0 | 0% | 1.98 | 1.45 | 73.23% | 0 | 0%
GNA_022400402_Capacity | Bay Area | San Francisco | JUDAH 0402 | 22400402 | Feeder | None | None | None | 69.38% | 0 | 0% | 2.09 | 1.29 | 61.72% | 0 | 0% | 2.09 | 1.3 | 62.2% | 0 | 0% | 2.09 | 1.33 | 63.64% | 0 | 0% | 2.09 | 1.38 | 66.03% | 0 | 0% | 2.09 | 1.45 | 69.38% | 0 | 0%
GNA_022011120_Capacity | Bay Area | San Francisco | MISSION (SF X) 1120 | 22011120 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022011124_Capacity | Bay Area | San Francisco | MISSION (SF X) 1124 | 22011124 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022011125_Capacity | Bay Area | San Francisco | MISSION (SF X) 1125 | 22011125 | Feeder | Demand Growth | Capacity | 2023 | 114.4% | 1.76 | 14.44% | 12.19 | 13.8 | 113.2% | 1.61 | 13.21% | 12.19 | 13.82 | 113.4% | 1.63 | 13.37% | 12.19 | 13.84 | 113.5% | 1.65 | 13.54% | 12.19 | 13.87 | 113.8% | 1.68 | 13.78% | 12.19 | 13.95 | 114.4% | 1.76 | 14.44%
GNA_022011126_Capacity | Bay Area | San Francisco | MISSION (SF X) 1126 (Warriors Arena) | 22011126 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022011127_Capacity | Bay Area | San Francisco | MISSION (SF X) 1127 | 22011127 | Feeder | None | None | None | 59.56% | 0 | 0% | 12.19 | 6.54 | 53.65% | 0 | 0% | 12.19 | 7.26 | 59.56% | 0 | 0% | 12.19 | 7.24 | 59.39% | 0 | 0% | 12.19 | 7.24 | 59.39% | 0 | 0% | 12.19 | 7.25 | 59.47% | 0 | 0%
GNA_022011128_Capacity | Bay Area | San Francisco | MISSION (SF X) 1128 | 22011128 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022091101_Capacity | Bay Area | San Francisco | SF G 1101 | 22091101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0225302_Capacity | Bay Area | San Francisco | 6TH AVENUE BANK 2 | 225302 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022530402_Capacity | Bay Area | San Francisco | 6TH AVENUE 0402 | 22530402 | Feeder | None | None | None | 39.91% | 0 | 0% | 2.18 | 0.75 | 34.4% | 0 | 0% | 2.18 | 0.77 | 35.32% | 0 | 0% | 2.18 | 0.8 | 36.7% | 0 | 0% | 2.18 | 0.82 | 37.61% | 0 | 0% | 2.18 | 0.87 | 39.91% | 0 | 0%
GNA_022091102_Capacity | Bay Area | San Francisco | SF G 1102 | 22091102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0220901_Capacity | Bay Area | San Francisco | SF G BANK 1 | 220901 | Bank | None | None | None | 25.09% | 0 | 0% | 21.4 | 5.03 | 23.5% | 0 | 0% | 21.4 | 5.1 | 23.83% | 0 | 0% | 21.4 | 5.12 | 23.93% | 0 | 0% | 21.4 | 5.23 | 24.44% | 0 | 0% | 21.4 | 5.37 | 25.09% | 0 | 0%
GNA_022090401_Capacity | Bay Area | San Francisco | SF G 0401 | 22090401 | Feeder | None | None | None | 14.03% | 0 | 0% | 2.78 | 0.37 | 13.31% | 0 | 0% | 2.78 | 0.37 | 13.31% | 0 | 0% | 2.78 | 0.37 | 13.31% | 0 | 0% | 2.78 | 0.38 | 13.67% | 0 | 0% | 2.78 | 0.39 | 14.03% | 0 | 0%
GNA_022090403_Capacity | Bay Area | San Francisco | SF G 0403 | 22090403 | Feeder | None | None | None | 30.4% | 0 | 0% | 2.5 | 0.71 | 28.4% | 0 | 0% | 2.5 | 0.72 | 28.8% | 0 | 0% | 2.5 | 0.72 | 28.8% | 0 | 0% | 2.5 | 0.73 | 29.2% | 0 | 0% | 2.5 | 0.76 | 30.4% | 0 | 0%
GNA_022090405_Capacity | Bay Area | San Francisco | SF G 0405 | 22090405 | Feeder | None | None | None | 56.8% | 0 | 0% | 2.5 | 1.39 | 55.6% | 0 | 0% | 2.5 | 1.39 | 55.6% | 0 | 0% | 2.5 | 1.4 | 56% | 0 | 0% | 2.5 | 1.4 | 56% | 0 | 0% | 2.5 | 1.42 | 56.8% | 0 | 0%
GNA_022090407_Capacity | Bay Area | San Francisco | SF G 0407 | 22090407 | Feeder | None | None | None | 63.6% | 0 | 0% | 2.5 | 1.49 | 59.6% | 0 | 0% | 2.5 | 1.51 | 60.4% | 0 | 0% | 2.5 | 1.52 | 60.8% | 0 | 0% | 2.5 | 1.56 | 62.4% | 0 | 0% | 2.5 | 1.59 | 63.6% | 0 | 0%
GNA_022090409_Capacity | Bay Area | San Francisco | SF G 0409 | 22090409 | Feeder | None | None | None | 26% | 0 | 0% | 2.5 | 0.6 | 24% | 0 | 0% | 2.5 | 0.61 | 24.4% | 0 | 0% | 2.5 | 0.61 | 24.4% | 0 | 0% | 2.5 | 0.62 | 24.8% | 0 | 0% | 2.5 | 0.65 | 26% | 0 | 0%
GNA_022090411_Capacity | Bay Area | San Francisco | SF G 0411 | 22090411 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022090413_Capacity | Bay Area | San Francisco | SF G 0413 | 22090413 | Feeder | None | None | None | 37.6% | 0 | 0% | 2.5 | 0.89 | 35.6% | 0 | 0% | 2.5 | 0.9 | 36% | 0 | 0% | 2.5 | 0.9 | 36% | 0 | 0% | 2.5 | 0.92 | 36.8% | 0 | 0% | 2.5 | 0.94 | 37.6% | 0 | 0%
GNA_0220902_Capacity | Bay Area | San Francisco | SF G BANK 2 | 220902 | Bank | None | None | None | 31.45% | 0 | 0% | 21.4 | 6.27 | 29.3% | 0 | 0% | 21.4 | 6.36 | 29.72% | 0 | 0% | 21.4 | 6.45 | 30.14% | 0 | 0% | 21.4 | 6.57 | 30.7% | 0 | 0% | 21.4 | 6.73 | 31.45% | 0 | 0%
GNA_022090402_Capacity | Bay Area | San Francisco | SF G 0402 | 22090402 | Feeder | None | None | None | 20.8% | 0 | 0% | 2.5 | 0.49 | 19.6% | 0 | 0% | 2.5 | 0.5 | 20% | 0 | 0% | 2.5 | 0.5 | 20% | 0 | 0% | 2.5 | 0.51 | 20.4% | 0 | 0% | 2.5 | 0.52 | 20.8% | 0 | 0%
GNA_022090404_Capacity | Bay Area | San Francisco | SF G 0404 | 22090404 | Feeder | None | None | None | 53.14% | 0 | 0% | 2.07 | 0.97 | 46.86% | 0 | 0% | 2.07 | 1 | 48.31% | 0 | 0% | 2.07 | 1.02 | 49.28% | 0 | 0% | 2.07 | 1.05 | 50.72% | 0 | 0% | 2.07 | 1.1 | 53.14% | 0 | 0%
GNA_022090406_Capacity | Bay Area | San Francisco | SF G 0406 | 22090406 | Feeder | None | None | None | 31.2% | 0 | 0% | 2.5 | 0.71 | 28.4% | 0 | 0% | 2.5 | 0.73 | 29.2% | 0 | 0% | 2.5 | 0.73 | 29.2% | 0 | 0% | 2.5 | 0.75 | 30% | 0 | 0% | 2.5 | 0.78 | 31.2% | 0 | 0%
GNA_022090408_Capacity | Bay Area | San Francisco | SF G 0408 | 22090408 | Feeder | None | None | None | 52% | 0 | 0% | 2.5 | 1.17 | 46.8% | 0 | 0% | 2.5 | 1.2 | 48% | 0 | 0% | 2.5 | 1.22 | 48.8% | 0 | 0% | 2.5 | 1.25 | 50% | 0 | 0% | 2.5 | 1.3 | 52% | 0 | 0%
GNA_022090410_Capacity | Bay Area | San Francisco | SF G 0410 | 22090410 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022090412_Capacity | Bay Area | San Francisco | SF G 0412 | 22090412 | Feeder | None | None | None | 38.91% | 0 | 0% | 2.57 | 0.95 | 36.96% | 0 | 0% | 2.57 | 0.95 | 36.96% | 0 | 0% | 2.57 | 0.97 | 37.74% | 0 | 0% | 2.57 | 0.98 | 38.13% | 0 | 0% | 2.57 | 1 | 38.91% | 0 | 0%
GNA_022090414_Capacity | Bay Area | San Francisco | SF G 0414 | 22090414 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022131101_Capacity | Bay Area | San Francisco | SF K 1101 | 22131101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0221301_Capacity | Bay Area | San Francisco | SF K BANK 1 | 221301 | Bank | None | None | None | 48.42% | 0 | 0% | 15.84 | 6.58 | 41.54% | 0 | 0% | 15.84 | 6.69 | 42.23% | 0 | 0% | 15.84 | 6.81 | 42.99% | 0 | 0% | 15.84 | 7 | 44.19% | 0 | 0% | 15.84 | 7.67 | 48.42% | 0 | 0%
GNA_022130401_Capacity | Bay Area | San Francisco | SF K 0401 | 22130401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022130403_Capacity | Bay Area | San Francisco | SF K 0403 | 22130403 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022130405_Capacity | Bay Area | San Francisco | SF K 0405 | 22130405 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022130407_Capacity | Bay Area | San Francisco | SF K 0407 | 22130407 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022130409_Capacity | Bay Area | San Francisco | SF K 0409 | 22130409 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022130411_Capacity | Bay Area | San Francisco | SF K 0411 | 22130411 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0221302_Capacity | Bay Area | San Francisco | SF K BANK 2 | 221302 | Bank | None | None | None | 29.1% | 0 | 0% | 15.84 | 4.09 | 25.82% | 0 | 0% | 15.84 | 4.17 | 26.33% | 0 | 0% | 15.84 | 4.27 | 26.96% | 0 | 0% | 15.84 | 4.46 | 28.16% | 0 | 0% | 15.84 | 4.61 | 29.1% | 0 | 0%
GNA_022130402_Capacity | Bay Area | San Francisco | SF K 0402 | 22130402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022130404_Capacity | Bay Area | San Francisco | SF K 0404 | 22130404 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022130406_Capacity | Bay Area | San Francisco | SF K 0406 | 22130406 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022130408_Capacity | Bay Area | San Francisco | SF K 0408 | 22130408 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022130410_Capacity | Bay Area | San Francisco | SF K 0410 | 22130410 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022281101_Capacity | Bay Area | San Francisco | SF N 1101 | 22281101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0222801_Capacity | Bay Area | San Francisco | SF N BANK 1 | 222801 | Bank | None | None | None | 22.03% | 0 | 0% | 15.84 | 3.11 | 19.63% | 0 | 0% | 15.84 | 3.16 | 19.95% | 0 | 0% | 15.84 | 3.24 | 20.45% | 0 | 0% | 15.84 | 3.35 | 21.15% | 0 | 0% | 15.84 | 3.49 | 22.03% | 0 | 0%
GNA_022280401_Capacity | Bay Area | San Francisco | SF N 0401 | 22280401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022280403_Capacity | Bay Area | San Francisco | SF N 0403 | 22280403 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022280405_Capacity | Bay Area | San Francisco | SF N 0405 | 22280405 | Feeder | None | None | None | 47.87% | 0 | 0% | 2.82 | 1.3 | 46.1% | 0 | 0% | 2.82 | 1.31 | 46.45% | 0 | 0% | 2.82 | 1.32 | 46.81% | 0 | 0% | 2.82 | 1.33 | 47.16% | 0 | 0% | 2.82 | 1.35 | 47.87% | 0 | 0%
GNA_0222802_Capacity | Bay Area | San Francisco | SF N BANK 2 | 222802 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022280402_Capacity | Bay Area | San Francisco | SF N 0402 | 22280402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022280406_Capacity | Bay Area | San Francisco | SF N 0406 | 22280406 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022280408_Capacity | Bay Area | San Francisco | SF N 0408 | 22280408 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0220109_Capacity | Bay Area | San Francisco | MISSION X BANK 9 | 220109 | Bank | None | None | None | 44.95% | 0 | 0% | 1.98 | 0.8 | 40.4% | 0 | 0% | 1.98 | 0.82 | 41.41% | 0 | 0% | 1.98 | 0.83 | 41.92% | 0 | 0% | 1.98 | 0.86 | 43.43% | 0 | 0% | 1.98 | 0.89 | 44.95% | 0 | 0%
GNA_022010401_Capacity | Bay Area | San Francisco | MISSION (SF X) 0401 | 22010401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0220110_Capacity | Bay Area | San Francisco | MISSION X BANK 10 | 220110 | Bank | None | None | None | 48.99% | 0 | 0% | 1.98 | 0.93 | 46.97% | 0 | 0% | 1.98 | 0.94 | 47.47% | 0 | 0% | 1.98 | 0.95 | 47.98% | 0 | 0% | 1.98 | 0.96 | 48.48% | 0 | 0% | 1.98 | 0.97 | 48.99% | 0 | 0%
GNA_022010402_Capacity | Bay Area | San Francisco | MISSION (SF X) 0402 | 22010402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0220301_Capacity | Bay Area | San Francisco | POTRERO A BANK 1 | 220301 | Bank | Demand Growth | Capacity | 2024 | 162.6% | 39.64 | 62.58% | 68.24 | 68.55 | 100.5% | 0.31 | 0.4543% | 68.24 | 78.86 | 115.6% | 10.62 | 15.56% | 68.24 | 86.75 | 127.1% | 18.51 | 27.12% | 63.34 | 95.01 | 150% | 31.67 | 50% | 63.34 | 102.98 | 162.6% | 39.64 | 62.58%
GNA_022031105_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1105 | 22031105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022031106_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1106 | 22031106 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022031107_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1107 | 22031107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022031109_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1109 | 22031109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0224801_Capacity | Bay Area | San Francisco | CASTRO BANK 1 | 224801 | Bank | None | None | None | 67.17% | 0 | 0% | 1.98 | 1.18 | 59.6% | 0 | 0% | 1.98 | 1.21 | 61.11% | 0 | 0% | 1.98 | 1.24 | 62.63% | 0 | 0% | 1.98 | 1.27 | 64.14% | 0 | 0% | 1.98 | 1.33 | 67.17% | 0 | 0%
GNA_022480401_Capacity | Bay Area | San Francisco | CASTRO 0401 | 22480401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022031110_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1110 | 22031110 | Feeder | Demand Growth | Capacity | 2024 | 117.2% | 1.63 | 17.21% | 9.47 | 8.76 | 92.5% | 0 | 0% | 9.47 | 10.98 | 115.9% | 1.51 | 15.95% | 9.47 | 10.92 | 115.3% | 1.45 | 15.31% | 9.47 | 11.02 | 116.4% | 1.55 | 16.37% | 9.47 | 11.1 | 117.2% | 1.63 | 17.21%
GNA_022031112_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1112 | 22031112 | Feeder | Demand Growth | Capacity | 2023 | 105.4% | 0.51 | 5.357% | 9.52 | 9.96 | 104.6% | 0.44 | 4.622% | 9.52 | 9.97 | 104.7% | 0.45 | 4.727% | 9.52 | 9.98 | 104.8% | 0.46 | 4.832% | 9.52 | 10 | 105% | 0.48 | 5.042% | 9.52 | 10.03 | 105.4% | 0.51 | 5.357%
GNA_022031114_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1114 | 22031114 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022031115_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1115 | 22031115 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022031117_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1117 | 22031117 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0226101_Capacity | Bay Area | San Francisco | PORTOLA BANK 1 | 226101 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022610401_Capacity | Bay Area | San Francisco | PORTOLA 0401 | 22610401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0226102_Capacity | Bay Area | San Francisco | PORTOLA BANK 2 | 226102 | Bank | None | None | None | 79.29% | 0 | 0% | 1.98 | 1.37 | 69.19% | 0 | 0% | 1.98 | 1.4 | 70.71% | 0 | 0% | 1.98 | 1.46 | 73.74% | 0 | 0% | 1.98 | 1.52 | 76.77% | 0 | 0% | 1.98 | 1.57 | 79.29% | 0 | 0%
GNA_022610402_Capacity | Bay Area | San Francisco | PORTOLA 0402 | 22610402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022031118_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1118 | 22031118 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022031121_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1121 | 22031121 | Feeder | Demand Growth | Capacity | 2025 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0220302_Capacity | Bay Area | San Francisco | POTRERO A BANK 2 | 220302 | Bank | None | None | None | 70.65% | 0 | 0% | 64.15 | 40.39 | 62.96% | 0 | 0% | 64.15 | 42.14 | 65.69% | 0 | 0% | 64.15 | 42.74 | 66.63% | 0 | 0% | 64.15 | 43.92 | 68.46% | 0 | 0% | 64.15 | 45.32 | 70.65% | 0 | 0%
GNA_022031116_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1116 | 22031116 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022031119_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1119 | 22031119 | Feeder | None | None | None | 96.83% | 0 | 0% | 8.19 | 7.18 | 87.67% | 0 | 0% | 8.19 | 7.8 | 95.24% | 0 | 0% | 8.19 | 7.8 | 95.24% | 0 | 0% | 8.19 | 7.85 | 95.85% | 0 | 0% | 8.19 | 7.93 | 96.83% | 0 | 0%
GNA_0220741_Capacity | Bay Area | San Francisco | SF E BANK 41 | 220741 | Bank | None | None | None | 52.83% | 0 | 0% | 9.88 | 4.82 | 48.79% | 0 | 0% | 9.88 | 4.88 | 49.39% | 0 | 0% | 9.88 | 4.95 | 50.1% | 0 | 0% | 9.88 | 5.06 | 51.21% | 0 | 0% | 9.88 | 5.22 | 52.83% | 0 | 0%
GNA_022070401_Capacity | Bay Area | San Francisco | SF E 0401 | 22070401 | Feeder | None | None | None | 61.28% | 0 | 0% | 2.35 | 1.36 | 57.87% | 0 | 0% | 2.35 | 1.37 | 58.3% | 0 | 0% | 2.35 | 1.37 | 58.3% | 0 | 0% | 2.35 | 1.4 | 59.57% | 0 | 0% | 2.35 | 1.44 | 61.28% | 0 | 0%
GNA_022070406_Capacity | Bay Area | San Francisco | SF E 0406 | 22070406 | Feeder | None | None | None | 68.09% | 0 | 0% | 2.35 | 1.49 | 63.4% | 0 | 0% | 2.35 | 1.51 | 64.26% | 0 | 0% | 2.35 | 1.53 | 65.11% | 0 | 0% | 2.35 | 1.56 | 66.38% | 0 | 0% | 2.35 | 1.6 | 68.09% | 0 | 0%
GNA_022070407_Capacity | Bay Area | San Francisco | SF E 0407 | 22070407 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022070408_Capacity | Bay Area | San Francisco | SF E 0408 | 22070408 | Feeder | None | None | None | 61.28% | 0 | 0% | 2.35 | 1.32 | 56.17% | 0 | 0% | 2.35 | 1.34 | 57.02% | 0 | 0% | 2.35 | 1.35 | 57.45% | 0 | 0% | 2.35 | 1.38 | 58.72% | 0 | 0% | 2.35 | 1.44 | 61.28% | 0 | 0%
GNA_0220742_Capacity | Bay Area | San Francisco | SF E BANK 42 | 220742 | Bank | None | None | None | 29.25% | 0 | 0% | 9.88 | 2.58 | 26.11% | 0 | 0% | 9.88 | 2.63 | 26.62% | 0 | 0% | 9.88 | 2.67 | 27.02% | 0 | 0% | 9.88 | 2.77 | 28.04% | 0 | 0% | 9.88 | 2.89 | 29.25% | 0 | 0%
GNA_022070405_Capacity | Bay Area | San Francisco | SF E 0405 | 22070405 | Feeder | None | None | None | 52.34% | 0 | 0% | 2.35 | 1.13 | 48.09% | 0 | 0% | 2.35 | 1.15 | 48.94% | 0 | 0% | 2.35 | 1.15 | 48.94% | 0 | 0% | 2.35 | 1.19 | 50.64% | 0 | 0% | 2.35 | 1.23 | 52.34% | 0 | 0%
GNA_022070409_Capacity | Bay Area | San Francisco | SF E 0409 | 22070409 | Feeder | None | None | None | 39.15% | 0 | 0% | 2.35 | 0.89 | 37.87% | 0 | 0% | 2.35 | 0.89 | 37.87% | 0 | 0% | 2.35 | 0.89 | 37.87% | 0 | 0% | 2.35 | 0.9 | 38.3% | 0 | 0% | 2.35 | 0.92 | 39.15% | 0 | 0%
GNA_022070410_Capacity | Bay Area | San Francisco | SF E 0410 | 22070410 | Feeder | None | None | None | 71.72% | 0 | 0% | 1.98 | 1.25 | 63.13% | 0 | 0% | 1.98 | 1.28 | 64.65% | 0 | 0% | 1.98 | 1.31 | 66.16% | 0 | 0% | 1.98 | 1.35 | 68.18% | 0 | 0% | 1.98 | 1.42 | 71.72% | 0 | 0%
GNA_022071101_Capacity | Bay Area | San Francisco | SF E 1101 | 22071101 | Feeder | None | None | None | 40.7% | 0 | 0% | 10.22 | 3.73 | 36.5% | 0 | 0% | 10.22 | 3.82 | 37.38% | 0 | 0% | 10.22 | 3.9 | 38.16% | 0 | 0% | 10.22 | 4.06 | 39.73% | 0 | 0% | 10.22 | 4.16 | 40.7% | 0 | 0%
GNA_022071103_Capacity | Bay Area | San Francisco | SF E 1103 | 22071103 | Feeder | None | None | None | 80.25% | 0 | 0% | 8.66 | 5.7 | 65.82% | 0 | 0% | 8.66 | 6.47 | 74.71% | 0 | 0% | 8.66 | 6.58 | 75.98% | 0 | 0% | 8.66 | 6.75 | 77.94% | 0 | 0% | 8.66 | 6.95 | 80.25% | 0 | 0%
GNA_022071105_Capacity | Bay Area | San Francisco | SF E 1105 | 22071105 | Feeder | None | None | None | 82.12% | 0 | 0% | 9.62 | 7.12 | 74.01% | 0 | 0% | 9.62 | 7.26 | 75.47% | 0 | 0% | 9.62 | 7.41 | 77.03% | 0 | 0% | 9.62 | 7.62 | 79.21% | 0 | 0% | 9.62 | 7.9 | 82.12% | 0 | 0%
GNA_0223901_Capacity | Bay Area | San Francisco | 18TH STREET BANK 1 | 223901 | Bank | None | None | None | 80.05% | 0 | 0% | 3.96 | 2.88 | 72.73% | 0 | 0% | 3.96 | 2.94 | 74.24% | 0 | 0% | 3.96 | 3.01 | 76.01% | 0 | 0% | 3.96 | 3.08 | 77.78% | 0 | 0% | 3.96 | 3.17 | 80.05% | 0 | 0%
GNA_022390401_Capacity | Bay Area | San Francisco | 18TH STREET 0401 | 22390401 | Feeder | None | None | None | 52.67% | 0 | 0% | 2.43 | 1.17 | 48.15% | 0 | 0% | 2.43 | 1.2 | 49.38% | 0 | 0% | 2.43 | 1.23 | 50.62% | 0 | 0% | 2.43 | 1.24 | 51.03% | 0 | 0% | 2.43 | 1.28 | 52.67% | 0 | 0%
GNA_022390402_Capacity | Bay Area | San Francisco | 18TH STREET 0402 | 22390402 | Feeder | None | None | None | 78.19% | 0 | 0% | 2.43 | 1.71 | 70.37% | 0 | 0% | 2.43 | 1.74 | 71.6% | 0 | 0% | 2.43 | 1.79 | 73.66% | 0 | 0% | 2.43 | 1.84 | 75.72% | 0 | 0% | 2.43 | 1.9 | 78.19% | 0 | 0%
GNA_022071107_Capacity | Bay Area | San Francisco | SF E 1107 | 22071107 | Feeder | None | None | None | 71.22% | 0 | 0% | 9.52 | 6.22 | 65.34% | 0 | 0% | 9.52 | 6.35 | 66.7% | 0 | 0% | 9.52 | 6.4 | 67.23% | 0 | 0% | 9.52 | 6.57 | 69.01% | 0 | 0% | 9.52 | 6.78 | 71.22% | 0 | 0%
GNA_0224802_Capacity | Bay Area | San Francisco | CASTRO BANK 2 | 224802 | Bank | None | None | None | 54.04% | 0 | 0% | 1.98 | 0.94 | 47.47% | 0 | 0% | 1.98 | 0.97 | 48.99% | 0 | 0% | 1.98 | 0.99 | 50% | 0 | 0% | 1.98 | 1.03 | 52.02% | 0 | 0% | 1.98 | 1.07 | 54.04% | 0 | 0%
GNA_022480402_Capacity | Bay Area | San Francisco | CASTRO 0402 | 22480402 | Feeder | None | None | None | 54.36% | 0 | 0% | 1.95 | 0.92 | 47.18% | 0 | 0% | 1.95 | 0.96 | 49.23% | 0 | 0% | 1.95 | 0.98 | 50.26% | 0 | 0% | 1.95 | 1.02 | 52.31% | 0 | 0% | 1.95 | 1.06 | 54.36% | 0 | 0%
GNA_0220310_Capacity | Bay Area | San Francisco | POTRERO A BANK 10 | 220310 | Bank | Demand Growth | Capacity | 2023 | 120.3% | 10.64 | 20.27% | 52.5 | 61.34 | 116.8% | 8.84 | 16.84% | 52.5 | 63.14 | 120.3% | 10.64 | 20.27% | 52.5 | 62.85 | 119.7% | 10.35 | 19.71% | 52.5 | 62.71 | 119.4% | 10.21 | 19.45% | 52.5 | 62.79 | 119.6% | 10.29 | 19.6%
GNA_022031101_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1101 | 22031101 | Feeder | None | None | None | 98.21% | 0 | 0% | 9.52 | 8.94 | 93.91% | 0 | 0% | 9.52 | 8.92 | 93.7% | 0 | 0% | 9.52 | 9.03 | 94.85% | 0 | 0% | 9.52 | 9.17 | 96.32% | 0 | 0% | 9.52 | 9.35 | 98.21% | 0 | 0%
GNA_022031102_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1102 | 22031102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022031103_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1103 | 22031103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022031104_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1104 | 22031104 | Feeder | None | None | None | 97.95% | 0 | 0% | 10.26 | 9.86 | 96.1% | 0 | 0% | 10.26 | 9.85 | 96% | 0 | 0% | 10.26 | 9.88 | 96.3% | 0 | 0% | 10.26 | 9.91 | 96.59% | 0 | 0% | 10.26 | 10.05 | 97.95% | 0 | 0%
GNA_022031108_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1108 | 22031108 | Feeder | Demand Growth | Capacity | 2023 | 157.3% | 5.43 | 57.34% | 9.47 | 13.79 | 145.6% | 4.32 | 45.62% | 9.47 | 14.9 | 157.3% | 5.43 | 57.34% | 9.47 | 14.77 | 156% | 5.3 | 55.97% | 9.47 | 14.71 | 155.3% | 5.24 | 55.33% | 9.47 | 14.73 | 155.5% | 5.26 | 55.54%
GNA_022031111_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1111 | 22031111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_022031113_Capacity | Bay Area | San Francisco | POTRERO (SF A) 1113 | 22031113 | Feeder | Demand Growth | Capacity | 2024 | 111.4% | 0.93 | 11.36% | 8.19 | 8.17 | 99.76% | 0 | 0% | 8.19 | 9.1 | 111.1% | 0.91 | 11.11% | 8.19 | 9.09 | 111% | 0.9 | 10.99% | 8.19 | 9.1 | 111.1% | 0.91 | 11.11% | 8.19 | 9.12 | 111.4% | 0.93 | 11.36%
GNA_0838702_Capacity | South Bay and Central Coast | San Jose | FMC BANK 2 | 838702 | Bank | None | None | None | 92.53% | 0 | 0% | 29.7 | 27.48 | 92.53% | 0 | 0% | 29.7 | 27.31 | 91.95% | 0 | 0% | 29.7 | 27.21 | 91.62% | 0 | 0% | 29.7 | 27.23 | 91.68% | 0 | 0% | 29.7 | 27.29 | 91.89% | 0 | 0%
GNA_083871105_Capacity | South Bay and Central Coast | San Jose | FMC 1105 (OLD 1101) | 83871105 | Feeder | None | None | None | 87.56% | 0 | 0% | 21.38 | 18.72 | 87.56% | 0 | 0% | 21.38 | 18.56 | 86.81% | 0 | 0% | 21.38 | 18.45 | 86.3% | 0 | 0% | 21.38 | 18.47 | 86.39% | 0 | 0% | 21.38 | 18.54 | 86.72% | 0 | 0%
GNA_083871108_Capacity | South Bay and Central Coast | San Jose | FMC 1108 (old 1110) | 83871108 | Feeder | None | None | None | 78.1% | 0 | 0% | 12.83 | 10.02 | 78.1% | 0 | 0% | 12.83 | 10.02 | 78.1% | 0 | 0% | 12.83 | 10.02 | 78.1% | 0 | 0% | 12.83 | 10.02 | 78.1% | 0 | 0% | 12.83 | 10.02 | 78.1% | 0 | 0%
GNA_0838703_Capacity | South Bay and Central Coast | San Jose | FMC BANK 3 | 838703 | Bank | None | None | None | 43.27% | 0 | 0% | 44.6 | 18.51 | 41.5% | 0 | 0% | 44.6 | 18.7 | 41.93% | 0 | 0% | 44.6 | 18.9 | 42.38% | 0 | 0% | 44.6 | 19.08 | 42.78% | 0 | 0% | 44.6 | 19.3 | 43.27% | 0 | 0%
GNA_083871109_Capacity | South Bay and Central Coast | San Jose | FMC 1109 | 83871109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083871111_Capacity | South Bay and Central Coast | San Jose | FMC 1111 | 83871111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0822503_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A BANK 3 | 822503 | Bank | None | None | None | 94.01% | 0 | 0% | 29.7 | 23.27 | 78.35% | 0 | 0% | 29.7 | 24.02 | 80.88% | 0 | 0% | 29.7 | 26.98 | 90.84% | 0 | 0% | 29.7 | 27.85 | 93.77% | 0 | 0% | 29.7 | 27.92 | 94.01% | 0 | 0%
GNA_082251109_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A 1109 | 82251109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082251110_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A 1110 | 82251110 | Feeder | None | None | None | 79.21% | 0 | 0% | 11.93 | 8.85 | 74.18% | 0 | 0% | 11.93 | 8.81 | 73.85% | 0 | 0% | 11.93 | 9.41 | 78.88% | 0 | 0% | 11.93 | 9.41 | 78.88% | 0 | 0% | 11.93 | 9.45 | 79.21% | 0 | 0%
GNA_082251111_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A 1111 | 82251111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082251112_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A 1112 | 82251112 | Feeder | None | None | None | 92.08% | 0 | 0% | 12 | 11.05 | 92.08% | 0 | 0% | 12 | 10.92 | 91% | 0 | 0% | 12 | 10.88 | 90.67% | 0 | 0% | 12 | 10.88 | 90.67% | 0 | 0% | 12 | 10.92 | 91% | 0 | 0%
GNA_0822601_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B BANK 1 | 822601 | Bank | None | None | None | 90.65% | 0 | 0% | 37.42 | 25.46 | 68.04% | 0 | 0% | 37.42 | 25.62 | 68.47% | 0 | 0% | 37.42 | 26.99 | 72.13% | 0 | 0% | 37.42 | 30.28 | 80.92% | 0 | 0% | 37.42 | 33.92 | 90.65% | 0 | 0%
GNA_082261101_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1101 | 82261101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082261102_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1102 | 82261102 | Feeder | None | None | None | 75.7% | 0 | 0% | 11.4 | 8.3 | 72.81% | 0 | 0% | 11.4 | 8.38 | 73.51% | 0 | 0% | 11.4 | 8.46 | 74.21% | 0 | 0% | 11.4 | 8.54 | 74.91% | 0 | 0% | 11.4 | 8.63 | 75.7% | 0 | 0%
GNA_082261103_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1103 | 82261103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082261104_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1104 | 82261104 | Feeder | None | None | None | 75.21% | 0 | 0% | 12.83 | 2.66 | 20.73% | 0 | 0% | 12.83 | 2.66 | 20.73% | 0 | 0% | 12.83 | 2.65 | 20.65% | 0 | 0% | 12.83 | 6.11 | 47.62% | 0 | 0% | 12.83 | 9.65 | 75.21% | 0 | 0%
GNA_0822602_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B BANK 2 | 822602 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082261105_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1105 | 82261105 | Feeder | None | None | None | 83.66% | 0 | 0% | 11.57 | 9.68 | 83.66% | 0 | 0% | 11.57 | 9.59 | 82.89% | 0 | 0% | 11.57 | 9.56 | 82.63% | 0 | 0% | 11.57 | 9.57 | 82.71% | 0 | 0% | 11.57 | 9.65 | 83.41% | 0 | 0%
GNA_082261106_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1106 | 82261106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082261107_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1107 | 82261107 | Feeder | Demand Growth | Capacity | 2027 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082261108_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1108 | 82261108 | Feeder | None | None | None | 92.6% | 0 | 0% | 12.83 | 11.88 | 92.6% | 0 | 0% | 12.83 | 11.83 | 92.21% | 0 | 0% | 12.83 | 11.81 | 92.05% | 0 | 0% | 12.83 | 11.8 | 91.97% | 0 | 0% | 12.83 | 11.83 | 92.21% | 0 | 0%
GNA_0822603_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B BANK 3 | 822603 | Bank | None | None | None | 99.01% | 0 | 0% | 44.6 | 44.16 | 99.01% | 0 | 0% | 44.6 | 43.95 | 98.54% | 0 | 0% | 44.6 | 43.77 | 98.14% | 0 | 0% | 44.6 | 43.79 | 98.18% | 0 | 0% | 44.6 | 43.91 | 98.45% | 0 | 0%
GNA_082261109_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1109 | 82261109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082261110_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1110 | 82261110 | Feeder | None | None | None | 82.34% | 0 | 0% | 12.06 | 9.93 | 82.34% | 0 | 0% | 12.06 | 9.8 | 81.26% | 0 | 0% | 12.06 | 9.69 | 80.35% | 0 | 0% | 12.06 | 9.68 | 80.27% | 0 | 0% | 12.06 | 9.76 | 80.93% | 0 | 0%
GNA_082261111_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1111 | 82261111 | Feeder | None | None | None | 77.47% | 0 | 0% | 11.05 | 8.27 | 74.84% | 0 | 0% | 11.05 | 8.35 | 75.57% | 0 | 0% | 11.05 | 8.42 | 76.2% | 0 | 0% | 11.05 | 8.5 | 76.92% | 0 | 0% | 11.05 | 8.56 | 77.47% | 0 | 0%
GNA_082261112_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1112 | 82261112 | Feeder | None | None | None | 94.38% | 0 | 0% | 11.57 | 10.92 | 94.38% | 0 | 0% | 11.57 | 10.64 | 91.96% | 0 | 0% | 11.57 | 10.39 | 89.8% | 0 | 0% | 11.57 | 10.25 | 88.59% | 0 | 0% | 11.57 | 10.18 | 87.99% | 0 | 0%
GNA_082261113_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1113 | 82261113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0822604_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B BANK 4 | 822604 | Bank | None | None | None | 69.06% | 0 | 0% | 44.54 | 28.11 | 63.11% | 0 | 0% | 44.54 | 28.54 | 64.08% | 0 | 0% | 44.54 | 28.55 | 64.1% | 0 | 0% | 44.54 | 29.6 | 66.46% | 0 | 0% | 44.54 | 30.76 | 69.06% | 0 | 0%
GNA_082261114_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1114 | 82261114 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082261115_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1115 | 82261115 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082261116_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1116 | 82261116 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082261117_Capacity | South Bay and Central Coast | San Jose | SAN JOSE B 1117 | 82261117 | Feeder | None | None | None | 82.56% | 0 | 0% | 12.44 | 10.27 | 82.56% | 0 | 0% | 12.44 | 10.24 | 82.32% | 0 | 0% | 12.44 | 10.22 | 82.15% | 0 | 0% | 12.44 | 10.21 | 82.07% | 0 | 0% | 12.44 | 10.21 | 82.07% | 0 | 0%
GNA_0837001_Capacity | South Bay and Central Coast | San Jose | STONE BANK 1 | 837001 | Bank | None | None | None | 60.16% | 0 | 0% | 44.6 | 26.18 | 58.7% | 0 | 0% | 44.6 | 26.43 | 59.26% | 0 | 0% | 44.6 | 26.41 | 59.22% | 0 | 0% | 44.6 | 26.63 | 59.71% | 0 | 0% | 44.6 | 26.83 | 60.16% | 0 | 0%
GNA_083701101_Capacity | South Bay and Central Coast | San Jose | STONE 1101 | 83701101 | Feeder | None | None | None | 87.38% | 0 | 0% | 12.44 | 10.87 | 87.38% | 0 | 0% | 12.44 | 10.78 | 86.66% | 0 | 0% | 12.44 | 10.69 | 85.93% | 0 | 0% | 12.44 | 10.77 | 86.58% | 0 | 0% | 12.44 | 10.87 | 87.38% | 0 | 0%
GNA_083701104_Capacity | South Bay and Central Coast | San Jose | STONE 1104 | 83701104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083701105_Capacity | South Bay and Central Coast | San Jose | STONE 1105 | 83701105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0837002_Capacity | South Bay and Central Coast | San Jose | STONE BANK 2 | 837002 | Bank | None | None | None | 86.59% | 0 | 0% | 44.6 | 36.74 | 82.38% | 0 | 0% | 44.6 | 38.02 | 85.25% | 0 | 0% | 44.6 | 38.53 | 86.39% | 0 | 0% | 44.6 | 38.53 | 86.39% | 0 | 0% | 44.6 | 38.62 | 86.59% | 0 | 0%
GNA_083701107_Capacity | South Bay and Central Coast | San Jose | STONE 1107 | 83701107 | Feeder | None | None | None | 76.77% | 0 | 0% | 12.83 | 9.42 | 73.42% | 0 | 0% | 12.83 | 9.66 | 75.29% | 0 | 0% | 12.83 | 9.71 | 75.68% | 0 | 0% | 12.83 | 9.77 | 76.15% | 0 | 0% | 12.83 | 9.85 | 76.77% | 0 | 0%
GNA_083701108_Capacity | South Bay and Central Coast | San Jose | STONE 1108 | 83701108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083701109_Capacity | South Bay and Central Coast | San Jose | STONE 1109 | 83701109 | Feeder | None | None | None | 87.86% | 0 | 0% | 12.44 | 10.79 | 86.74% | 0 | 0% | 12.44 | 10.77 | 86.58% | 0 | 0% | 12.44 | 10.78 | 86.66% | 0 | 0% | 12.44 | 10.84 | 87.14% | 0 | 0% | 12.44 | 10.93 | 87.86% | 0 | 0%
GNA_083701110_Capacity | South Bay and Central Coast | San Jose | STONE 1110 | 83701110 | Feeder | None | None | None | 84.8% | 0 | 0% | 12.83 | 10.61 | 82.7% | 0 | 0% | 12.83 | 10.88 | 84.8% | 0 | 0% | 12.83 | 10.78 | 84.02% | 0 | 0% | 12.83 | 10.75 | 83.79% | 0 | 0% | 12.83 | 10.78 | 84.02% | 0 | 0%
GNA_0822501_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A BANK 1 | 822501 | Bank | None | None | None | 22.88% | 0 | 0% | 19.8 | 3.99 | 20.15% | 0 | 0% | 19.8 | 4.1 | 20.71% | 0 | 0% | 19.8 | 4.22 | 21.31% | 0 | 0% | 19.8 | 4.37 | 22.07% | 0 | 0% | 19.8 | 4.53 | 22.88% | 0 | 0%
GNA_082250403_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A 0403 | 82250403 | Feeder | None | None | None | 63.11% | 0 | 0% | 3.28 | 2.01 | 61.28% | 0 | 0% | 3.28 | 2.02 | 61.59% | 0 | 0% | 3.28 | 2.02 | 61.59% | 0 | 0% | 3.28 | 2.03 | 61.89% | 0 | 0% | 3.28 | 2.07 | 63.11% | 0 | 0%
GNA_082250404_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A 0404 | 82250404 | Feeder | None | None | None | 25.96% | 0 | 0% | 2.35 | 0.59 | 25.11% | 0 | 0% | 2.35 | 0.59 | 25.11% | 0 | 0% | 2.35 | 0.6 | 25.53% | 0 | 0% | 2.35 | 0.61 | 25.96% | 0 | 0% | 2.35 | 0.61 | 25.96% | 0 | 0%
GNA_082250405_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A 0405 | 82250405 | Feeder | None | None | None | 100.4% | 0.01 | 0.4255% | 2.35 | 1.88 | 80% | 0 | 0% | 2.35 | 1.99 | 84.68% | 0 | 0% | 2.35 | 2.11 | 89.79% | 0 | 0% | 2.35 | 2.24 | 95.32% | 0 | 0% | 2.35 | 2.36 | 100.4% | 0.01 | 0.4255%
GNA_0822502_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A BANK 2 | 822502 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082250407_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A 0407 | 82250407 | Feeder | None | None | None | 85.96% | 0 | 0% | 2.35 | 2.02 | 85.96% | 0 | 0% | 2.35 | 2.02 | 85.96% | 0 | 0% | 2.35 | 2.01 | 85.53% | 0 | 0% | 2.35 | 2 | 85.11% | 0 | 0% | 2.35 | 1.99 | 84.68% | 0 | 0%
GNA_082250408_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A 0408 | 82250408 | Feeder | Demand Growth | Capacity | 2023 | 111.1% | 0.26 | 11.06% | 2.35 | 2.61 | 111.1% | 0.26 | 11.06% | 2.35 | 2.6 | 110.6% | 0.25 | 10.64% | 2.35 | 2.6 | 110.6% | 0.25 | 10.64% | 2.35 | 2.6 | 110.6% | 0.25 | 10.64% | 2.35 | 2.61 | 111.1% | 0.26 | 11.06%
GNA_082250410_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A 0410 | 82250410 | Feeder | Demand Growth | Capacity | 2023 | 118.3% | 0.43 | 18.3% | 2.35 | 2.65 | 112.8% | 0.3 | 12.77% | 2.35 | 2.66 | 113.2% | 0.31 | 13.19% | 2.35 | 2.68 | 114% | 0.33 | 14.04% | 2.35 | 2.71 | 115.3% | 0.36 | 15.32% | 2.35 | 2.78 | 118.3% | 0.43 | 18.3%
GNA_0822504_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A BANK 4 | 822504 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082251113_Capacity | South Bay and Central Coast | San Jose | SAN JOSE A 1113 | 82251113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0821902_Capacity | South Bay and Central Coast | San Jose | MABURY BANK 2 | 821902 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082191103_Capacity | South Bay and Central Coast | San Jose | MABURY 1103 | 82191103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082191104_Capacity | South Bay and Central Coast | San Jose | MABURY 1104 | 82191104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082191105_Capacity | South Bay and Central Coast | San Jose | MABURY 1105 | 82191105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082191106_Capacity | South Bay and Central Coast | San Jose | MABURY 1106 | 82191106 | Feeder | None | None | None | 98.79% | 0 | 0% | 12.44 | 11.96 | 96.14% | 0 | 0% | 12.44 | 11.89 | 95.58% | 0 | 0% | 12.44 | 11.94 | 95.98% | 0 | 0% | 12.44 | 12.08 | 97.11% | 0 | 0% | 12.44 | 12.29 | 98.79% | 0 | 0%
GNA_0835301_Capacity | South Bay and Central Coast | San Jose | MC KEE BANK 1 | 835301 | Bank | None | None | None | 90.27% | 0 | 0% | 29.7 | 25.67 | 86.43% | 0 | 0% | 29.7 | 26.62 | 89.63% | 0 | 0% | 29.7 | 26.55 | 89.39% | 0 | 0% | 29.7 | 26.64 | 89.7% | 0 | 0% | 29.7 | 26.81 | 90.27% | 0 | 0%
GNA_083531103_Capacity | South Bay and Central Coast | San Jose | MC KEE 1103 | 83531103 | Feeder | Demand Growth | Capacity | 2023 | 114.3% | 1.65 | 14.26% | 11.57 | 11.87 | 102.6% | 0.3 | 2.593% | 11.57 | 12.9 | 111.5% | 1.33 | 11.5% | 11.57 | 12.94 | 111.8% | 1.37 | 11.84% | 11.57 | 13.07 | 113% | 1.5 | 12.96% | 11.57 | 13.22 | 114.3% | 1.65 | 14.26%
GNA_083531104_Capacity | South Bay and Central Coast | San Jose | MC KEE 1104 | 83531104 | Feeder | None | None | None | 59.55% | 0 | 0% | 11.57 | 6.89 | 59.55% | 0 | 0% | 11.57 | 6.83 | 59.03% | 0 | 0% | 11.57 | 6.78 | 58.6% | 0 | 0% | 11.57 | 6.77 | 58.51% | 0 | 0% | 11.57 | 6.79 | 58.69% | 0 | 0%
GNA_083531105_Capacity | South Bay and Central Coast | San Jose | MC KEE 1105 | 83531105 | Feeder | None | None | None | 88.33% | 0 | 0% | 11.65 | 10.29 | 88.33% | 0 | 0% | 11.65 | 10.22 | 87.73% | 0 | 0% | 11.65 | 10.17 | 87.3% | 0 | 0% | 11.65 | 10.13 | 86.95% | 0 | 0% | 11.65 | 10.12 | 86.87% | 0 | 0%
GNA_0835302_Capacity | South Bay and Central Coast | San Jose | MC KEE BANK 2 | 835302 | Bank | None | None | None | 93.77% | 0 | 0% | 44.6 | 40.01 | 89.71% | 0 | 0% | 44.6 | 41.22 | 92.42% | 0 | 0% | 44.6 | 41.21 | 92.4% | 0 | 0% | 44.6 | 41.42 | 92.87% | 0 | 0% | 44.6 | 41.82 | 93.77% | 0 | 0%
GNA_083531106_Capacity | South Bay and Central Coast | San Jose | MC KEE 1106 | 83531106 | Feeder | None | None | None | 96.68% | 0 | 0% | 12.06 | 11.62 | 96.35% | 0 | 0% | 12.06 | 11.57 | 95.94% | 0 | 0% | 12.06 | 11.57 | 95.94% | 0 | 0% | 12.06 | 11.62 | 96.35% | 0 | 0% | 12.06 | 11.66 | 96.68% | 0 | 0%
GNA_083531107_Capacity | South Bay and Central Coast | San Jose | MC KEE 1107 | 83531107 | Feeder | Demand Growth | Capacity | 2023 | 123.6% | 2.73 | 23.6% | 11.57 | 14 | 121% | 2.43 | 21% | 11.57 | 13.99 | 120.9% | 2.42 | 20.92% | 11.57 | 14 | 121% | 2.43 | 21% | 11.57 | 14.09 | 121.8% | 2.52 | 21.78% | 11.57 | 14.3 | 123.6% | 2.73 | 23.6%
GNA_083531108_Capacity | South Bay and Central Coast | San Jose | MC KEE 1108 | 83531108 | Feeder | Demand Growth | Capacity | 2023 | 120% | 2.31 | 19.97% | 11.57 | 12.23 | 105.7% | 0.66 | 5.704% | 11.57 | 13.51 | 116.8% | 1.94 | 16.77% | 11.57 | 13.55 | 117.1% | 1.98 | 17.11% | 11.57 | 13.67 | 118.2% | 2.1 | 18.15% | 11.57 | 13.88 | 120% | 2.31 | 19.97%
GNA_0835303_Capacity | South Bay and Central Coast | San Jose | MC KEE BANK 3 | 835303 | Bank | None | None | None | 91.93% | 0 | 0% | 44.6 | 41 | 91.93% | 0 | 0% | 44.6 | 40.9 | 91.7% | 0 | 0% | 44.6 | 40.74 | 91.35% | 0 | 0% | 44.6 | 40.77 | 91.41% | 0 | 0% | 44.6 | 40.95 | 91.82% | 0 | 0%
GNA_083531109_Capacity | South Bay and Central Coast | San Jose | MC KEE 1109 | 83531109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083531110_Capacity | South Bay and Central Coast | San Jose | MC KEE 1110 | 83531110 | Feeder | Demand Growth | Capacity | 2023 | 107.4% | 0.86 | 7.382% | 11.65 | 12.1 | 103.9% | 0.45 | 3.863% | 11.65 | 12.15 | 104.3% | 0.5 | 4.292% | 11.65 | 12.17 | 104.5% | 0.52 | 4.464% | 11.65 | 12.29 | 105.5% | 0.64 | 5.494% | 11.65 | 12.51 | 107.4% | 0.86 | 7.382%
GNA_083531111_Capacity | South Bay and Central Coast | San Jose | MC KEE 1111 | 83531111 | Feeder | None | None | None | 94.45% | 0 | 0% | 12.44 | 11.75 | 94.45% | 0 | 0% | 12.44 | 11.72 | 94.21% | 0 | 0% | 12.44 | 11.66 | 93.73% | 0 | 0% | 12.44 | 11.62 | 93.41% | 0 | 0% | 12.44 | 11.62 | 93.41% | 0 | 0%
GNA_083531112_Capacity | South Bay and Central Coast | San Jose | MC KEE 1112 | 83531112 | Feeder | None | None | None | 88.02% | 0 | 0% | 12.44 | 10.7 | 86.01% | 0 | 0% | 12.44 | 10.77 | 86.58% | 0 | 0% | 12.44 | 10.82 | 86.98% | 0 | 0% | 12.44 | 10.89 | 87.54% | 0 | 0% | 12.44 | 10.95 | 88.02% | 0 | 0%
GNA_0820102_Capacity | South Bay and Central Coast | San Jose | EVERGREEN BANK 2 | 820102 | Bank | None | None | None | 99.84% | 0 | 0% | 44.6 | 43.94 | 98.52% | 0 | 0% | 44.6 | 43.81 | 98.23% | 0 | 0% | 44.6 | 43.84 | 98.3% | 0 | 0% | 44.6 | 44.12 | 98.92% | 0 | 0% | 44.6 | 44.53 | 99.84% | 0 | 0%
GNA_082012101_Capacity | South Bay and Central Coast | San Jose | EVERGREEN 2101 | 82012101 | Feeder | None | None | None | 64.81% | 0 | 0% | 22.22 | 14.4 | 64.81% | 0 | 0% | 22.22 | 14.22 | 64% | 0 | 0% | 22.22 | 14.08 | 63.37% | 0 | 0% | 22.22 | 14.05 | 63.23% | 0 | 0% | 22.22 | 14.06 | 63.28% | 0 | 0%
GNA_082012102_Capacity | South Bay and Central Coast | San Jose | EVERGREEN 2102 | 82012102 | Feeder | None | None | None | 89.51% | 0 | 0% | 19.26 | 16.95 | 88.01% | 0 | 0% | 19.26 | 17.03 | 88.42% | 0 | 0% | 19.26 | 17.08 | 88.68% | 0 | 0% | 19.26 | 17.15 | 89.04% | 0 | 0% | 19.26 | 17.24 | 89.51% | 0 | 0%
GNA_082012103_Capacity | South Bay and Central Coast | San Jose | EVERGREEN 2103 | 82012103 | Feeder | None | None | None | 78.61% | 0 | 0% | 19.26 | 14.91 | 77.41% | 0 | 0% | 19.26 | 14.88 | 77.26% | 0 | 0% | 19.26 | 14.85 | 77.1% | 0 | 0% | 19.26 | 14.94 | 77.57% | 0 | 0% | 19.26 | 15.14 | 78.61% | 0 | 0%
GNA_0820103_Capacity | South Bay and Central Coast | San Jose | EVERGREEN BANK 3 | 820103 | Bank | None | None | None | 68.61% | 0 | 0% | 44.6 | 29.37 | 65.85% | 0 | 0% | 44.6 | 29.54 | 66.23% | 0 | 0% | 44.6 | 29.82 | 66.86% | 0 | 0% | 44.6 | 30.2 | 67.71% | 0 | 0% | 44.6 | 30.6 | 68.61% | 0 | 0%
GNA_082012104_Capacity | South Bay and Central Coast | San Jose | EVERGREEN 2104 | 82012104 | Feeder | None | None | None | 67.79% | 0 | 0% | 21.11 | 13.75 | 65.14% | 0 | 0% | 21.11 | 13.84 | 65.56% | 0 | 0% | 21.11 | 13.98 | 66.22% | 0 | 0% | 21.11 | 14.14 | 66.98% | 0 | 0% | 21.11 | 14.31 | 67.79% | 0 | 0%
GNA_082012105_Capacity | South Bay and Central Coast | San Jose | EVERGREEN 2105 | 82012105 | Feeder | None | None | None | 99.48% | 0 | 0% | 21.11 | 20.34 | 96.35% | 0 | 0% | 21.11 | 20.41 | 96.68% | 0 | 0% | 21.11 | 20.54 | 97.3% | 0 | 0% | 21.11 | 20.77 | 98.39% | 0 | 0% | 21.11 | 21 | 99.48% | 0 | 0%
GNA_0833901_Capacity | South Bay and Central Coast | San Jose | SWIFT BANK 1 | 833901 | Bank | None | None | None | 86.01% | 0 | 0% | 44.52 | 38 | 85.35% | 0 | 0% | 44.52 | 37.99 | 85.33% | 0 | 0% | 44.52 | 38.03 | 85.42% | 0 | 0% | 44.52 | 38.13 | 85.65% | 0 | 0% | 44.52 | 38.29 | 86.01% | 0 | 0%
GNA_083392102_Capacity | South Bay and Central Coast | San Jose | SWIFT 2102 | 83392102 | Feeder | None | None | None | 66.37% | 0 | 0% | 20.04 | 12.87 | 64.22% | 0 | 0% | 20.04 | 12.92 | 64.47% | 0 | 0% | 20.04 | 13 | 64.87% | 0 | 0% | 20.04 | 13.12 | 65.47% | 0 | 0% | 20.04 | 13.3 | 66.37% | 0 | 0%
GNA_083392106_Capacity | South Bay and Central Coast | San Jose | SWIFT 2106 | 83392106 | Feeder | None | None | None | 88.72% | 0 | 0% | 20.04 | 17.78 | 88.72% | 0 | 0% | 20.04 | 17.74 | 88.52% | 0 | 0% | 20.04 | 17.73 | 88.47% | 0 | 0% | 20.04 | 17.74 | 88.52% | 0 | 0% | 20.04 | 17.78 | 88.72% | 0 | 0%
GNA_0833902_Capacity | South Bay and Central Coast | San Jose | SWIFT BANK 2 | 833902 | Bank | None | None | None | 90.59% | 0 | 0% | 44.52 | 38.58 | 86.66% | 0 | 0% | 44.52 | 38.82 | 87.2% | 0 | 0% | 44.52 | 39.06 | 87.74% | 0 | 0% | 44.52 | 39.66 | 89.08% | 0 | 0% | 44.52 | 40.33 | 90.59% | 0 | 0%
GNA_083392107_Capacity | South Bay and Central Coast | San Jose | SWIFT 2107 | 83392107 | Feeder | None | None | None | 96.76% | 0 | 0% | 20.04 | 18.87 | 94.16% | 0 | 0% | 20.04 | 18.92 | 94.41% | 0 | 0% | 20.04 | 18.97 | 94.66% | 0 | 0% | 20.04 | 19.17 | 95.66% | 0 | 0% | 20.04 | 19.39 | 96.76% | 0 | 0%
GNA_083392108_Capacity | South Bay and Central Coast | San Jose | SWIFT 2108 | 83392108 | Feeder | Demand Growth | Capacity | 2023 | 113.6% | 2.72 | 13.57% | 20.04 | 21.91 | 109.3% | 1.87 | 9.331% | 20.04 | 21.97 | 109.6% | 1.93 | 9.631% | 20.04 | 22.07 | 110.1% | 2.03 | 10.13% | 20.04 | 22.38 | 111.7% | 2.34 | 11.68% | 20.04 | 22.76 | 113.6% | 2.72 | 13.57%
GNA_0833903_Capacity | South Bay and Central Coast | San Jose | SWIFT BANK 3 | 833903 | Bank | None | None | None | 100.1% | 0.04 | 0.08985% | 44.52 | 44.37 | 99.66% | 0 | 0% | 44.52 | 44.31 | 99.53% | 0 | 0% | 44.52 | 44.21 | 99.3% | 0 | 0% | 44.52 | 44.27 | 99.44% | 0 | 0% | 44.52 | 44.56 | 100.1% | 0.04 | 0.08985%
GNA_083392109_Capacity | South Bay and Central Coast | San Jose | SWIFT 2109 | 83392109 | Feeder | None | None | None | 74.15% | 0 | 0% | 20.04 | 14.85 | 74.1% | 0 | 0% | 20.04 | 14.75 | 73.6% | 0 | 0% | 20.04 | 14.67 | 73.2% | 0 | 0% | 20.04 | 14.7 | 73.35% | 0 | 0% | 20.04 | 14.86 | 74.15% | 0 | 0%
GNA_083392110_Capacity | South Bay and Central Coast | San Jose | SWIFT 2110 | 83392110 | Feeder | None | None | None | 64.07% | 0 | 0% | 20.04 | 12.51 | 62.43% | 0 | 0% | 20.04 | 12.56 | 62.67% | 0 | 0% | 20.04 | 12.61 | 62.92% | 0 | 0% | 20.04 | 12.7 | 63.37% | 0 | 0% | 20.04 | 12.84 | 64.07% | 0 | 0%
GNA_083392111_Capacity | South Bay and Central Coast | San Jose | SWIFT 2111 | 83392111 | Feeder | Demand Growth | Capacity | 2023 | 102.5% | 0.5 | 2.495% | 20.04 | 20.54 | 102.5% | 0.5 | 2.495% | 20.04 | 20.27 | 101.1% | 0.23 | 1.148% | 20.04 | 20.01 | 99.85% | 0 | 0% | 20.04 | 19.75 | 98.55% | 0 | 0% | 20.04 | 19.6 | 97.8% | 0 | 0%
GNA_0828301_Capacity | South Bay and Central Coast | San Jose | MILPITAS BANK 1 | 828301 | Bank | None | None | None | 76.26% | 0 | 0% | 44.6 | 33.94 | 76.1% | 0 | 0% | 44.6 | 33.9 | 76.01% | 0 | 0% | 44.6 | 33.89 | 75.99% | 0 | 0% | 44.6 | 33.96 | 76.14% | 0 | 0% | 44.6 | 34.01 | 76.26% | 0 | 0%
GNA_082831101_Capacity | South Bay and Central Coast | San Jose | MILPITAS 1101 | 82831101 | Feeder | None | None | None | 89.02% | 0 | 0% | 11.57 | 9.93 | 85.83% | 0 | 0% | 11.57 | 9.96 | 86.08% | 0 | 0% | 11.57 | 10.01 | 86.52% | 0 | 0% | 11.57 | 10.14 | 87.64% | 0 | 0% | 11.57 | 10.3 | 89.02% | 0 | 0%
GNA_082831103_Capacity | South Bay and Central Coast | San Jose | MILPITAS 1103 | 82831103 | Feeder | None | None | None | 83.06% | 0 | 0% | 11.57 | 9.61 | 83.06% | 0 | 0% | 11.57 | 9.57 | 82.71% | 0 | 0% | 11.57 | 9.54 | 82.45% | 0 | 0% | 11.57 | 9.54 | 82.45% | 0 | 0% | 11.57 | 9.49 | 82.02% | 0 | 0%
GNA_082831105_Capacity | South Bay and Central Coast | San Jose | MILPITAS 1105 | 82831105 | Feeder | None | None | None | 92.65% | 0 | 0% | 11.57 | 10.72 | 92.65% | 0 | 0% | 11.57 | 10.68 | 92.31% | 0 | 0% | 11.57 | 10.62 | 91.79% | 0 | 0% | 11.57 | 10.55 | 91.18% | 0 | 0% | 11.57 | 10.5 | 90.75% | 0 | 0%
GNA_082831104_Capacity | South Bay and Central Coast | San Jose | MILPITAS 1104 (21 KV FEEDER) | 82831104 | Feeder | None | None | None | 25.52% | 0 | 0% | 19.59 | 4.62 | 23.58% | 0 | 0% | 19.59 | 4.72 | 24.09% | 0 | 0% | 19.59 | 4.81 | 24.55% | 0 | 0% | 19.59 | 4.91 | 25.06% | 0 | 0% | 19.59 | 5 | 25.52% | 0 | 0%
GNA_0828302_Capacity | South Bay and Central Coast | San Jose | MILPITAS BANK 2 | 828302 | Bank | None | None | None | 97.61% | 0 | 0% | 29.7 | 28.78 | 96.9% | 0 | 0% | 29.7 | 28.78 | 96.9% | 0 | 0% | 29.7 | 28.77 | 96.87% | 0 | 0% | 29.7 | 28.87 | 97.21% | 0 | 0% | 29.7 | 28.99 | 97.61% | 0 | 0%
GNA_082831106_Capacity | South Bay and Central Coast | San Jose | MILPITAS 1106 | 82831106 | Feeder | None | None | None | 90.06% | 0 | 0% | 11.57 | 10.42 | 90.06% | 0 | 0% | 11.57 | 10.41 | 89.97% | 0 | 0% | 11.57 | 10.38 | 89.71% | 0 | 0% | 11.57 | 10.38 | 89.71% | 0 | 0% | 11.57 | 10.39 | 89.8% | 0 | 0%
GNA_082831108_Capacity | South Bay and Central Coast | San Jose | MILPITAS 1108 | 82831108 | Feeder | None | None | None | 95.16% | 0 | 0% | 11.57 | 10.68 | 92.31% | 0 | 0% | 11.57 | 10.73 | 92.74% | 0 | 0% | 11.57 | 10.78 | 93.17% | 0 | 0% | 11.57 | 10.88 | 94.04% | 0 | 0% | 11.57 | 11.01 | 95.16% | 0 | 0%
GNA_082831109_Capacity | South Bay and Central Coast | San Jose | MILPITAS 1109 | 82831109 | Feeder | None | None | None | 82.71% | 0 | 0% | 11.57 | 9.57 | 82.71% | 0 | 0% | 11.57 | 9.54 | 82.45% | 0 | 0% | 11.57 | 9.52 | 82.28% | 0 | 0% | 11.57 | 9.5 | 82.11% | 0 | 0% | 11.57 | 9.48 | 81.94% | 0 | 0%
GNA_0147201_Capacity | South Bay and Central Coast | San Jose | DIXON LANDING BANK 1 | 147201 | Bank | None | None | None | 87.28% | 0 | 0% | 44.1 | 34.57 | 78.39% | 0 | 0% | 44.1 | 37.72 | 85.53% | 0 | 0% | 44.1 | 38.27 | 86.78% | 0 | 0% | 44.1 | 38.37 | 87.01% | 0 | 0% | 44.1 | 38.49 | 87.28% | 0 | 0%
GNA_014722101_Capacity | South Bay and Central Coast | San Jose | DIXON LANDING 2101 | 14722101 | Feeder | None | None | None | 56.09% | 0 | 0% | 20.04 | 11.24 | 56.09% | 0 | 0% | 20.04 | 11.2 | 55.89% | 0 | 0% | 20.04 | 11.17 | 55.74% | 0 | 0% | 20.04 | 11.16 | 55.69% | 0 | 0% | 20.04 | 11.13 | 55.54% | 0 | 0%
GNA_014722102_Capacity | South Bay and Central Coast | San Jose | DIXON LANDING 2102 | 14722102 | Feeder | None | None | None | 32.98% | 0 | 0% | 20.04 | 5.65 | 28.19% | 0 | 0% | 20.04 | 6.61 | 32.98% | 0 | 0% | 20.04 | 6.6 | 32.93% | 0 | 0% | 20.04 | 6.58 | 32.83% | 0 | 0% | 20.04 | 6.59 | 32.88% | 0 | 0%
GNA_014722103_Capacity | South Bay and Central Coast | San Jose | DIXON LANDING 2103 | 14722103 | Feeder | Demand Growth | Capacity | 2024 | 114.3% | 2.86 | 14.27% | 20.04 | 19.36 | 96.61% | 0 | 0% | 20.04 | 22.21 | 110.8% | 2.17 | 10.83% | 20.04 | 22.76 | 113.6% | 2.72 | 13.57% | 20.04 | 22.83 | 113.9% | 2.79 | 13.92% | 20.04 | 22.9 | 114.3% | 2.86 | 14.27%
GNA_0828303_Capacity | South Bay and Central Coast | San Jose | MILPITAS BANK 3 | 828303 | Bank | Demand Growth | Capacity | 2024 | 110.7% | 4.76 | 10.67% | 44.6 | 37.06 | 83.09% | 0 | 0% | 44.6 | 48.59 | 108.9% | 3.99 | 8.946% | 44.6 | 48.66 | 109.1% | 4.06 | 9.103% | 44.6 | 48.93 | 109.7% | 4.33 | 9.709% | 44.6 | 49.36 | 110.7% | 4.76 | 10.67%
GNA_082832110_Capacity | South Bay and Central Coast | San Jose | MILPITAS 2110 (12 KV FEEDER) | 82832110 | Feeder | None | None | None | 96.13% | 0 | 0% | 12.67 | 11.71 | 92.42% | 0 | 0% | 12.67 | 11.74 | 92.66% | 0 | 0% | 12.67 | 11.76 | 92.82% | 0 | 0% | 12.67 | 11.92 | 94.08% | 0 | 0% | 12.67 | 12.18 | 96.13% | 0 | 0%
GNA_082832111_Capacity | South Bay and Central Coast | San Jose | MILPITAS 2111 | 82832111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082832112_Capacity | South Bay and Central Coast | San Jose | MILPITAS 2112 | 82832112 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0828306_Capacity | South Bay and Central Coast | San Jose | MILPITAS BANK 6 | 828306 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082832113_Capacity | South Bay and Central Coast | San Jose | MILPITAS 2113 | 82832113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082832114_Capacity | South Bay and Central Coast | San Jose | MILPITAS 2114 | 82832114 | Feeder | None | None | None | 65.92% | 0 | 0% | 20.04 | 12.93 | 64.52% | 0 | 0% | 20.04 | 12.99 | 64.82% | 0 | 0% | 20.04 | 13.06 | 65.17% | 0 | 0% | 20.04 | 13.12 | 65.47% | 0 | 0% | 20.04 | 13.21 | 65.92% | 0 | 0%
GNA_082832115_Capacity | South Bay and Central Coast | San Jose | MILPITAS 2115 | 82832115 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0838901_Capacity | South Bay and Central Coast | San Jose | MONTAGUE BANK 1 | 838901 | Bank | None | None | None | 90.27% | 0 | 0% | 44.6 | 38.48 | 86.28% | 0 | 0% | 44.6 | 40.09 | 89.89% | 0 | 0% | 44.6 | 40.14 | 90% | 0 | 0% | 44.6 | 40.18 | 90.09% | 0 | 0% | 44.6 | 40.26 | 90.27% | 0 | 0%
GNA_083892101_Capacity | South Bay and Central Coast | San Jose | MONTAGUE 2101 | 83892101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083892102_Capacity | South Bay and Central Coast | San Jose | MONTAGUE 2102 | 83892102 | Feeder | None | None | None | 64.87% | 0 | 0% | 20.04 | 13 | 64.87% | 0 | 0% | 20.04 | 12.95 | 64.62% | 0 | 0% | 20.04 | 12.92 | 64.47% | 0 | 0% | 20.04 | 12.89 | 64.32% | 0 | 0% | 20.04 | 12.91 | 64.42% | 0 | 0%
GNA_083892103_Capacity | South Bay and Central Coast | San Jose | MONTAGUE 2103 | 83892103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0838902_Capacity | South Bay and Central Coast | San Jose | MONTAGUE BANK 2 | 838902 | Bank | None | None | None | 86.26% | 0 | 0% | 44.6 | 35.12 | 78.74% | 0 | 0% | 44.6 | 35.23 | 78.99% | 0 | 0% | 44.6 | 35.35 | 79.26% | 0 | 0% | 44.6 | 38.24 | 85.74% | 0 | 0% | 44.6 | 38.47 | 86.26% | 0 | 0%
GNA_083892104_Capacity | South Bay and Central Coast | San Jose | MONTAGUE 2104 | 83892104 | Feeder | None | None | None | 89.77% | 0 | 0% | 19.15 | 16.81 | 87.78% | 0 | 0% | 19.15 | 16.87 | 88.09% | 0 | 0% | 19.15 | 16.92 | 88.36% | 0 | 0% | 19.15 | 17.04 | 88.98% | 0 | 0% | 19.15 | 17.19 | 89.77% | 0 | 0%
GNA_083892105_Capacity | South Bay and Central Coast | San Jose | MONTAGUE 2105 | 83892105 | Feeder | None | None | None | 70.51% | 0 | 0% | 20.04 | 11.08 | 55.29% | 0 | 0% | 20.04 | 11.16 | 55.69% | 0 | 0% | 20.04 | 11.25 | 56.14% | 0 | 0% | 20.04 | 14.04 | 70.06% | 0 | 0% | 20.04 | 14.13 | 70.51% | 0 | 0%
GNA_083892106_Capacity | South Bay and Central Coast | San Jose | MONTAGUE 2106 | 83892106 | Feeder | None | None | None | 37.43% | 0 | 0% | 20.04 | 7.5 | 37.43% | 0 | 0% | 20.04 | 7.47 | 37.28% | 0 | 0% | 20.04 | 7.43 | 37.08% | 0 | 0% | 20.04 | 7.38 | 36.83% | 0 | 0% | 20.04 | 7.33 | 36.58% | 0 | 0%
GNA_0838903_Capacity | South Bay and Central Coast | San Jose | MONTAGUE BANK 3 | 838903 | Bank | Demand Growth | Capacity | 2024 | 106.1% | 2.72 | 6.099% | 44.6 | 41.29 | 92.58% | 0 | 0% | 44.6 | 45.49 | 102% | 0.89 | 1.996% | 44.6 | 47.32 | 106.1% | 2.72 | 6.099% | 44.6 | 47.32 | 106.1% | 2.72 | 6.099% | 44.6 | 47.32 | 106.1% | 2.72 | 6.099%
GNA_083892107_Capacity | South Bay and Central Coast | San Jose | MONTAGUE 2107 | 83892107 | Feeder | None | None | None | 64.55% | 0 | 0% | 18.7 | 12.07 | 64.55% | 0 | 0% | 18.7 | 12.07 | 64.55% | 0 | 0% | 18.7 | 12.06 | 64.49% | 0 | 0% | 18.7 | 12.06 | 64.49% | 0 | 0% | 18.7 | 12.06 | 64.49% | 0 | 0%
GNA_083892108_Capacity | South Bay and Central Coast | San Jose | MONTAGUE 2108 | 83892108 | Feeder | None | None | None | 52.66% | 0 | 0% | 22.22 | 11.7 | 52.66% | 0 | 0% | 22.22 | 11.69 | 52.61% | 0 | 0% | 22.22 | 11.68 | 52.57% | 0 | 0% | 22.22 | 11.69 | 52.61% | 0 | 0% | 22.22 | 11.7 | 52.66% | 0 | 0%
GNA_083892109_Capacity | South Bay and Central Coast | San Jose | MONTAGUE 2109 | 83892109 | Feeder | None | None | None | 85.92% | 0 | 0% | 17.33 | 14.89 | 85.92% | 0 | 0% | 17.33 | 14.86 | 85.75% | 0 | 0% | 17.33 | 14.84 | 85.63% | 0 | 0% | 17.33 | 14.82 | 85.52% | 0 | 0% | 17.33 | 14.82 | 85.52% | 0 | 0%
GNA_083892110_Capacity | South Bay and Central Coast | San Jose | MONTAGUE 2110 | 83892110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0831801_Capacity | South Bay and Central Coast | San Jose | LLAGAS BANK 1 | 831801 | Bank | None | None | None | 84.61% | 0 | 0% | 44.5 | 32.51 | 73.06% | 0 | 0% | 44.5 | 36.06 | 81.03% | 0 | 0% | 44.5 | 37.32 | 83.87% | 0 | 0% | 44.5 | 37.49 | 84.25% | 0 | 0% | 44.5 | 37.65 | 84.61% | 0 | 0%
GNA_083182101_Capacity | South Bay and Central Coast | San Jose | LLAGAS 2101 | 83182101 | Feeder | None | None | None | 95.36% | 0 | 0% | 21.11 | 17.62 | 83.47% | 0 | 0% | 21.11 | 17.69 | 83.8% | 0 | 0% | 21.11 | 19.88 | 94.17% | 0 | 0% | 21.11 | 20 | 94.74% | 0 | 0% | 21.11 | 20.13 | 95.36% | 0 | 0%
GNA_083182102_Capacity | South Bay and Central Coast | San Jose | LLAGAS 2102 | 83182102 | Feeder | None | None | None | 72.38% | 0 | 0% | 21.11 | 15.28 | 72.38% | 0 | 0% | 21.11 | 15.24 | 72.19% | 0 | 0% | 21.11 | 14.29 | 67.69% | 0 | 0% | 21.11 | 14.31 | 67.79% | 0 | 0% | 21.11 | 14.33 | 67.88% | 0 | 0%
GNA_0831802_Capacity | South Bay and Central Coast | San Jose | LLAGAS BANK 2 | 831802 | Bank | None | None | None | 96.26% | 0 | 0% | 44.6 | 27.46 | 61.57% | 0 | 0% | 44.6 | 42.93 | 96.26% | 0 | 0% | 44.6 | 26.8 | 60.09% | 0 | 0% | 44.6 | 26.9 | 60.31% | 0 | 0% | 44.6 | 26.99 | 60.52% | 0 | 0%
GNA_083182103_Capacity | South Bay and Central Coast | San Jose | LLAGAS 2103 | 83182103 | Feeder | Demand Growth | Capacity | 2023 | 125.5% | 4.61 | 25.46% | 18.11 | 22.67 | 125.2% | 4.56 | 25.18% | 18.11 | 22.72 | 125.5% | 4.61 | 25.46% | 18.11 | 21.6 | 119.3% | 3.49 | 19.27% | 18.11 | 21.69 | 119.8% | 3.58 | 19.77% | 18.11 | 21.81 | 120.4% | 3.7 | 20.43%
GNA_083182104_Capacity | South Bay and Central Coast | San Jose | LLAGAS 2104 | 83182104 | Feeder | None | None | None | 27.29% | 0 | 0% | 17.33 | 4.73 | 27.29% | 0 | 0% | 17.33 | 4.72 | 27.24% | 0 | 0% | 17.33 | 4.71 | 27.18% | 0 | 0% | 17.33 | 4.71 | 27.18% | 0 | 0% | 17.33 | 4.69 | 27.06% | 0 | 0%
GNA_083182109_Capacity | South Bay and Central Coast | San Jose | LLAGAS 2109 (TEMP SERVICE) | 83182109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0831803_Capacity | South Bay and Central Coast | San Jose | LLAGAS BANK 3 | 831803 | Bank | Demand Growth | Capacity | 2023 | 139.6% | 17.67 | 39.62% | 49.06 | 51.43 | 104.8% | 2.37 | 4.831% | 49.06 | 49.54 | 101% | 0.48 | 0.9784% | 49.06 | 50.21 | 102.3% | 1.15 | 2.344% | 44.6 | 59.51 | 133.4% | 14.91 | 33.43% | 44.6 | 62.27 | 139.6% | 17.67 | 39.62%
GNA_083182105_Capacity | South Bay and Central Coast | San Jose | LLAGAS 2105 | 83182105 | Feeder | None | None | None | 99.95% | 0 | 0% | 21.11 | 20.59 | 97.54% | 0 | 0% | 21.11 | 20.66 | 97.87% | 0 | 0% | 21.11 | 21.03 | 99.62% | 0 | 0% | 21.11 | 21 | 99.48% | 0 | 0% | 21.11 | 21.1 | 99.95% | 0 | 0%
GNA_083182106_Capacity | South Bay and Central Coast | San Jose | LLAGAS 2106 | 83182106 | Feeder | None | None | None | 98.6% | 0 | 0% | 22.22 | 19.67 | 88.52% | 0 | 0% | 22.22 | 21.25 | 95.63% | 0 | 0% | 22.22 | 21.35 | 96.08% | 0 | 0% | 22.22 | 21.81 | 98.15% | 0 | 0% | 22.22 | 21.91 | 98.6% | 0 | 0%
GNA_083182107_Capacity | South Bay and Central Coast | San Jose | LLAGAS 2107 | 83182107 | Feeder | Demand Growth | Capacity | 2026 | 158% | 12.25 | 58.03% | 21.11 | 20.28 | 96.07% | 0 | 0% | 21.11 | 20.35 | 96.4% | 0 | 0% | 21.11 | 20.43 | 96.78% | 0 | 0% | 21.11 | 30.25 | 143.3% | 9.14 | 43.3% | 21.11 | 33.36 | 158% | 12.25 | 58.03%
GNA_0832401_Capacity | South Bay and Central Coast | San Jose | MORGAN HILL BANK 1 | 832401 | Bank | None | None | None | 78.05% | 0 | 0% | 44.6 | 34.06 | 76.37% | 0 | 0% | 44.6 | 33.89 | 75.99% | 0 | 0% | 44.6 | 34.81 | 78.05% | 0 | 0% | 44.6 | 34.52 | 77.4% | 0 | 0% | 44.6 | 34.07 | 76.39% | 0 | 0%
GNA_083242104_Capacity | South Bay and Central Coast | San Jose | MORGAN HILL 2104 | 83242104 | Feeder | None | None | None | 91.03% | 0 | 0% | 21.74 | 18.83 | 86.61% | 0 | 0% | 21.74 | 18.75 | 86.25% | 0 | 0% | 21.74 | 19.79 | 91.03% | 0 | 0% | 21.74 | 19.64 | 90.34% | 0 | 0% | 21.74 | 19.44 | 89.42% | 0 | 0%
GNA_083242105_Capacity | South Bay and Central Coast | San Jose | MORGAN HILL 2105 | 83242105 | Feeder | None | None | None | 77.23% | 0 | 0% | 22.22 | 17.16 | 77.23% | 0 | 0% | 22.22 | 17.08 | 76.87% | 0 | 0% | 22.22 | 16.99 | 76.46% | 0 | 0% | 22.22 | 16.87 | 75.92% | 0 | 0% | 22.22 | 16.66 | 74.98% | 0 | 0%
GNA_0832402_Capacity | South Bay and Central Coast | San Jose | MORGAN HILL BANK 2 | 832402 | Bank | Demand Growth | Capacity | 2023 | 134% | 10.09 | 33.97% | 29.7 | 35.79 | 120.5% | 6.09 | 20.51% | 29.7 | 39.21 | 132% | 9.51 | 32.02% | 29.7 | 39.35 | 132.5% | 9.65 | 32.49% | 29.7 | 39.54 | 133.1% | 9.84 | 33.13% | 29.7 | 39.79 | 134% | 10.09 | 33.97%
GNA_083242106_Capacity | South Bay and Central Coast | San Jose | MORGAN HILL 2106 | 83242106 | Feeder | None | None | None | 99.55% | 0 | 0% | 13.22 | 12.72 | 96.22% | 0 | 0% | 13.22 | 12.8 | 96.82% | 0 | 0% | 13.22 | 12.91 | 97.66% | 0 | 0% | 13.22 | 13.02 | 98.49% | 0 | 0% | 13.22 | 13.16 | 99.55% | 0 | 0%
GNA_083242108_Capacity | South Bay and Central Coast | San Jose | MORGAN HILL 2108 | 83242108 | Feeder | Demand Growth | Capacity | 2023 | 133.2% | 6.94 | 33.22% | 20.89 | 24.23 | 116% | 3.34 | 15.99% | 20.89 | 27.59 | 132.1% | 6.7 | 32.07% | 20.89 | 27.65 | 132.4% | 6.76 | 32.36% | 20.89 | 27.72 | 132.7% | 6.83 | 32.7% | 20.89 | 27.83 | 133.2% | 6.94 | 33.22%
GNA_0832403_Capacity | South Bay and Central Coast | San Jose | MORGAN HILL BANK 3 | 832403 | Bank | Demand Growth | Capacity | 2023 | 113% | 5.8 | 13% | 44.6 | 49.52 | 111% | 4.92 | 11.03% | 44.6 | 49.7 | 111.4% | 5.1 | 11.43% | 44.6 | 49.85 | 111.8% | 5.25 | 11.77% | 44.6 | 50.1 | 112.3% | 5.5 | 12.33% | 44.6 | 50.4 | 113% | 5.8 | 13%
GNA_083242109_Capacity | South Bay and Central Coast | San Jose | MORGAN HILL 2109 | 83242109 | Feeder | Demand Growth | Capacity | 2023 | 114.5% | 2.85 | 14.52% | 19.63 | 22.31 | 113.7% | 2.68 | 13.65% | 19.63 | 22.37 | 114% | 2.74 | 13.96% | 19.63 | 22.43 | 114.3% | 2.8 | 14.26% | 19.63 | 22.46 | 114.4% | 2.83 | 14.42% | 19.63 | 22.48 | 114.5% | 2.85 | 14.52%
GNA_083242110_Capacity | South Bay and Central Coast | San Jose | MORGAN HILL 2110 | 83242110 | Feeder | None | None | None | 73.54% | 0 | 0% | 18.63 | 13.33 | 71.55% | 0 | 0% | 18.63 | 13.41 | 71.98% | 0 | 0% | 18.63 | 13.51 | 72.52% | 0 | 0% | 18.63 | 13.59 | 72.95% | 0 | 0% | 18.63 | 13.7 | 73.54% | 0 | 0%
GNA_083242111_Capacity | South Bay and Central Coast | San Jose | MORGAN HILL 2111 | 83242111 | Feeder | None | None | None | 86.86% | 0 | 0% | 18.11 | 15.48 | 85.48% | 0 | 0% | 18.11 | 15.54 | 85.81% | 0 | 0% | 18.11 | 15.59 | 86.09% | 0 | 0% | 18.11 | 15.65 | 86.42% | 0 | 0% | 18.11 | 15.73 | 86.86% | 0 | 0%
GNA_0838001_Capacity | South Bay and Central Coast | San Jose | TRIMBLE BANK 1 | 838001 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083801101_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 1101 | 83801101 | Feeder | None | None | None | 89.37% | 0 | 0% | 11.57 | 10.34 | 89.37% | 0 | 0% | 11.57 | 10.34 | 89.37% | 0 | 0% | 11.57 | 10.34 | 89.37% | 0 | 0% | 11.57 | 10.33 | 89.28% | 0 | 0% | 11.57 | 10.33 | 89.28% | 0 | 0%
GNA_083801103_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 1103 | 83801103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083801104_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 1104 | 83801104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083801105_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 1105 | 83801105 | Feeder | None | None | None | 49.78% | 0 | 0% | 11.57 | 4.45 | 38.46% | 0 | 0% | 11.57 | 5.75 | 49.7% | 0 | 0% | 11.57 | 5.76 | 49.78% | 0 | 0% | 11.57 | 5.76 | 49.78% | 0 | 0% | 11.57 | 5.75 | 49.7% | 0 | 0%
GNA_083801106_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 1106 | 83801106 | Feeder | None | None | None | 76.15% | 0 | 0% | 11.57 | 8.39 | 72.52% | 0 | 0% | 11.57 | 8.5 | 73.47% | 0 | 0% | 11.57 | 8.6 | 74.33% | 0 | 0% | 11.57 | 8.7 | 75.19% | 0 | 0% | 11.57 | 8.81 | 76.15% | 0 | 0%
GNA_0838002_Capacity | South Bay and Central Coast | San Jose | TRIMBLE BANK 2 | 838002 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083801107_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 1107 | 83801107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083801109_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 1109 | 83801109 | Feeder | None | None | None | 41.49% | 0 | 0% | 11.57 | 4.8 | 41.49% | 0 | 0% | 11.57 | 4.79 | 41.4% | 0 | 0% | 11.57 | 4.78 | 41.31% | 0 | 0% | 11.57 | 4.78 | 41.31% | 0 | 0% | 11.57 | 4.78 | 41.31% | 0 | 0%
GNA_083801110_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 1110 | 83801110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083801111_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 1111 | 83801111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0824602_Capacity | South Bay and Central Coast | San Jose | NORTECH BANK 2 | 824602 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082462107_Capacity | South Bay and Central Coast | San Jose | NORTECH 2107 | 82462107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0824603_Capacity | South Bay and Central Coast | San Jose | NORTECH BANK 3 | 824603 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082462109_Capacity | South Bay and Central Coast | San Jose | NORTECH 2109 | 82462109 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082462110_Capacity | South Bay and Central Coast | San Jose | NORTECH 2110 | 82462110 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082462111_Capacity | South Bay and Central Coast | San Jose | NORTECH 2111 | 82462111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0823401_Capacity | South Bay and Central Coast | San Jose | RIVER OAKS BANK 1 | 823401 | Bank | None | None | None | 91.4% | 0 | 0% | 44.4 | 40.58 | 91.4% | 0 | 0% | 44.4 | 40.57 | 91.37% | 0 | 0% | 44.4 | 40.56 | 91.35% | 0 | 0% | 44.4 | 40.57 | 91.37% | 0 | 0% | 44.4 | 40.56 | 91.35% | 0 | 0%
GNA_082342101_Capacity | South Bay and Central Coast | San Jose | RIVER OAKS 2101 | 82342101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082342102_Capacity | South Bay and Central Coast | San Jose | RIVER OAKS 2102 | 82342102 | Feeder | None | None | None | 84.47% | 0 | 0% | 22.22 | 18.77 | 84.47% | 0 | 0% | 22.22 | 18.77 | 84.47% | 0 | 0% | 22.22 | 18.76 | 84.43% | 0 | 0% | 22.22 | 18.76 | 84.43% | 0 | 0% | 22.22 | 18.75 | 84.38% | 0 | 0%
GNA_0823402_Capacity | South Bay and Central Coast | San Jose | RIVER OAKS BANK 2 | 823402 | Bank | None | None | None | 97.29% | 0 | 0% | 44.6 | 43.39 | 97.29% | 0 | 0% | 44.6 | 43.39 | 97.29% | 0 | 0% | 44.6 | 43.37 | 97.24% | 0 | 0% | 44.6 | 43.35 | 97.2% | 0 | 0% | 44.6 | 43.35 | 97.2% | 0 | 0%
GNA_082342106_Capacity | South Bay and Central Coast | San Jose | RIVER OAKS 2106 | 82342106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082342107_Capacity | South Bay and Central Coast | San Jose | RIVER OAKS 2107 | 82342107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082342108_Capacity | South Bay and Central Coast | San Jose | RIVER OAKS 2108 | 82342108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0838003_Capacity | South Bay and Central Coast | San Jose | TRIMBLE BANK 3 | 838003 | Bank | None | None | None | 96.88% | 0 | 0% | 44.6 | 36.39 | 81.59% | 0 | 0% | 44.6 | 41.89 | 93.92% | 0 | 0% | 44.6 | 43.21 | 96.88% | 0 | 0% | 44.6 | 41.91 | 93.97% | 0 | 0% | 44.6 | 42.04 | 94.26% | 0 | 0%
GNA_083802114_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 2114 | 83802114 | Feeder | None | None | None | 52.1% | 0 | 0% | 20.04 | 6.96 | 34.73% | 0 | 0% | 20.04 | 9.93 | 49.55% | 0 | 0% | 20.04 | 10.1 | 50.4% | 0 | 0% | 20.04 | 10.27 | 51.25% | 0 | 0% | 20.04 | 10.44 | 52.1% | 0 | 0%
GNA_083802115_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 2115 | 83802115 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083802116_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 2116 | 83802116 | Feeder | None | None | None | 87.21% | 0 | 0% | 19.93 | 16.17 | 81.13% | 0 | 0% | 19.93 | 17.38 | 87.21% | 0 | 0% | 19.93 | 17.35 | 87.05% | 0 | 0% | 19.93 | 17.34 | 87% | 0 | 0% | 19.93 | 17.33 | 86.95% | 0 | 0%
GNA_0838005_Capacity | South Bay and Central Coast | San Jose | TRIMBLE BANK 5 | 838005 | Bank | Demand Growth | Capacity | 2026 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083802117_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 2117 | 83802117 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_083802118_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 2118 | 83802118 | Feeder | None | None | None | 99.75% | 0 | 0% | 20.04 | 15 | 74.85% | 0 | 0% | 20.04 | 13.57 | 67.71% | 0 | 0% | 20.04 | 13.71 | 68.41% | 0 | 0% | 20.04 | 19.8 | 98.8% | 0 | 0% | 20.04 | 19.99 | 99.75% | 0 | 0%
GNA_083802119_Capacity | South Bay and Central Coast | San Jose | TRIMBLE 2119 | 83802119 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0829501_Capacity | South Bay and Central Coast | San Jose | EDENVALE BANK 1 | 829501 | Bank | None | None | None | 66.64% | 0 | 0% | 44.6 | 28.51 | 63.92% | 0 | 0% | 44.6 | 28.62 | 64.17% | 0 | 0% | 44.6 | 28.74 | 64.44% | 0 | 0% | 44.6 | 29.16 | 65.38% | 0 | 0% | 44.6 | 29.72 | 66.64% | 0 | 0%
GNA_082951101_Capacity | South Bay and Central Coast | San Jose | EDENVALE 1101 | 82951101 | Feeder | None | None | None | 75.8% | 0 | 0% | 11.57 | 8.51 | 73.55% | 0 | 0% | 11.57 | 8.49 | 73.38% | 0 | 0% | 11.57 | 8.49 | 73.38% | 0 | 0% | 11.57 | 8.6 | 74.33% | 0 | 0% | 11.57 | 8.77 | 75.8% | 0 | 0%
GNA_082951102_Capacity | South Bay and Central Coast | San Jose | EDENVALE 1102 | 82951102 | Feeder | None | None | None | 97.32% | 0 | 0% | 11.57 | 11.05 | 95.51% | 0 | 0% | 11.57 | 11.09 | 95.85% | 0 | 0% | 11.57 | 11.1 | 95.94% | 0 | 0% | 11.57 | 11.19 | 96.72% | 0 | 0% | 11.57 | 11.26 | 97.32% | 0 | 0%
GNA_082951103_Capacity | South Bay and Central Coast | San Jose | EDENVALE 1103 | 82951103 | Feeder | None | None | None | 92.27% | 0 | 0% | 12.42 | 10.96 | 88.24% | 0 | 0% | 12.42 | 10.96 | 88.24% | 0 | 0% | 12.42 | 11.01 | 88.65% | 0 | 0% | 12.42 | 11.16 | 89.86% | 0 | 0% | 12.42 | 11.46 | 92.27% | 0 | 0%
GNA_0829502_Capacity | South Bay and Central Coast | San Jose | EDENVALE BANK 2 | 829502 | Bank | None | None | None | 90% | 0 | 0% | 44.52 | 38.43 | 86.32% | 0 | 0% | 44.52 | 38.46 | 86.39% | 0 | 0% | 44.52 | 38.74 | 87.02% | 0 | 0% | 44.52 | 39.21 | 88.07% | 0 | 0% | 44.52 | 40.07 | 90% | 0 | 0%
GNA_082952105_Capacity | South Bay and Central Coast | San Jose | EDENVALE 2105 | 82952105 | Feeder | None | None | None | 89.11% | 0 | 0% | 22.22 | 19.8 | 89.11% | 0 | 0% | 22.22 | 19.52 | 87.85% | 0 | 0% | 22.22 | 19.41 | 87.35% | 0 | 0% | 22.22 | 19.45 | 87.53% | 0 | 0% | 22.22 | 19.66 | 88.48% | 0 | 0%
GNA_082952106_Capacity | South Bay and Central Coast | San Jose | EDENVALE 2106 | 82952106 | Feeder | None | None | None | 97.63% | 0 | 0% | 21.11 | 20.24 | 95.88% | 0 | 0% | 21.11 | 20.27 | 96.02% | 0 | 0% | 21.11 | 20.28 | 96.07% | 0 | 0% | 21.11 | 20.42 | 96.73% | 0 | 0% | 21.11 | 20.61 | 97.63% | 0 | 0%
GNA_082952107_Capacity | South Bay and Central Coast | San Jose | EDENVALE 2107 | 82952107 | Feeder | None | None | None | 49.17% | 0 | 0% | 21.11 | 8.44 | 39.98% | 0 | 0% | 21.11 | 8.9 | 42.16% | 0 | 0% | 21.11 | 9.4 | 44.53% | 0 | 0% | 21.11 | 9.88 | 46.8% | 0 | 0% | 21.11 | 10.38 | 49.17% | 0 | 0%
GNA_0829503_Capacity | South Bay and Central Coast | San Jose | EDENVALE BANK 3 | 829503 | Bank | None | None | None | 94% | 0 | 0% | 44.52 | 40.38 | 90.7% | 0 | 0% | 44.52 | 40.58 | 91.15% | 0 | 0% | 44.52 | 40.83 | 91.71% | 0 | 0% | 44.52 | 41.24 | 92.63% | 0 | 0% | 44.52 | 41.85 | 94% | 0 | 0%
GNA_082952108_Capacity | South Bay and Central Coast | San Jose | EDENVALE 2108 | 82952108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082952109_Capacity | South Bay and Central Coast | San Jose | EDENVALE 2109 | 82952109 | Feeder | None | None | None | 95.96% | 0 | 0% | 20.04 | 18.39 | 91.77% | 0 | 0% | 20.04 | 18.52 | 92.42% | 0 | 0% | 20.04 | 18.66 | 93.11% | 0 | 0% | 20.04 | 18.91 | 94.36% | 0 | 0% | 20.04 | 19.23 | 95.96% | 0 | 0%
GNA_082952110_Capacity | South Bay and Central Coast | San Jose | EDENVALE 2110 | 82952110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0829504_Capacity | South Bay and Central Coast | San Jose | EDENVALE BANK 4 | 829504 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082952111_Capacity | South Bay and Central Coast | San Jose | EDENVALE 2111 | 82952111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082952112_Capacity | South Bay and Central Coast | San Jose | EDENVALE 2112 | 82952112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082952113_Capacity | South Bay and Central Coast | San Jose | EDENVALE 2113 | 82952113 | Feeder | None | None | None | 80.96% | 0 | 0% | 21.11 | 17.09 | 80.96% | 0 | 0% | 21.11 | 16.97 | 80.39% | 0 | 0% | 21.11 | 16.85 | 79.82% | 0 | 0% | 21.11 | 16.93 | 80.2% | 0 | 0% | 21.11 | 17.07 | 80.86% | 0 | 0%
GNA_0834301_Capacity | South Bay and Central Coast | San Jose | HICKS BANK 1 | 834301 | Bank | None | None | None | 95.4% | 0 | 0% | 59.37 | 55.33 | 93.2% | 0 | 0% | 59.37 | 55.11 | 92.82% | 0 | 0% | 59.37 | 55.15 | 92.89% | 0 | 0% | 59.37 | 55.72 | 93.85% | 0 | 0% | 59.37 | 56.64 | 95.4% | 0 | 0%
GNA_083432101_Capacity | South Bay and Central Coast | San Jose | HICKS 2101 | 83432101 | Feeder | None | None | None | 95.21% | 0 | 0% | 20.26 | 18.53 | 91.46% | 0 | 0% | 20.26 | 18.39 | 90.77% | 0 | 0% | 20.26 | 18.41 | 90.87% | 0 | 0% | 20.26 | 18.8 | 92.79% | 0 | 0% | 20.26 | 19.29 | 95.21% | 0 | 0%
GNA_083432102_Capacity | South Bay and Central Coast | San Jose | HICKS 2102 | 83432102 | Feeder | None | None | None | 65.07% | 0 | 0% | 20.07 | 13.06 | 65.07% | 0 | 0% | 20.07 | 13.05 | 65.02% | 0 | 0% | 20.07 | 13.03 | 64.92% | 0 | 0% | 20.07 | 13.05 | 65.02% | 0 | 0% | 20.07 | 13.04 | 64.97% | 0 | 0%
GNA_083432103_Capacity | South Bay and Central Coast | San Jose | HICKS 2103 | 83432103 | Feeder | None | None | None | 66.92% | 0 | 0% | 20.89 | 13.64 | 65.29% | 0 | 0% | 20.89 | 13.58 | 65.01% | 0 | 0% | 20.89 | 13.6 | 65.1% | 0 | 0% | 20.89 | 13.74 | 65.77% | 0 | 0% | 20.89 | 13.98 | 66.92% | 0 | 0%
GNA_083432105_Capacity | South Bay and Central Coast | San Jose | HICKS 2105 | 83432105 | Feeder | None | None | None | 84.37% | 0 | 0% | 21.11 | 17.16 | 81.29% | 0 | 0% | 21.11 | 17.07 | 80.86% | 0 | 0% | 21.11 | 17.14 | 81.19% | 0 | 0% | 21.11 | 17.47 | 82.76% | 0 | 0% | 21.11 | 17.81 | 84.37% | 0 | 0%
GNA_0834305_Capacity | South Bay and Central Coast | San Jose | HICKS BANK 5 | 834305 | Bank | None | None | None | 38.57% | 0 | 0% | 59.37 | 22.55 | 37.98% | 0 | 0% | 59.37 | 22.59 | 38.05% | 0 | 0% | 59.37 | 22.62 | 38.1% | 0 | 0% | 59.37 | 22.73 | 38.29% | 0 | 0% | 59.37 | 22.9 | 38.57% | 0 | 0%
GNA_083432111_Capacity | South Bay and Central Coast | San Jose | HICKS 2111 | 83432111 | Feeder | None | None | None | 95.26% | 0 | 0% | 21.11 | 19.76 | 93.6% | 0 | 0% | 21.11 | 19.79 | 93.75% | 0 | 0% | 21.11 | 19.82 | 93.89% | 0 | 0% | 21.11 | 19.94 | 94.46% | 0 | 0% | 21.11 | 20.11 | 95.26% | 0 | 0%
GNA_0839103_Capacity | South Bay and Central Coast | San Jose | PIERCY BANK 3 | 839103 | Bank | None | None | None | 95.53% | 0 | 0% | 44.54 | 40.99 | 92.03% | 0 | 0% | 44.54 | 41.19 | 92.48% | 0 | 0% | 44.54 | 41.42 | 93% | 0 | 0% | 44.54 | 41.89 | 94.05% | 0 | 0% | 44.54 | 42.55 | 95.53% | 0 | 0%
GNA_083912109_Capacity | South Bay and Central Coast | San Jose | PIERCY 2109 | 83912109 | Feeder | None | None | None | 83.84% | 0 | 0% | 22.22 | 17.78 | 80.02% | 0 | 0% | 22.22 | 17.88 | 80.47% | 0 | 0% | 22.22 | 17.98 | 80.92% | 0 | 0% | 22.22 | 18.25 | 82.13% | 0 | 0% | 22.22 | 18.63 | 83.84% | 0 | 0%
GNA_083912110_Capacity | South Bay and Central Coast | San Jose | PIERCY 2110 | 83912110 | Feeder | None | None | None | 64.99% | 0 | 0% | 22.22 | 13.97 | 62.87% | 0 | 0% | 22.22 | 13.99 | 62.96% | 0 | 0% | 22.22 | 14.03 | 63.14% | 0 | 0% | 22.22 | 14.2 | 63.91% | 0 | 0% | 22.22 | 14.44 | 64.99% | 0 | 0%
GNA_083912111_Capacity | South Bay and Central Coast | San Jose | PIERCY 2111 | 83912111 | Feeder | None | None | None | 80.06% | 0 | 0% | 22.22 | 17.4 | 78.31% | 0 | 0% | 22.22 | 17.45 | 78.53% | 0 | 0% | 22.22 | 17.57 | 79.07% | 0 | 0% | 22.22 | 17.67 | 79.52% | 0 | 0% | 22.22 | 17.79 | 80.06% | 0 | 0%
GNA_0829601_Capacity | South Bay and Central Coast | San Jose | SANTA TERESA BANK 1 | 829601 | Bank | None | None | None | 92.76% | 0 | 0% | 44.6 | 20.96 | 47% | 0 | 0% | 44.6 | 29.14 | 65.34% | 0 | 0% | 44.6 | 41.37 | 92.76% | 0 | 0% | 44.6 | 8.19 | 18.36% | 0 | 0% | 44.6 | 9.67 | 21.68% | 0 | 0%
GNA_082962101_Capacity | South Bay and Central Coast | San Jose | SANTA TERESA 2101 | 82962101 | Feeder | Demand Growth | Capacity | 2025 | 114.6% | 3.24 | 14.58% | 22.22 | 16.73 | 75.29% | 0 | 0% | 22.22 | 20.14 | 90.64% | 0 | 0% | 22.22 | 25.46 | 114.6% | 3.24 | 14.58% | 22.22 | 8.13 | 36.59% | 0 | 0% | 22.22 | 8.13 | 36.59% | 0 | 0%
GNA_082962102_Capacity | South Bay and Central Coast | San Jose | SANTA TERESA 2102 | 82962102 | Feeder | None | None | None | 67.87% | 0 | 0% | 22.22 | 2.96 | 13.32% | 0 | 0% | 22.22 | 8.03 | 36.14% | 0 | 0% | 22.22 | 15.08 | 67.87% | 0 | 0% | 22.22 | -0.72 | -3.24% | 0 | 0% | 22.22 | 0.76 | 3.42% | 0 | 0%
GNA_0823101_Capacity | South Bay and Central Coast | San Jose | ALMADEN BANK 1 | 823101 | Bank | None | None | None | 74.95% | 0 | 0% | 29.7 | 21.97 | 73.97% | 0 | 0% | 29.7 | 21.81 | 73.43% | 0 | 0% | 29.7 | 21.77 | 73.3% | 0 | 0% | 29.7 | 22 | 74.07% | 0 | 0% | 29.7 | 22.26 | 74.95% | 0 | 0%
GNA_082311101_Capacity | South Bay and Central Coast | San Jose | ALMADEN 1101 | 82311101 | Feeder | None | None | None | 82.58% | 0 | 0% | 12.34 | 9.97 | 80.79% | 0 | 0% | 12.34 | 9.9 | 80.23% | 0 | 0% | 12.34 | 9.92 | 80.39% | 0 | 0% | 12.34 | 10.05 | 81.44% | 0 | 0% | 12.34 | 10.19 | 82.58% | 0 | 0%
GNA_082311102_Capacity | South Bay and Central Coast | San Jose | ALMADEN 1102 | 82311102 | Feeder | Demand Growth | Capacity | 2023 | 103.2% | 0.38 | 3.215% | 11.82 | 12.13 | 102.6% | 0.31 | 2.623% | 11.82 | 12.04 | 101.9% | 0.22 | 1.861% | 11.82 | 11.99 | 101.4% | 0.17 | 1.438% | 11.82 | 12.08 | 102.2% | 0.26 | 2.2% | 11.82 | 12.2 | 103.2% | 0.38 | 3.215%
GNA_0823103_Capacity | South Bay and Central Coast | San Jose | ALMADEN BANK 3 | 823103 | Bank | None | None | None | 76.26% | 0 | 0% | 29.7 | 22.23 | 74.85% | 0 | 0% | 29.7 | 22.1 | 74.41% | 0 | 0% | 29.7 | 22.13 | 74.51% | 0 | 0% | 29.7 | 22.42 | 75.49% | 0 | 0% | 29.7 | 22.65 | 76.26% | 0 | 0%
GNA_082311110_Capacity | South Bay and Central Coast | San Jose | ALMADEN 1110 | 82311110 | Feeder | None | None | None | 57.67% | 0 | 0% | 12.19 | 6.71 | 55.05% | 0 | 0% | 12.19 | 6.7 | 54.96% | 0 | 0% | 12.19 | 6.74 | 55.29% | 0 | 0% | 12.19 | 6.87 | 56.36% | 0 | 0% | 12.19 | 7.03 | 57.67% | 0 | 0%
GNA_082311111_Capacity | South Bay and Central Coast | San Jose | ALMADEN 1111 | 82311111 | Feeder | Demand Growth | Capacity | 2023 | 113% | 1.59 | 13.04% | 12.19 | 13.78 | 113% | 1.59 | 13.04% | 12.19 | 13.56 | 111.2% | 1.37 | 11.24% | 12.19 | 13.56 | 111.2% | 1.37 | 11.24% | 12.19 | 13.71 | 112.5% | 1.52 | 12.47% | 12.19 | 13.78 | 113% | 1.59 | 13.04%
GNA_0829201_Capacity | South Bay and Central Coast | San Jose | EL PATIO BANK 1 | 829201 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082921101_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1101 | 82921101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082921102_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1102 | 82921102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082921103_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1103 | 82921103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_082921104_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1104 | 82921104 | Feeder | None | None | None | 77.11% | 0 | 0% | 12.19 | 9.4 | 77.11% | 0 | 0% | 12.19 | 9.26 | 75.96% | 0 | 0% | 12.19 | 9.12 | 74.82% | 0 | 0% | 12.19 | 9.07 | 74.41% | 0 | 0% | 12.19 | 9.1 | 74.65% | 0 | 0%
GNA_082921105_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1105 | 82921105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0829202_Capacity | South Bay and Central Coast | San Jose | EL PATIO BANK 2 | 829202 | Bank | None | None | None | 82.94% | 0 | 0% | 44.6 | 35.42 | 79.42% | 0 | 0% | 44.6 | 36.74 | 82.38% | 0 | 0% | 44.6 | 36.66 | 82.2% | 0 | 0% | 44.6 | 36.75 | 82.4% | 0 | 0% | 44.6 | 36.99 | 82.94% | 0 | 0%
GNA_082921107_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1107 | 82921107 | Feeder | Demand Growth | Capacity | 2023 | 109.5% | 1.12 | 9.492% | 11.8 | 12.71 | 107.7% | 0.91 | 7.712% | 11.8 | 12.72 | 107.8% | 0.92 | 7.797% | 11.8 | 12.73 | 107.9% | 0.93 | 7.881% | 11.8 | 12.79 | 108.4% | 0.99 | 8.39% | 11.8 | 12.92 | 109.5% | 1.12 | 9.492%
GNA_082921108_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1108 | 82921108 | Feeder | None | None | None | 97.13% | 0 | 0% | 12.19 | 10.45 | 85.73% | 0 | 0% | 12.19 | 11.82 | 96.96% | 0 | 0% | 12.19 | 11.8 | 96.8% | 0 | 0% | 12.19 | 11.81 | 96.88% | 0 | 0% | 12.19 | 11.84 | 97.13% | 0 | 0%
GNA_082921109_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1109 | 82921109 | Feeder | None | None | None | 89.05% | 0 | 0% | 12.06 | 10.47 | 86.82% | 0 | 0% | 12.06 | 10.45 | 86.65% | 0 | 0% | 12.06 | 10.45 | 86.65% | 0 | 0% | 12.06 | 10.57 | 87.65% | 0 | 0% | 12.06 | 10.74 | 89.05% | 0 | 0%
GNA_0829203_Capacity | South Bay and Central Coast | San Jose | EL PATIO BANK 3 | 829203 | Bank | None | None | None | 75.29% | 0 | 0% | 44.6 | 28.6 | 64.13% | 0 | 0% | 44.6 | 31.49 | 70.61% | 0 | 0% | 44.6 | 33.4 | 74.89% | 0 | 0% | 44.6 | 33.48 | 75.07% | 0 | 0% | 44.6 | 33.58 | 75.29% | 0 | 0%
GNA_082921111_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1111 | 82921111 | Feeder | None | None | None | 16.11% | 0 | 0% | 10.8 | 1.74 | 16.11% | 0 | 0% | 10.8 | 1.72 | 15.93% | 0 | 0% | 10.8 | 1.71 | 15.83% | 0 | 0% | 10.8 | 1.7 | 15.74% | 0 | 0% | 10.8 | 1.7 | 15.74% | 0 | 0%
GNA_082921112_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1112 | 82921112 | Feeder | None | None | None | 97.87% | 0 | 0% | 12.19 | 10.11 | 82.94% | 0 | 0% | 12.19 | 11.38 | 93.36% | 0 | 0% | 12.19 | 11.51 | 94.42% | 0 | 0% | 12.19 | 11.72 | 96.14% | 0 | 0% | 12.19 | 11.93 | 97.87% | 0 | 0%
GNA_082921113_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1113 | 82921113 | Feeder | None | None | None | 97.95% | 0 | 0% | 12.19 | 11.94 | 97.95% | 0 | 0% | 12.19 | 11.88 | 97.46% | 0 | 0% | 12.19 | 11.81 | 96.88% | 0 | 0% | 12.19 | 11.79 | 96.72% | 0 | 0% | 12.19 | 11.78 | 96.64% | 0 | 0%
GNA_082921114_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1114 (previously 1115) | 82921114 | Feeder | None | None | None | 89.8% | 0 | 0% | 11.57 | 6.87 | 59.38% | 0 | 0% | 11.57 | 8.44 | 72.95% | 0 | 0% | 11.57 | 10.39 | 89.8% | 0 | 0% | 11.57 | 10.38 | 89.71% | 0 | 0% | 11.57 | 10.36 | 89.54% | 0 | 0%
GNA_0829204_Capacity | South Bay and Central Coast | San Jose | EL PATIO BANK 4 | 829204 | Bank | None | None | None | 76.87% | 0 | 0% | 44.53 | 33.17 | 74.49% | 0 | 0% | 44.53 | 34.05 | 76.47% | 0 | 0% | 44.53 | 33.96 | 76.26% | 0 | 0% | 44.53 | 34.1 | 76.58% | 0 | 0% | 44.53 | 34.23 | 76.87% | 0 | 0%
GNA_082921116_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1116 (previously 1110) | 82921116 | Feeder | None | None | None | 92.83% | 0 | 0% | 11.57 | 9.59 | 82.89% | 0 | 0% | 11.57 | 10.6 | 91.62% | 0 | 0% | 11.57 | 10.61 | 91.7% | 0 | 0% | 11.57 | 10.68 | 92.31% | 0 | 0% | 11.57 | 10.74 | 92.83% | 0 | 0%
GNA_082921117_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1117 (previously 1114) | 82921117 | Feeder | None | None | None | 66.03% | 0 | 0% | 11.57 | 7.64 | 66.03% | 0 | 0% | 11.57 | 7.58 | 65.51% | 0 | 0% | 11.57 | 7.54 | 65.17% | 0 | 0% | 11.57 | 7.54 | 65.17% | 0 | 0% | 11.57 | 7.52 | 65% | 0 | 0%
GNA_082921118_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1118 (previously 1101) | 82921118 | Feeder | None | None | None | 58.17% | 0 | 0% | 11.57 | 6.61 | 57.13% | 0 | 0% | 11.57 | 6.61 | 57.13% | 0 | 0% | 11.57 | 6.61 | 57.13% | 0 | 0% | 11.57 | 6.66 | 57.56% | 0 | 0% | 11.57 | 6.73 | 58.17% | 0 | 0%
GNA_082921119_Capacity | South Bay and Central Coast | San Jose | EL PATIO 1119 (previously 1102) | 82921119 | Feeder | None | None | None | 77.87% | 0 | 0% | 11.57 | 9.01 | 77.87% | 0 | 0% | 11.57 | 8.97 | 77.53% | 0 | 0% | 11.57 | 8.93 | 77.18% | 0 | 0% | 11.57 | 8.95 | 77.36% | 0 | 0% | 11.57 | 8.98 | 77.61% | 0 | 0%
GNA_0834302_Capacity | South Bay and Central Coast | San Jose | HICKS BANK 2 | 834302 | Bank | Demand Growth | Capacity | 2023 | 117.4% | 7.75 | 17.38% | 44.6 | 50.99 | 114.3% | 6.39 | 14.33% | 44.6 | 50.96 | 114.3% | 6.36 | 14.26% | 44.6 | 51.04 | 114.4% | 6.44 | 14.44% | 44.6 | 51.69 | 115.9% | 7.09 | 15.9% | 44.6 | 52.35 | 117.4% | 7.75 | 17.38%
GNA_083431108_Capacity | South Bay and Central Coast | San Jose | HICKS 1108 | 83431108 | Feeder | None | None | None | 95.85% | 0 | 0% | 12.06 | 11.32 | 93.86% | 0 | 0% | 12.06 | 11.31 | 93.78% | 0 | 0% | 12.06 | 11.33 | 93.95% | 0 | 0% | 12.06 | 11.44 | 94.86% | 0 | 0% | 12.06 | 11.56 | 95.85% | 0 | 0%
GNA_083431109_Capacity | South Bay and Central Coast | San Jose | HICKS 1109 | 83431109 | Feeder | None | None | None | 98.51% | 0 | 0% | 12.06 | 11.69 | 96.93% | 0 | 0% | 12.06 | 11.62 | 96.35% | 0 | 0% | 12.06 | 11.59 | 96.1% | 0 | 0% | 12.06 | 11.72 | 97.18% | 0 | 0% | 12.06 | 11.88 | 98.51% | 0 | 0%
GNA_083431110_Capacity | South Bay and Central Coast | San Jose | HICKS 1110 | 83431110 | Feeder | Demand Growth | Capacity | 2023 | 112.4% | 1.5 | 12.44% | 12.06 | 13.15 | 109% | 1.09 | 9.038% | 12.06 | 13.09 | 108.5% | 1.03 | 8.541% | 12.06 | 13.16 | 109.1% | 1.1 | 9.121% | 12.06 | 13.35 | 110.7% | 1.29 | 10.7% | 12.06 | 13.56 | 112.4% | 1.5 | 12.44%
GNA_083431111_Capacity | South Bay and Central Coast | San Jose | HICKS 1111 | 83431111 | Feeder | None | None | None | 91.38% | 0 | 0% | 12.06 | 11.01 | 91.29% | 0 | 0% | 12.06 | 10.84 | 89.88% | 0 | 0% | 12.06 | 10.76 | 89.22% | 0 | 0% | 12.06 | 10.89 | 90.3% | 0 | 0% | 12.06 | 11.02 | 91.38% | 0 | 0%
GNA_083431112_Capacity | South Bay and Central Coast | San Jose | HICKS 1112 | 83431112 | Feeder | None | None | None | 30.55% | 0 | 0% | 12.44 | 3.49 | 28.05% | 0 | 0% | 12.44 | 3.76 | 30.23% | 0 | 0% | 12.44 | 3.76 | 30.23% | 0 | 0% | 12.44 | 3.78 | 30.39% | 0 | 0% | 12.44 | 3.8 | 30.55% | 0 | 0%
GNA_0834303_Capacity | South Bay and Central Coast | San Jose | HICKS BANK 3 | 834303 | Bank | None | None | None | 87.58% | 0 | 0% | 44.6 | 38.91 | 87.24% | 0 | 0% | 44.6 | 38.75 | 86.88% | 0 | 0% | 44.6 | 38.54 | 86.41% | 0 | 0% | 44.6 | 38.72 | 86.82% | 0 | 0% | 44.6 | 39.06 | 87.58% | 0 | 0%
GNA_083431113_Capacity | South Bay and Central Coast | San Jose | HICKS 1113 | 83431113 | Feeder | None | None | None | 81.01% | 0 | 0% | 12.06 | 9.77 | 81.01% | 0 | 0% | 12.06 | 9.69 | 80.35% | 0 | 0% | 12.06 | 9.59 | 79.52% | 0 | 0% | 12.06 | 9.62 | 79.77% | 0 | 0% | 12.06 | 9.72 | 80.6% | 0 | 0%
GNA_083431114_Capacity | South Bay and Central Coast | San Jose | HICKS 1114 | 83431114 | Feeder | None | None | None | 84.91% | 0 | 0% | 12.06 | 10.21 | 84.66% | 0 | 0% | 12.06 | 10.19 | 84.49% | 0 | 0% | 12.06 | 10.14 | 84.08% | 0 | 0% | 12.06 | 10.19 | 84.49% | 0 | 0% | 12.06 | 10.24 | 84.91% | 0 | 0%
GNA_083431115_Capacity | South Bay and Central Coast | San Jose | HICKS 1115 | 83431115 | Feeder | None | None | None | 89.55% | 0 | 0% | 12.06 | 10.32 | 85.57% | 0 | 0% | 12.06 | 10.39 | 86.15% | 0 | 0% | 12.06 | 10.45 | 86.65% | 0 | 0% | 12.06 | 10.61 | 87.98% | 0 | 0% | 12.06 | 10.8 | 89.55% | 0 | 0%
GNA_083431116_Capacity | South Bay and Central Coast | San Jose | HICKS 1116 | 83431116 | Feeder | None | None | None | 92.85% | 0 | 0% | 12.44 | 11.55 | 92.85% | 0 | 0% | 12.44 | 11.46 | 92.12% | 0 | 0% | 12.44 | 11.35 | 91.24% | 0 | 0% | 12.44 | 11.34 | 91.16% | 0 | 0% | 12.44 | 11.35 | 91.24% | 0 | 0%
GNA_1521001_Capacity | North Valley and Sierra | Sierra | ALLEGHANY BANK 1 | 1521001 | Bank | None | None | None | 16.2% | 0 | 0% | 11.73 | 1.9 | 16.2% | 0 | 0% | 11.73 | 1.89 | 16.11% | 0 | 0% | 11.73 | 1.9 | 16.2% | 0 | 0% | 11.73 | 1.9 | 16.2% | 0 | 0% | 11.73 | 1.9 | 16.2% | 0 | 0%
GNA_152101101_Capacity | North Valley and Sierra | Sierra | ALLEGHANY 1101 | 152101101 | Feeder | None | None | None | 19.1% | 0 | 0% | 7.12 | 1.36 | 19.1% | 0 | 0% | 7.12 | 1.35 | 18.96% | 0 | 0% | 7.12 | 1.36 | 19.1% | 0 | 0% | 7.12 | 1.36 | 19.1% | 0 | 0% | 7.12 | 1.36 | 19.1% | 0 | 0%
GNA_152101102_Capacity | North Valley and Sierra | Sierra | ALLEGHANY 1102 | 152101102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1536601_Capacity | North Valley and Sierra | Sierra | APPLE HILL BANK 1 | 1536601 | Bank | None | None | None | 91.04% | 0 | 0% | 15.84 | 14.42 | 91.04% | 0 | 0% | 15.84 | 14.3 | 90.28% | 0 | 0% | 15.84 | 14.21 | 89.71% | 0 | 0% | 15.84 | 14.14 | 89.27% | 0 | 0% | 15.84 | 14.08 | 88.89% | 0 | 0%
GNA_153662102_Capacity | North Valley and Sierra | Sierra | APPLE HILL 2102 | 153662102 | Feeder | None | None | None | 79.38% | 0 | 0% | 16.44 | 13.05 | 79.38% | 0 | 0% | 16.44 | 12.93 | 78.65% | 0 | 0% | 16.44 | 12.84 | 78.1% | 0 | 0% | 16.44 | 12.77 | 77.68% | 0 | 0% | 16.44 | 12.71 | 77.31% | 0 | 0%
GNA_1536602_Capacity | North Valley and Sierra | Sierra | APPLE HILL BANK 2 | 1536602 | Bank | None | None | None | 65.85% | 0 | 0% | 15.84 | 10.37 | 65.47% | 0 | 0% | 15.84 | 10.36 | 65.4% | 0 | 0% | 15.84 | 10.36 | 65.4% | 0 | 0% | 15.84 | 10.39 | 65.59% | 0 | 0% | 15.84 | 10.43 | 65.85% | 0 | 0%
GNA_153661103_Capacity | North Valley and Sierra | Sierra | APPLE HILL 1103 | 153661103 | Feeder | None | None | None | 64.41% | 0 | 0% | 10.76 | 6.89 | 64.03% | 0 | 0% | 10.76 | 6.89 | 64.03% | 0 | 0% | 10.76 | 6.89 | 64.03% | 0 | 0% | 10.76 | 6.91 | 64.22% | 0 | 0% | 10.76 | 6.93 | 64.41% | 0 | 0%
GNA_153661104_Capacity | North Valley and Sierra | Sierra | APPLE HILL 1104 | 153661104 | Feeder | None | None | None | 49.71% | 0 | 0% | 12.19 | 6.06 | 49.71% | 0 | 0% | 12.19 | 6.02 | 49.38% | 0 | 0% | 12.19 | 6.01 | 49.3% | 0 | 0% | 12.19 | 5.99 | 49.14% | 0 | 0% | 12.19 | 5.99 | 49.14% | 0 | 0%
GNA_1580301_Capacity | North Valley and Sierra | Sierra | ECHO SUMMIT BANK 1 | 1580301 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_158031101_Capacity | North Valley and Sierra | Sierra | ECHO SUMMIT 1101 | 158031101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1527601_Capacity | North Valley and Sierra | Sierra | EL DORADO P H BANK 1 | 1527601 | Bank | None | None | None | 91.21% | 0 | 0% | 11.94 | 10.89 | 91.21% | 0 | 0% | 11.94 | 10.83 | 90.7% | 0 | 0% | 11.94 | 10.83 | 90.7% | 0 | 0% | 11.94 | 10.8 | 90.45% | 0 | 0% | 11.94 | 10.79 | 90.37% | 0 | 0%
GNA_152762101_Capacity | North Valley and Sierra | Sierra | EL DORADO P H 2101 | 152762101 | Feeder | None | None | None | 42.81% | 0 | 0% | 14.81 | 6.34 | 42.81% | 0 | 0% | 14.81 | 6.28 | 42.4% | 0 | 0% | 14.81 | 6.27 | 42.34% | 0 | 0% | 14.81 | 6.22 | 42% | 0 | 0% | 14.81 | 6.21 | 41.93% | 0 | 0%
GNA_152762102_Capacity | North Valley and Sierra | Sierra | EL DORADO P H 2102 | 152762102 | Feeder | None | None | None | 50.94% | 0 | 0% | 7.44 | 3.79 | 50.94% | 0 | 0% | 7.44 | 3.79 | 50.94% | 0 | 0% | 7.44 | 3.79 | 50.94% | 0 | 0% | 7.44 | 3.79 | 50.94% | 0 | 0% | 7.44 | 3.78 | 50.81% | 0 | 0%
GNA_1537601_Capacity | North Valley and Sierra | Sierra | CATLETT BANK 1 | 1537601 | Bank | None | None | None | 82.47% | 0 | 0% | 9.3 | 6.31 | 67.85% | 0 | 0% | 9.3 | 7.66 | 82.37% | 0 | 0% | 9.3 | 7.66 | 82.37% | 0 | 0% | 9.3 | 7.65 | 82.26% | 0 | 0% | 9.3 | 7.67 | 82.47% | 0 | 0%
GNA_153761102_Capacity | North Valley and Sierra | Sierra | CATLETT 1102 | 153761102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1537602_Capacity | North Valley and Sierra | Sierra | CATLETT BANK 2 | 1537602 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_153761105_Capacity | North Valley and Sierra | Sierra | CATLETT 1105 | 153761105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1521501_Capacity | North Valley and Sierra | Sierra | EAST NICOLAUS BANK 1 | 1521501 | Bank | None | None | None | 85.42% | 0 | 0% | 15.84 | 12.11 | 76.45% | 0 | 0% | 15.84 | 13.53 | 85.42% | 0 | 0% | 15.84 | 13.51 | 85.29% | 0 | 0% | 15.84 | 13.5 | 85.23% | 0 | 0% | 15.84 | 13.52 | 85.35% | 0 | 0%
GNA_152151101_Capacity | North Valley and Sierra | Sierra | EAST NICOLAUS 1101 | 152151101 | Feeder | None | None | None | 53.63% | 0 | 0% | 8.13 | 4.36 | 53.63% | 0 | 0% | 8.13 | 4.36 | 53.63% | 0 | 0% | 8.13 | 4.35 | 53.51% | 0 | 0% | 8.13 | 4.35 | 53.51% | 0 | 0% | 8.13 | 4.35 | 53.51% | 0 | 0%
GNA_152151102_Capacity | North Valley and Sierra | Sierra | EAST NICOLAUS 1102 | 152151102 | Feeder | None | None | None | 37.58% | 0 | 0% | 9.9 | 3.72 | 37.58% | 0 | 0% | 9.9 | 3.72 | 37.58% | 0 | 0% | 9.9 | 3.71 | 37.47% | 0 | 0% | 9.9 | 3.71 | 37.47% | 0 | 0% | 9.9 | 3.72 | 37.58% | 0 | 0%
GNA_152151103_Capacity | North Valley and Sierra | Sierra | EAST NICOLAUS 1103 | 152151103 | Feeder | None | None | None | 93.25% | 0 | 0% | 8.15 | 6.17 | 75.71% | 0 | 0% | 8.15 | 7.6 | 93.25% | 0 | 0% | 8.15 | 7.6 | 93.25% | 0 | 0% | 8.15 | 7.58 | 93.01% | 0 | 0% | 8.15 | 7.58 | 93.01% | 0 | 0%
GNA_1537301_Capacity | North Valley and Sierra | Sierra | PLUMAS BANK 1 | 1537301 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_153731101_Capacity | North Valley and Sierra | Sierra | PLUMAS 1101 | 153731101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_153731102_Capacity | North Valley and Sierra | Sierra | PLUMAS 1102 | 153731102 | Feeder | None | None | None | 60.06% | 0 | 0% | 7.01 | 3.85 | 54.92% | 0 | 0% | 7.01 | 3.94 | 56.21% | 0 | 0% | 7.01 | 4.03 | 57.49% | 0 | 0% | 7.01 | 4.12 | 58.77% | 0 | 0% | 7.01 | 4.21 | 60.06% | 0 | 0%
GNA_1537302_Capacity | North Valley and Sierra | Sierra | PLUMAS BANK 2 | 1537302 | Bank | None | None | None | 42.22% | 0 | 0% | 44.5 | 18.09 | 40.65% | 0 | 0% | 44.5 | 18.27 | 41.06% | 0 | 0% | 44.5 | 18.43 | 41.42% | 0 | 0% | 44.5 | 18.61 | 41.82% | 0 | 0% | 44.5 | 18.79 | 42.22% | 0 | 0%
GNA_153732106_Capacity | North Valley and Sierra | Sierra | PLUMAS 2106 | 153732106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_153732107_Capacity | North Valley and Sierra | Sierra | PLUMAS 2107 | 153732107 | Feeder | None | None | None | 66.43% | 0 | 0% | 22.22 | 14.43 | 64.94% | 0 | 0% | 22.22 | 14.51 | 65.3% | 0 | 0% | 22.22 | 14.58 | 65.62% | 0 | 0% | 22.22 | 14.68 | 66.07% | 0 | 0% | 22.22 | 14.76 | 66.43% | 0 | 0%
GNA_1528101_Capacity | North Valley and Sierra | Sierra | WHEATLAND BANK 1 | 1528101 | Bank | None | None | None | 59.76% | 0 | 0% | 12.6 | 7.11 | 56.43% | 0 | 0% | 12.6 | 7.2 | 57.14% | 0 | 0% | 12.6 | 7.29 | 57.86% | 0 | 0% | 12.6 | 7.42 | 58.89% | 0 | 0% | 12.6 | 7.53 | 59.76% | 0 | 0%
GNA_152811102_Capacity | North Valley and Sierra | Sierra | WHEATLAND 1102 | 152811102 | Feeder | None | None | None | 66.24% | 0 | 0% | 11.67 | 7.31 | 62.64% | 0 | 0% | 11.67 | 7.4 | 63.41% | 0 | 0% | 11.67 | 7.49 | 64.18% | 0 | 0% | 11.67 | 7.62 | 65.3% | 0 | 0% | 11.67 | 7.73 | 66.24% | 0 | 0%
GNA_1528102_Capacity | North Valley and Sierra | Sierra | WHEATLAND BANK 2 | 1528102 | Bank | None | None | None | 42.96% | 0 | 0% | 29.7 | 11.72 | 39.46% | 0 | 0% | 29.7 | 11.81 | 39.76% | 0 | 0% | 29.7 | 12.49 | 42.05% | 0 | 0% | 29.7 | 12.62 | 42.49% | 0 | 0% | 29.7 | 12.76 | 42.96% | 0 | 0%
GNA_152811104_Capacity | North Valley and Sierra | Sierra | WHEATLAND 1104 | 152811104 | Feeder | None | None | None | 58.69% | 0 | 0% | 12.83 | 6.55 | 51.05% | 0 | 0% | 12.83 | 6.63 | 51.68% | 0 | 0% | 12.83 | 7.3 | 56.9% | 0 | 0% | 12.83 | 7.41 | 57.76% | 0 | 0% | 12.83 | 7.53 | 58.69% | 0 | 0%
GNA_152811105_Capacity | North Valley and Sierra | Sierra | WHEATLAND 1105 | 152811105 | Feeder | None | None | None | 87.56% | 0 | 0% | 6.03 | 5.28 | 87.56% | 0 | 0% | 6.03 | 5.24 | 86.9% | 0 | 0% | 6.03 | 5.19 | 86.07% | 0 | 0% | 6.03 | 5.14 | 85.24% | 0 | 0% | 6.03 | 5.15 | 85.41% | 0 | 0%
GNA_1523001_Capacity | North Valley and Sierra | Sierra | BONNIE NOOK BANK 1 | 1523001 | Bank | None | None | None | 90.96% | 0 | 0% | 1.77 | 1.6 | 90.4% | 0 | 0% | 1.77 | 1.6 | 90.4% | 0 | 0% | 1.77 | 1.6 | 90.4% | 0 | 0% | 1.77 | 1.6 | 90.4% | 0 | 0% | 1.77 | 1.61 | 90.96% | 0 | 0%
GNA_152301101_Capacity | North Valley and Sierra | Sierra | BONNIE NOOK 1101 | 152301101 | Feeder | None | None | None | 24.3% | 0 | 0% | 3.21 | 0.78 | 24.3% | 0 | 0% | 3.21 | 0.78 | 24.3% | 0 | 0% | 3.21 | 0.78 | 24.3% | 0 | 0% | 3.21 | 0.78 | 24.3% | 0 | 0% | 3.21 | 0.78 | 24.3% | 0 | 0%
GNA_152301102_Capacity | North Valley and Sierra | Sierra | BONNIE NOOK 1102 | 152301102 | Feeder | None | None | None | 27.73% | 0 | 0% | 3.21 | 0.88 | 27.41% | 0 | 0% | 3.21 | 0.89 | 27.73% | 0 | 0% | 3.21 | 0.88 | 27.41% | 0 | 0% | 3.21 | 0.89 | 27.73% | 0 | 0% | 3.21 | 0.89 | 27.73% | 0 | 0%
GNA_1524301_Capacity | North Valley and Sierra | Sierra | SHADY GLEN BANK 1 | 1524301 | Bank | None | None | None | 96.7% | 0 | 0% | 8.79 | 8.5 | 96.7% | 0 | 0% | 8.79 | 8.43 | 95.9% | 0 | 0% | 8.79 | 8.47 | 96.36% | 0 | 0% | 8.79 | 8.43 | 95.9% | 0 | 0% | 8.79 | 8.41 | 95.68% | 0 | 0%
GNA_152431101_Capacity | North Valley and Sierra | Sierra | SHADY GLEN 1101 | 152431101 | Feeder | None | None | None | 68.65% | 0 | 0% | 8.55 | 5.85 | 68.42% | 0 | 0% | 8.55 | 5.81 | 67.95% | 0 | 0% | 8.55 | 5.87 | 68.65% | 0 | 0% | 8.55 | 5.84 | 68.3% | 0 | 0% | 8.55 | 5.85 | 68.42% | 0 | 0%
GNA_152431102_Capacity | North Valley and Sierra | Sierra | SHADY GLEN 1102 | 152431102 | Feeder | None | None | None | 25.16% | 0 | 0% | 10.69 | 2.69 | 25.16% | 0 | 0% | 10.69 | 2.67 | 24.98% | 0 | 0% | 10.69 | 2.64 | 24.7% | 0 | 0% | 10.69 | 2.63 | 24.6% | 0 | 0% | 10.69 | 2.61 | 24.42% | 0 | 0%
GNA_1524801_Capacity | North Valley and Sierra | Sierra | BRUNSWICK BANK 1 | 1524801 | Bank | None | None | None | 80.54% | 0 | 0% | 29.7 | 23.92 | 80.54% | 0 | 0% | 29.7 | 23.79 | 80.1% | 0 | 0% | 29.7 | 23.67 | 79.7% | 0 | 0% | 29.7 | 23.62 | 79.53% | 0 | 0% | 29.7 | 23.67 | 79.7% | 0 | 0%
GNA_152481102_Capacity | North Valley and Sierra | Sierra | BRUNSWICK 1102 | 152481102 | Feeder | None | None | None | 42.53% | 0 | 0% | 13.26 | 5.64 | 42.53% | 0 | 0% | 13.26 | 5.51 | 41.55% | 0 | 0% | 13.26 | 5.38 | 40.57% | 0 | 0% | 13.26 | 5.3 | 39.97% | 0 | 0% | 13.26 | 5.25 | 39.59% | 0 | 0%
GNA_152481103_Capacity | North Valley and Sierra | Sierra | BRUNSWICK 1103 | 152481103 | Feeder | None | None | None | 83.92% | 0 | 0% | 12.25 | 10.28 | 83.92% | 0 | 0% | 12.25 | 10.14 | 82.78% | 0 | 0% | 12.25 | 9.97 | 81.39% | 0 | 0% | 12.25 | 9.83 | 80.24% | 0 | 0% | 12.25 | 9.72 | 79.35% | 0 | 0%
GNA_152481104_Capacity | North Valley and Sierra | Sierra | BRUNSWICK 1104 | 152481104 | Feeder | None | None | None | 73.11% | 0 | 0% | 12.83 | 9.38 | 73.11% | 0 | 0% | 12.83 | 9.32 | 72.64% | 0 | 0% | 12.83 | 9.3 | 72.49% | 0 | 0% | 12.83 | 9.26 | 72.17% | 0 | 0% | 12.83 | 9.27 | 72.25% | 0 | 0%
GNA_1524802_Capacity | North Valley and Sierra | Sierra | BRUNSWICK BANK 2 | 1524802 | Bank | None | None | None | 71.97% | 0 | 0% | 39.6 | 28.5 | 71.97% | 0 | 0% | 39.6 | 28.19 | 71.19% | 0 | 0% | 39.6 | 27.98 | 70.66% | 0 | 0% | 39.6 | 27.81 | 70.23% | 0 | 0% | 39.6 | 27.77 | 70.13% | 0 | 0%
GNA_152481105_Capacity | North Valley and Sierra | Sierra | BRUNSWICK 1105 | 152481105 | Feeder | None | None | None | 91.84% | 0 | 0% | 12.25 | 11.23 | 91.67% | 0 | 0% | 12.25 | 11.06 | 90.29% | 0 | 0% | 12.25 | 11.1 | 90.61% | 0 | 0% | 12.25 | 11.18 | 91.27% | 0 | 0% | 12.25 | 11.25 | 91.84% | 0 | 0%
GNA_152481106_Capacity | North Valley and Sierra | Sierra | BRUNSWICK 1106 | 152481106 | Feeder | None | None | None | 93.92% | 0 | 0% | 15.14 | 14.22 | 93.92% | 0 | 0% | 15.14 | 14.08 | 93% | 0 | 0% | 15.14 | 13.96 | 92.21% | 0 | 0% | 15.14 | 13.85 | 91.48% | 0 | 0% | 15.14 | 13.82 | 91.28% | 0 | 0%
GNA_152481107_Capacity | North Valley and Sierra | Sierra | BRUNSWICK 1107 | 152481107 | Feeder | None | None | None | 51.19% | 0 | 0% | 15.14 | 7.75 | 51.19% | 0 | 0% | 15.14 | 7.7 | 50.86% | 0 | 0% | 15.14 | 7.68 | 50.73% | 0 | 0% | 15.14 | 7.64 | 50.46% | 0 | 0% | 15.14 | 7.67 | 50.66% | 0 | 0%
GNA_1524803_Capacity | North Valley and Sierra | Sierra | BRUNSWICK BANK 3 | 1524803 | Bank | None | None | None | 35.42% | 0 | 0% | 29.7 | 10.52 | 35.42% | 0 | 0% | 29.7 | 10.35 | 34.85% | 0 | 0% | 29.7 | 10.18 | 34.28% | 0 | 0% | 29.7 | 9.98 | 33.6% | 0 | 0% | 29.7 | 9.91 | 33.37% | 0 | 0%
GNA_152481110_Capacity | North Valley and Sierra | Sierra | BRUNSWICK 1110 | 152481110 | Feeder | None | None | None | 74.52% | 0 | 0% | 14.13 | 10.53 | 74.52% | 0 | 0% | 14.13 | 10.37 | 73.39% | 0 | 0% | 14.13 | 10.2 | 72.19% | 0 | 0% | 14.13 | 9.99 | 70.7% | 0 | 0% | 14.13 | 9.92 | 70.21% | 0 | 0%
GNA_1520302_Capacity | North Valley and Sierra | Sierra | GRASS VALLEY BANK 2 | 1520302 | Bank | None | None | None | 84.69% | 0 | 0% | 17.63 | 14.93 | 84.69% | 0 | 0% | 17.63 | 14.81 | 84% | 0 | 0% | 17.63 | 14.75 | 83.66% | 0 | 0% | 17.63 | 14.73 | 83.55% | 0 | 0% | 17.63 | 14.78 | 83.83% | 0 | 0%
GNA_152031101_Capacity | North Valley and Sierra | Sierra | GRASS VALLEY 1101 | 152031101 | Feeder | None | None | None | 43.15% | 0 | 0% | 12.19 | 5.26 | 43.15% | 0 | 0% | 12.19 | 5.24 | 42.99% | 0 | 0% | 12.19 | 5.23 | 42.9% | 0 | 0% | 12.19 | 5.22 | 42.82% | 0 | 0% | 12.19 | 5.23 | 42.9% | 0 | 0%
GNA_152031102_Capacity | North Valley and Sierra | Sierra | GRASS VALLEY 1102 | 152031102 | Feeder | None | None | None | 37.41% | 0 | 0% | 12.19 | 4.56 | 37.41% | 0 | 0% | 12.19 | 4.51 | 37% | 0 | 0% | 12.19 | 4.49 | 36.83% | 0 | 0% | 12.19 | 4.47 | 36.67% | 0 | 0% | 12.19 | 4.46 | 36.59% | 0 | 0%
GNA_152031103_Capacity | North Valley and Sierra | Sierra | GRASS VALLEY 1103 | 152031103 | Feeder | None | None | None | 53.06% | 0 | 0% | 10.46 | 5.55 | 53.06% | 0 | 0% | 10.46 | 5.5 | 52.58% | 0 | 0% | 10.46 | 5.47 | 52.29% | 0 | 0% | 10.46 | 5.47 | 52.29% | 0 | 0% | 10.46 | 5.51 | 52.68% | 0 | 0%
GNA_1526901_Capacity | North Valley and Sierra | Sierra | HIGGINS BANK 1 | 1526901 | Bank | None | None | None | 54.86% | 0 | 0% | 44.55 | 24.44 | 54.86% | 0 | 0% | 44.55 | 24.23 | 54.39% | 0 | 0% | 44.55 | 24.05 | 53.98% | 0 | 0% | 44.55 | 23.99 | 53.85% | 0 | 0% | 44.55 | 24.06 | 54.01% | 0 | 0%
GNA_152691103_Capacity | North Valley and Sierra | Sierra | HIGGINS 1103 | 152691103 | Feeder | None | None | None | 77.34% | 0 | 0% | 15.14 | 11.71 | 77.34% | 0 | 0% | 15.14 | 11.62 | 76.75% | 0 | 0% | 15.14 | 11.54 | 76.22% | 0 | 0% | 15.14 | 11.52 | 76.09% | 0 | 0% | 15.14 | 11.52 | 76.09% | 0 | 0%
GNA_152691104_Capacity | North Valley and Sierra | Sierra | HIGGINS 1104 | 152691104 | Feeder | None | None | None | 77.94% | 0 | 0% | 15.14 | 11.8 | 77.94% | 0 | 0% | 15.14 | 11.68 | 77.15% | 0 | 0% | 15.14 | 11.59 | 76.55% | 0 | 0% | 15.14 | 11.54 | 76.22% | 0 | 0% | 15.14 | 11.61 | 76.68% | 0 | 0%
GNA_1526902_Capacity | North Valley and Sierra | Sierra | HIGGINS BANK 2 | 1526902 | Bank | None | None | None | 44.07% | 0 | 0% | 15.84 | 6.98 | 44.07% | 0 | 0% | 15.84 | 6.92 | 43.69% | 0 | 0% | 15.84 | 6.88 | 43.43% | 0 | 0% | 15.84 | 6.84 | 43.18% | 0 | 0% | 15.84 | 6.83 | 43.12% | 0 | 0%
GNA_152691107_Capacity | North Valley and Sierra | Sierra | HIGGINS 1107 | 152691107 | Feeder | None | None | None | 53.5% | 0 | 0% | 14.13 | 7.56 | 53.5% | 0 | 0% | 14.13 | 7.5 | 53.08% | 0 | 0% | 14.13 | 7.46 | 52.8% | 0 | 0% | 14.13 | 7.42 | 52.51% | 0 | 0% | 14.13 | 7.41 | 52.44% | 0 | 0%
GNA_1526903_Capacity | North Valley and Sierra | Sierra | HIGGINS BANK 3 | 1526903 | Bank | None | None | None | 55.62% | 0 | 0% | 15.84 | 8.76 | 55.3% | 0 | 0% | 15.84 | 8.67 | 54.73% | 0 | 0% | 15.84 | 8.65 | 54.61% | 0 | 0% | 15.84 | 8.7 | 54.92% | 0 | 0% | 15.84 | 8.81 | 55.62% | 0 | 0%
GNA_152691109_Capacity | North Valley and Sierra | Sierra | HIGGINS 1109 | 152691109 | Feeder | None | None | None | 39.38% | 0 | 0% | 12.19 | 4.74 | 38.88% | 0 | 0% | 12.19 | 4.74 | 38.88% | 0 | 0% | 12.19 | 4.74 | 38.88% | 0 | 0% | 12.19 | 4.76 | 39.05% | 0 | 0% | 12.19 | 4.8 | 39.38% | 0 | 0%
GNA_152691110_Capacity | North Valley and Sierra | Sierra | HIGGINS 1110 | 152691110 | Feeder | None | None | None | 47.91% | 0 | 0% | 12.19 | 5.84 | 47.91% | 0 | 0% | 12.19 | 5.79 | 47.5% | 0 | 0% | 12.19 | 5.75 | 47.17% | 0 | 0% | 12.19 | 5.76 | 47.25% | 0 | 0% | 12.19 | 5.81 | 47.66% | 0 | 0%
GNA_1536101_Capacity | North Valley and Sierra | Sierra | CLARKSVILLE BANK 1 | 1536101 | Bank | None | None | None | 73.45% | 0 | 0% | 44.6 | 32.54 | 72.96% | 0 | 0% | 44.6 | 32.48 | 72.83% | 0 | 0% | 44.6 | 32.47 | 72.8% | 0 | 0% | 44.6 | 32.54 | 72.96% | 0 | 0% | 44.6 | 32.76 | 73.45% | 0 | 0%
GNA_153612103_Capacity | North Valley and Sierra | Sierra | CLARKSVILLE 2103 | 153612103 | Feeder | None | None | None | 76.15% | 0 | 0% | 23.56 | 17.6 | 74.7% | 0 | 0% | 23.56 | 17.64 | 74.87% | 0 | 0% | 23.56 | 17.7 | 75.13% | 0 | 0% | 23.56 | 17.79 | 75.51% | 0 | 0% | 23.56 | 17.94 | 76.15% | 0 | 0%
GNA_153612104_Capacity | North Valley and Sierra | Sierra | CLARKSVILLE 2104 | 153612104 | Feeder | None | None | None | 91.36% | 0 | 0% | 21.41 | 19.56 | 91.36% | 0 | 0% | 21.41 | 19.46 | 90.89% | 0 | 0% | 21.41 | 19.39 | 90.57% | 0 | 0% | 21.41 | 19.37 | 90.47% | 0 | 0% | 21.41 | 19.44 | 90.8% | 0 | 0%
GNA_1536102_Capacity | North Valley and Sierra | Sierra | CLARKSVILLE BANK 2 | 1536102 | Bank | None | None | None | 85.47% | 0 | 0% | 44.6 | 37.31 | 83.65% | 0 | 0% | 44.6 | 37.2 | 83.41% | 0 | 0% | 44.6 | 37.14 | 83.27% | 0 | 0% | 44.6 | 37.45 | 83.97% | 0 | 0% | 44.6 | 38.12 | 85.47% | 0 | 0%
GNA_153612105_Capacity | North Valley and Sierra | Sierra | CLARKSVILLE 2105 | 153612105 | Feeder | None | None | None | 97.15% | 0 | 0% | 21.41 | 20.07 | 93.74% | 0 | 0% | 21.41 | 20.19 | 94.3% | 0 | 0% | 21.41 | 20.29 | 94.77% | 0 | 0% | 21.41 | 20.52 | 95.84% | 0 | 0% | 21.41 | 20.8 | 97.15% | 0 | 0%
GNA_153612106_Capacity | North Valley and Sierra | Sierra | CLARKSVILLE 2106 | 153612106 | Feeder | None | None | None | 92.7% | 0 | 0% | 21.11 | 18.93 | 89.67% | 0 | 0% | 21.11 | 18.95 | 89.77% | 0 | 0% | 21.11 | 19.02 | 90.1% | 0 | 0% | 21.11 | 19.23 | 91.09% | 0 | 0% | 21.11 | 19.57 | 92.7% | 0 | 0%
GNA_1536103_Capacity | North Valley and Sierra | Sierra | CLARKSVILLE BANK 3 | 1536103 | Bank | None | None | None | 97.78% | 0 | 0% | 44.6 | 42.83 | 96.03% | 0 | 0% | 44.6 | 42.85 | 96.08% | 0 | 0% | 44.6 | 42.94 | 96.28% | 0 | 0% | 44.6 | 43.22 | 96.91% | 0 | 0% | 44.6 | 43.61 | 97.78% | 0 | 0%
GNA_153612109_Capacity | North Valley and Sierra | Sierra | CLARKSVILLE 2109 | 153612109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_153612110_Capacity | North Valley and Sierra | Sierra | CLARKSVILLE 2110 | 153612110 | Feeder | None | None | None | 97.75% | 0 | 0% | 23.56 | 22.65 | 96.14% | 0 | 0% | 23.56 | 22.63 | 96.05% | 0 | 0% | 23.56 | 22.64 | 96.1% | 0 | 0% | 23.56 | 22.82 | 96.86% | 0 | 0% | 23.56 | 23.03 | 97.75% | 0 | 0%
GNA_1536501_Capacity | North Valley and Sierra | Sierra | SHINGLE SPRINGS BANK 1 | 1536501 | Bank | None | None | None | 81% | 0 | 0% | 15.84 | 12.83 | 81% | 0 | 0% | 15.84 | 12.75 | 80.49% | 0 | 0% | 15.84 | 12.69 | 80.11% | 0 | 0% | 15.84 | 12.73 | 80.37% | 0 | 0% | 15.84 | 12.81 | 80.87% | 0 | 0%
GNA_153651103_Capacity | North Valley and Sierra | Sierra | SHINGLE SPRINGS 1103 | 153651103 | Feeder | None | None | None | 67.84% | 0 | 0% | 10.76 | 7.3 | 67.84% | 0 | 0% | 10.76 | 7.27 | 67.57% | 0 | 0% | 10.76 | 7.24 | 67.29% | 0 | 0% | 10.76 | 7.23 | 67.19% | 0 | 0% | 10.76 | 7.25 | 67.38% | 0 | 0%
GNA_153651104_Capacity | North Valley and Sierra | Sierra | SHINGLE SPRINGS 1104 | 153651104 | Feeder | None | None | None | 44.71% | 0 | 0% | 12.19 | 5.38 | 44.13% | 0 | 0% | 12.19 | 5.37 | 44.05% | 0 | 0% | 12.19 | 5.37 | 44.05% | 0 | 0% | 12.19 | 5.4 | 44.3% | 0 | 0% | 12.19 | 5.45 | 44.71% | 0 | 0%
GNA_1536502_Capacity | North Valley and Sierra | Sierra | SHINGLE SPRINGS BANK 2 | 1536502 | Bank | None | None | None | 96.02% | 0 | 0% | 15.84 | 15.02 | 94.82% | 0 | 0% | 15.84 | 15 | 94.7% | 0 | 0% | 15.84 | 15.02 | 94.82% | 0 | 0% | 15.84 | 15.1 | 95.33% | 0 | 0% | 15.84 | 15.21 | 96.02% | 0 | 0%
GNA_153652105_Capacity | North Valley and Sierra | Sierra | SHINGLE SPRINGS 2105 | 153652105 | Feeder | None | None | None | 76.82% | 0 | 0% | 19.63 | 14.89 | 75.85% | 0 | 0% | 19.63 | 14.87 | 75.75% | 0 | 0% | 19.63 | 14.89 | 75.85% | 0 | 0% | 19.63 | 14.96 | 76.21% | 0 | 0% | 19.63 | 15.08 | 76.82% | 0 | 0%
GNA_1536503_Capacity | North Valley and Sierra | Sierra | SHINGLE SPRINGS BANK 3 | 1536503 | Bank | None | None | None | 95.18% | 0 | 0% | 44.6 | 42.45 | 95.18% | 0 | 0% | 44.6 | 42.2 | 94.62% | 0 | 0% | 44.6 | 41.96 | 94.08% | 0 | 0% | 44.6 | 41.93 | 94.01% | 0 | 0% | 44.6 | 41.92 | 93.99% | 0 | 0%
GNA_153652108_Capacity | North Valley and Sierra | Sierra | SHINGLE SPRINGS 2108 | 153652108 | Feeder | None | None | None | 71.32% | 0 | 0% | 19.63 | 14 | 71.32% | 0 | 0% | 19.63 | 13.91 | 70.86% | 0 | 0% | 19.63 | 13.83 | 70.45% | 0 | 0% | 19.63 | 13.83 | 70.45% | 0 | 0% | 19.63 | 13.84 | 70.5% | 0 | 0%
GNA_153652109_Capacity | North Valley and Sierra | Sierra | SHINGLE SPRINGS 2109 | 153652109 | Feeder | None | None | None | 71.57% | 0 | 0% | 21.67 | 15.51 | 71.57% | 0 | 0% | 21.67 | 15.37 | 70.93% | 0 | 0% | 21.67 | 15.25 | 70.37% | 0 | 0% | 21.67 | 15.23 | 70.28% | 0 | 0% | 21.67 | 15.24 | 70.33% | 0 | 0%
GNA_153652110_Capacity | North Valley and Sierra | Sierra | SHINGLE SPRINGS 2110 | 153652110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1524701_Capacity | North Valley and Sierra | Sierra | COLUMBIA HILL BANK 1 | 1524701 | Bank | None | None | None | 72.51% | 0 | 0% | 4.11 | 2.97 | 72.26% | 0 | 0% | 4.11 | 2.96 | 72.02% | 0 | 0% | 4.11 | 2.96 | 72.02% | 0 | 0% | 4.11 | 2.96 | 72.02% | 0 | 0% | 4.11 | 2.98 | 72.51% | 0 | 0%
GNA_152471101_Capacity | North Valley and Sierra | Sierra | COLUMBIA HILL 1101 | 152471101 | Feeder | None | None | None | 72.91% | 0 | 0% | 4.06 | 2.95 | 72.66% | 0 | 0% | 4.06 | 2.94 | 72.41% | 0 | 0% | 4.06 | 2.94 | 72.41% | 0 | 0% | 4.06 | 2.94 | 72.41% | 0 | 0% | 4.06 | 2.96 | 72.91% | 0 | 0%
GNA_1522601_Capacity | North Valley and Sierra | Sierra | DIAMOND SPRINGS BANK 1 | 1522601 | Bank | None | None | None | 86.93% | 0 | 0% | 15.84 | 13.77 | 86.93% | 0 | 0% | 15.84 | 13.68 | 86.36% | 0 | 0% | 15.84 | 13.59 | 85.8% | 0 | 0% | 15.84 | 13.56 | 85.61% | 0 | 0% | 15.84 | 13.56 | 85.61% | 0 | 0%
GNA_152261103_Capacity | North Valley and Sierra | Sierra | DIAMOND SPRINGS 1103 | 152261103 | Feeder | None | None | None | 97.71% | 0 | 0% | 11.33 | 11.07 | 97.71% | 0 | 0% | 11.33 | 11 | 97.09% | 0 | 0% | 11.33 | 10.95 | 96.65% | 0 | 0% | 11.33 | 10.94 | 96.56% | 0 | 0% | 11.33 | 10.94 | 96.56% | 0 | 0%
GNA_152261104_Capacity | North Valley and Sierra | Sierra | DIAMOND SPRINGS 1104 | 152261104 | Feeder | None | None | None | 35.13% | 0 | 0% | 11.33 | 3.98 | 35.13% | 0 | 0% | 11.33 | 3.95 | 34.86% | 0 | 0% | 11.33 | 3.91 | 34.51% | 0 | 0% | 11.33 | 3.89 | 34.33% | 0 | 0% | 11.33 | 3.89 | 34.33% | 0 | 0%
GNA_1522602_Capacity | North Valley and Sierra | Sierra | DIAMOND SPRINGS BANK 2 | 1522602 | Bank | None | None | None | 61.35% | 0 | 0% | 44.6 | 26.48 | 59.37% | 0 | 0% | 44.6 | 27.36 | 61.35% | 0 | 0% | 44.6 | 27.24 | 61.08% | 0 | 0% | 44.6 | 27.15 | 60.87% | 0 | 0% | 44.6 | 27.17 | 60.92% | 0 | 0%
GNA_152261105_Capacity | North Valley and Sierra | Sierra | DIAMOND SPRINGS 1105 | 152261105 | Feeder | None | None | None | 80.59% | 0 | 0% | 10.46 | 8.43 | 80.59% | 0 | 0% | 10.46 | 8.4 | 80.31% | 0 | 0% | 10.46 | 8.38 | 80.11% | 0 | 0% | 10.46 | 8.37 | 80.02% | 0 | 0% | 10.46 | 8.39 | 80.21% | 0 | 0%
GNA_152261106_Capacity | North Valley and Sierra | Sierra | DIAMOND SPRINGS 1106 | 152261106 | Feeder | None | None | None | 86.42% | 0 | 0% | 10.46 | 9.04 | 86.42% | 0 | 0% | 10.46 | 8.88 | 84.89% | 0 | 0% | 10.46 | 8.74 | 83.56% | 0 | 0% | 10.46 | 8.64 | 82.6% | 0 | 0% | 10.46 | 8.65 | 82.7% | 0 | 0%
GNA_152261107_Capacity | North Valley and Sierra | Sierra | DIAMOND SPRINGS 1107 | 152261107 | Feeder | None | None | None | 84.86% | 0 | 0% | 13.21 | 10.07 | 76.23% | 0 | 0% | 13.21 | 11.21 | 84.86% | 0 | 0% | 13.21 | 11.17 | 84.56% | 0 | 0% | 13.21 | 11.16 | 84.48% | 0 | 0% | 13.21 | 11.16 | 84.48% | 0 | 0%
GNA_1530802_Capacity | North Valley and Sierra | Sierra | PLACERVILLE BANK 2 | 1530802 | Bank | None | None | None | 41.92% | 0 | 0% | 29.7 | 12.45 | 41.92% | 0 | 0% | 29.7 | 12.38 | 41.68% | 0 | 0% | 29.7 | 12.31 | 41.45% | 0 | 0% | 29.7 | 12.26 | 41.28% | 0 | 0% | 29.7 | 12.25 | 41.25% | 0 | 0%
GNA_153082106_Capacity | North Valley and Sierra | Sierra | PLACERVILLE 2106 | 153082106 | Feeder | None | None | None | 76.32% | 0 | 0% | 17.74 | 13.54 | 76.32% | 0 | 0% | 17.74 | 13.47 | 75.93% | 0 | 0% | 17.74 | 13.4 | 75.54% | 0 | 0% | 17.74 | 13.35 | 75.25% | 0 | 0% | 17.74 | 13.34 | 75.2% | 0 | 0%
GNA_1530803_Capacity | North Valley and Sierra | Sierra | PLACERVILLE BANK 3 | 1530803 | Bank | None | None | None | 76.13% | 0 | 0% | 29.7 | 22.61 | 76.13% | 0 | 0% | 29.7 | 22.48 | 75.69% | 0 | 0% | 29.7 | 22.38 | 75.35% | 0 | 0% | 29.7 | 22.28 | 75.02% | 0 | 0% | 29.7 | 22.27 | 74.98% | 0 | 0%
GNA_153081109_Capacity | North Valley and Sierra | Sierra | PLACERVILLE 1109 | 153081109 | Feeder | None | None | None | 17.38% | 0 | 0% | 10.76 | 1.87 | 17.38% | 0 | 0% | 10.76 | 1.84 | 17.1% | 0 | 0% | 10.76 | 1.81 | 16.82% | 0 | 0% | 10.76 | 1.76 | 16.36% | 0 | 0% | 10.76 | 1.74 | 16.17% | 0 | 0%
GNA_153081110_Capacity | North Valley and Sierra | Sierra | PLACERVILLE 1110 | 153081110 | Feeder | None | None | None | 56.78% | 0 | 0% | 10.76 | 6.11 | 56.78% | 0 | 0% | 10.76 | 6.07 | 56.41% | 0 | 0% | 10.76 | 6.03 | 56.04% | 0 | 0% | 10.76 | 5.99 | 55.67% | 0 | 0% | 10.76 | 5.97 | 55.48% | 0 | 0%
GNA_153081111_Capacity | North Valley and Sierra | Sierra | PLACERVILLE 1111 | 153081111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_153081112_Capacity | North Valley and Sierra | Sierra | PLACERVILLE 1112 | 153081112 | Feeder | None | None | None | 74.86% | 0 | 0% | 10.46 | 7.83 | 74.86% | 0 | 0% | 10.46 | 7.77 | 74.28% | 0 | 0% | 10.46 | 7.73 | 73.9% | 0 | 0% | 10.46 | 7.71 | 73.71% | 0 | 0% | 10.46 | 7.7 | 73.61% | 0 | 0%
GNA_1523202_Capacity | North Valley and Sierra | Sierra | DRUM BANK 2 | 1523202 | Bank | None | None | None | 75.71% | 0 | 0% | 0.7 | 0.53 | 75.71% | 0 | 0% | 0.7 | 0.53 | 75.71% | 0 | 0% | 0.7 | 0.53 | 75.71% | 0 | 0% | 0.7 | 0.53 | 75.71% | 0 | 0% | 0.7 | 0.53 | 75.71% | 0 | 0%
GNA_152321101_Capacity | North Valley and Sierra | Sierra | DRUM 1101 | 152321101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1522502_Capacity | North Valley and Sierra | Sierra | SPAULDING BANK 2 | 1522502 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152251101_Capacity | North Valley and Sierra | Sierra | SPAULDING 1101 | 152251101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1525901_Capacity | North Valley and Sierra | Sierra | SUMMIT BANK 1 | 1525901 | Bank | None | None | None | 26.42% | 0 | 0% | 8.44 | 2.22 | 26.3% | 0 | 0% | 8.44 | 2.22 | 26.3% | 0 | 0% | 8.44 | 2.22 | 26.3% | 0 | 0% | 8.44 | 2.22 | 26.3% | 0 | 0% | 8.44 | 2.23 | 26.42% | 0 | 0%
GNA_152591101_Capacity | North Valley and Sierra | Sierra | SUMMIT 1101 | 152591101 | Feeder | None | None | None | 27.39% | 0 | 0% | 7.12 | 1.91 | 26.83% | 0 | 0% | 7.12 | 1.92 | 26.97% | 0 | 0% | 7.12 | 1.93 | 27.11% | 0 | 0% | 7.12 | 1.94 | 27.25% | 0 | 0% | 7.12 | 1.95 | 27.39% | 0 | 0%
GNA_152591102_Capacity | North Valley and Sierra | Sierra | SUMMIT 1102 | 152591102 | Feeder | None | None | None | 20.28% | 0 | 0% | 3.55 | 0.72 | 20.28% | 0 | 0% | 3.55 | 0.72 | 20.28% | 0 | 0% | 3.55 | 0.71 | 20% | 0 | 0% | 3.55 | 0.71 | 20% | 0 | 0% | 3.55 | 0.71 | 20% | 0 | 0%
GNA_1522901_Capacity | North Valley and Sierra | Sierra | TAMARACK BANK 1 | 1522901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152291101_Capacity | North Valley and Sierra | Sierra | TAMARACK 1101 | 152291101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152291102_Capacity | North Valley and Sierra | Sierra | TAMARACK 1102 | 152291102 | Feeder | None | None | None | 15.77% | 0 | 0% | 3.36 | 0.53 | 15.77% | 0 | 0% | 3.36 | 0.53 | 15.77% | 0 | 0% | 3.36 | 0.53 | 15.77% | 0 | 0% | 3.36 | 0.53 | 15.77% | 0 | 0% | 3.36 | 0.53 | 15.77% | 0 | 0%
GNA_1521801_Capacity | North Valley and Sierra | Sierra | FOREST HILL BANK 1 | 1521801 | Bank | None | None | None | 45.11% | 0 | 0% | 19.73 | 8.9 | 45.11% | 0 | 0% | 19.73 | 8.87 | 44.96% | 0 | 0% | 19.73 | 8.85 | 44.86% | 0 | 0% | 19.73 | 8.84 | 44.8% | 0 | 0% | 19.73 | 8.84 | 44.8% | 0 | 0%
GNA_152181101_Capacity | North Valley and Sierra | Sierra | FORESTHILL 1101 | 152181101 | Feeder | None | None | None | 66.79% | 0 | 0% | 10.69 | 7.14 | 66.79% | 0 | 0% | 10.69 | 7.11 | 66.51% | 0 | 0% | 10.69 | 7.1 | 66.42% | 0 | 0% | 10.69 | 7.09 | 66.32% | 0 | 0% | 10.69 | 7.09 | 66.32% | 0 | 0%
GNA_152181102_Capacity | North Valley and Sierra | Sierra | FORESTHILL 1102 | 152181102 | Feeder | None | None | None | 47.96% | 0 | 0% | 3.19 | 1.53 | 47.96% | 0 | 0% | 3.19 | 1.53 | 47.96% | 0 | 0% | 3.19 | 1.53 | 47.96% | 0 | 0% | 3.19 | 1.53 | 47.96% | 0 | 0% | 3.19 | 1.53 | 47.96% | 0 | 0%
GNA_1525701_Capacity | North Valley and Sierra | Sierra | HORSESHOE BANK 1 | 1525701 | Bank | None | None | None | 55.56% | 0 | 0% | 44.55 | 23.59 | 52.95% | 0 | 0% | 44.55 | 23.85 | 53.54% | 0 | 0% | 44.55 | 24.15 | 54.21% | 0 | 0% | 44.55 | 24.43 | 54.84% | 0 | 0% | 44.55 | 24.75 | 55.56% | 0 | 0%
GNA_152571101_Capacity | North Valley and Sierra | Sierra | HORSESHOE 1101 | 152571101 | Feeder | None | None | None | 70.88% | 0 | 0% | 12.19 | 8.25 | 67.68% | 0 | 0% | 12.19 | 8.34 | 68.42% | 0 | 0% | 12.19 | 8.44 | 69.24% | 0 | 0% | 12.19 | 8.54 | 70.06% | 0 | 0% | 12.19 | 8.64 | 70.88% | 0 | 0%
GNA_152571102_Capacity | North Valley and Sierra | Sierra | HORSESHOE 1102 | 152571102 | Feeder | None | None | None | 71.21% | 0 | 0% | 12.19 | 8.34 | 68.42% | 0 | 0% | 12.19 | 8.42 | 69.07% | 0 | 0% | 12.19 | 8.5 | 69.73% | 0 | 0% | 12.19 | 8.58 | 70.39% | 0 | 0% | 12.19 | 8.68 | 71.21% | 0 | 0%
GNA_152571103_Capacity | North Valley and Sierra | Sierra | HORSESHOE 1103 | 152571103 | Feeder | None | None | None | 79.29% | 0 | 0% | 12.36 | 9.38 | 75.89% | 0 | 0% | 12.36 | 9.48 | 76.7% | 0 | 0% | 12.36 | 9.59 | 77.59% | 0 | 0% | 12.36 | 9.69 | 78.4% | 0 | 0% | 12.36 | 9.8 | 79.29% | 0 | 0%
GNA_1525702_Capacity | North Valley and Sierra | Sierra | HORSESHOE BANK 2 | 1525702 | Bank | None | None | None | 56.75% | 0 | 0% | 44.55 | 24.96 | 56.03% | 0 | 0% | 44.55 | 25.02 | 56.16% | 0 | 0% | 44.55 | 25.08 | 56.3% | 0 | 0% | 44.55 | 25.18 | 56.52% | 0 | 0% | 44.55 | 25.28 | 56.75% | 0 | 0%
GNA_152571104_Capacity | North Valley and Sierra | Sierra | HORSESHOE 1104 | 152571104 | Feeder | None | None | None | 59.39% | 0 | 0% | 12.19 | 7.24 | 59.39% | 0 | 0% | 12.19 | 7.23 | 59.31% | 0 | 0% | 12.19 | 7.23 | 59.31% | 0 | 0% | 12.19 | 7.22 | 59.23% | 0 | 0% | 12.19 | 7.22 | 59.23% | 0 | 0%
GNA_152571105_Capacity | North Valley and Sierra | Sierra | HORSESHOE 1105 | 152571105 | Feeder | None | None | None | 68.83% | 0 | 0% | 12.19 | 8.39 | 68.83% | 0 | 0% | 12.19 | 8.38 | 68.74% | 0 | 0% | 12.19 | 8.35 | 68.5% | 0 | 0% | 12.19 | 8.36 | 68.58% | 0 | 0% | 12.19 | 8.35 | 68.5% | 0 | 0%
GNA_152571106_Capacity | North Valley and Sierra | Sierra | HORSESHOE 1106 | 152571106 | Feeder | None | None | None | 84.47% | 0 | 0% | 12.36 | 10.05 | 81.31% | 0 | 0% | 12.36 | 10.13 | 81.96% | 0 | 0% | 12.36 | 10.23 | 82.77% | 0 | 0% | 12.36 | 10.32 | 83.5% | 0 | 0% | 12.36 | 10.44 | 84.47% | 0 | 0%
GNA_1537001_Capacity | North Valley and Sierra | Sierra | LINCOLN BANK 1 | 1537001 | Bank | None | None | None | 91.62% | 0 | 0% | 29.7 | 26.76 | 90.1% | 0 | 0% | 29.7 | 26.84 | 90.37% | 0 | 0% | 29.7 | 26.91 | 90.61% | 0 | 0% | 29.7 | 27.06 | 91.11% | 0 | 0% | 29.7 | 27.21 | 91.62% | 0 | 0%
GNA_153701101_Capacity | North Valley and Sierra | Sierra | LINCOLN 1101 | 153701101 | Feeder | None | None | None | 74.07% | 0 | 0% | 15.12 | 10.86 | 71.83% | 0 | 0% | 15.12 | 10.92 | 72.22% | 0 | 0% | 15.12 | 10.98 | 72.62% | 0 | 0% | 15.12 | 11.08 | 73.28% | 0 | 0% | 15.12 | 11.2 | 74.07% | 0 | 0%
GNA_153701102_Capacity | North Valley and Sierra | Sierra | LINCOLN 1102 | 153701102 | Feeder | None | None | None | 82.01% | 0 | 0% | 15.12 | 12.25 | 81.02% | 0 | 0% | 15.12 | 12.23 | 80.89% | 0 | 0% | 15.12 | 12.2 | 80.69% | 0 | 0% | 15.12 | 12.29 | 81.28% | 0 | 0% | 15.12 | 12.4 | 82.01% | 0 | 0%
GNA_1537002_Capacity | North Valley and Sierra | Sierra | LINCOLN BANK 2 | 1537002 | Bank | None | None | None | 58.02% | 0 | 0% | 44.55 | 25.84 | 58% | 0 | 0% | 44.55 | 25.79 | 57.89% | 0 | 0% | 44.55 | 25.83 | 57.98% | 0 | 0% | 44.55 | 25.85 | 58.02% | 0 | 0% | 44.55 | 25.82 | 57.96% | 0 | 0%
GNA_153702108_Capacity | North Valley and Sierra | Sierra | LINCOLN 2108 | 153702108 | Feeder | None | None | None | 95.41% | 0 | 0% | 10.67 | 9.74 | 91.28% | 0 | 0% | 10.67 | 9.82 | 92.03% | 0 | 0% | 10.67 | 9.92 | 92.97% | 0 | 0% | 10.67 | 10.04 | 94.1% | 0 | 0% | 10.67 | 10.18 | 95.41% | 0 | 0%
GNA_153702109_Capacity | North Valley and Sierra | Sierra | LINCOLN 2109 | 153702109 | Feeder | None | None | None | 67.87% | 0 | 0% | 22.22 | 15.08 | 67.87% | 0 | 0% | 22.22 | 15.03 | 67.64% | 0 | 0% | 22.22 | 15.03 | 67.64% | 0 | 0% | 22.22 | 15 | 67.51% | 0 | 0% | 22.22 | 14.95 | 67.28% | 0 | 0%
GNA_1537003_Capacity | North Valley and Sierra | Sierra | LINCOLN BANK 3 | 1537003 | Bank | None | None | None | 99.37% | 0 | 0% | 15.84 | 15.48 | 97.73% | 0 | 0% | 15.84 | 15.65 | 98.8% | 0 | 0% | 15.84 | 15.24 | 96.21% | 0 | 0% | 15.84 | 15.49 | 97.79% | 0 | 0% | 15.84 | 15.74 | 99.37% | 0 | 0%
GNA_153701104_Capacity | North Valley and Sierra | Sierra | LINCOLN 1104 | 153701104 | Feeder | None | None | None | 72.08% | 0 | 0% | 8.13 | 5.78 | 71.09% | 0 | 0% | 8.13 | 5.86 | 72.08% | 0 | 0% | 8.13 | 5.35 | 65.81% | 0 | 0% | 8.13 | 5.47 | 67.28% | 0 | 0% | 8.13 | 5.6 | 68.88% | 0 | 0%
GNA_153701105_Capacity | North Valley and Sierra | Sierra | LINCOLN 1105 | 153701105 | Feeder | None | None | None | 69.84% | 0 | 0% | 15.12 | 10.11 | 66.87% | 0 | 0% | 15.12 | 10.19 | 67.39% | 0 | 0% | 15.12 | 10.31 | 68.19% | 0 | 0% | 15.12 | 10.43 | 68.98% | 0 | 0% | 15.12 | 10.56 | 69.84% | 0 | 0%
GNA_1523302_Capacity | North Valley and Sierra | Sierra | EAST MARYSVILLE BANK 2 | 1523302 | Bank | None | None | None | 94.88% | 0 | 0% | 12.31 | 10.99 | 89.28% | 0 | 0% | 12.31 | 11.13 | 90.41% | 0 | 0% | 12.31 | 11.26 | 91.47% | 0 | 0% | 12.31 | 11.46 | 93.1% | 0 | 0% | 12.31 | 11.68 | 94.88% | 0 | 0%
GNA_152331105_Capacity | North Valley and Sierra | Sierra | EAST MARYSVILLE 1105 | 152331105 | Feeder | None | None | None | 93.03% | 0 | 0% | 12.19 | 10.65 | 87.37% | 0 | 0% | 12.19 | 10.78 | 88.43% | 0 | 0% | 12.19 | 10.92 | 89.58% | 0 | 0% | 12.19 | 11.12 | 91.22% | 0 | 0% | 12.19 | 11.34 | 93.03% | 0 | 0%
GNA_1523303_Capacity | North Valley and Sierra | Sierra | EAST MARYSVILLE BANK 3 | 1523303 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152331107_Capacity | North Valley and Sierra | Sierra | EAST MARYSVILLE 1107 | 152331107 | Feeder | None | None | None | 57.37% | 0 | 0% | 11.33 | 6.31 | 55.69% | 0 | 0% | 11.33 | 6.25 | 55.16% | 0 | 0% | 11.33 | 6.27 | 55.34% | 0 | 0% | 11.33 | 6.35 | 56.05% | 0 | 0% | 11.33 | 6.5 | 57.37% | 0 | 0%
GNA_152331108_Capacity | North Valley and Sierra | Sierra | EAST MARYSVILLE 1108 | 152331108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1520101_Capacity | North Valley and Sierra | Sierra | MARYSVILLE BANK 1 | 1520101 | Bank | None | None | None | 84.65% | 0 | 0% | 29.7 | 23.15 | 77.95% | 0 | 0% | 29.7 | 23.3 | 78.45% | 0 | 0% | 29.7 | 23.45 | 78.96% | 0 | 0% | 29.7 | 23.68 | 79.73% | 0 | 0% | 29.7 | 25.14 | 84.65% | 0 | 0%
GNA_152011106_Capacity | North Valley and Sierra | Sierra | MARYSVILLE 1106 | 152011106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152011107_Capacity | North Valley and Sierra | Sierra | MARYSVILLE 1107 | 152011107 | Feeder | None | None | None | 69.6% | 0 | 0% | 10.46 | 7.28 | 69.6% | 0 | 0% | 10.46 | 7.21 | 68.93% | 0 | 0% | 10.46 | 7.15 | 68.36% | 0 | 0% | 10.46 | 7.11 | 67.97% | 0 | 0% | 10.46 | 7.05 | 67.4% | 0 | 0%
GNA_152011108_Capacity | North Valley and Sierra | Sierra | MARYSVILLE 1108 | 152011108 | Feeder | None | None | None | 93.16% | 0 | 0% | 13.6 | 11.96 | 87.94% | 0 | 0% | 13.6 | 12.11 | 89.04% | 0 | 0% | 13.6 | 12.25 | 90.07% | 0 | 0% | 13.6 | 12.44 | 91.47% | 0 | 0% | 13.6 | 12.67 | 93.16% | 0 | 0%
GNA_1520103_Capacity | North Valley and Sierra | Sierra | MARYSVILLE BANK 3 | 1520103 | Bank | None | None | None | 98.75% | 0 | 0% | 17.63 | 16.32 | 92.57% | 0 | 0% | 17.63 | 16.63 | 94.33% | 0 | 0% | 17.63 | 16.99 | 96.37% | 0 | 0% | 17.63 | 17.41 | 98.75% | 0 | 0% | 17.63 | 16.73 | 94.9% | 0 | 0%
GNA_152011102_Capacity | North Valley and Sierra | Sierra | MARYSVILLE 1102 | 152011102 | Feeder | None | None | None | 33.11% | 0 | 0% | 13.68 | 4.31 | 31.51% | 0 | 0% | 13.68 | 4.33 | 31.65% | 0 | 0% | 13.68 | 4.4 | 32.16% | 0 | 0% | 13.68 | 4.53 | 33.11% | 0 | 0% | 13.68 | 3.49 | 25.51% | 0 | 0%
GNA_152011103_Capacity | North Valley and Sierra | Sierra | MARYSVILLE 1103 | 152011103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152011104_Capacity | North Valley and Sierra | Sierra | MARYSVILLE 1104 | 152011104 | Feeder | None | None | None | 24.48% | 0 | 0% | 8.13 | 1.77 | 21.77% | 0 | 0% | 8.13 | 1.79 | 22.02% | 0 | 0% | 8.13 | 1.8 | 22.14% | 0 | 0% | 8.13 | 1.85 | 22.76% | 0 | 0% | 8.13 | 1.99 | 24.48% | 0 | 0%
GNA_152011105_Capacity | North Valley and Sierra | Sierra | MARYSVILLE 1105 | 152011105 | Feeder | None | None | None | 67.22% | 0 | 0% | 9.58 | 5.85 | 61.06% | 0 | 0% | 9.58 | 5.96 | 62.21% | 0 | 0% | 9.58 | 6.09 | 63.57% | 0 | 0% | 9.58 | 6.25 | 65.24% | 0 | 0% | 9.58 | 6.44 | 67.22% | 0 | 0%
GNA_1529001_Capacity | North Valley and Sierra | Sierra | OLIVEHURST BANK 1 | 1529001 | Bank | None | None | None | 45.52% | 0 | 0% | 29.7 | 11.84 | 39.87% | 0 | 0% | 29.7 | 12.62 | 42.49% | 0 | 0% | 29.7 | 13.06 | 43.97% | 0 | 0% | 29.7 | 13.49 | 45.42% | 0 | 0% | 29.7 | 13.52 | 45.52% | 0 | 0%
GNA_152901101_Capacity | North Valley and Sierra | Sierra | OLIVEHURST 1101 | 152901101 | Feeder | None | None | None | 92.88% | 0 | 0% | 9.41 | 7.06 | 75.03% | 0 | 0% | 9.41 | 7.85 | 83.42% | 0 | 0% | 9.41 | 8.29 | 88.1% | 0 | 0% | 9.41 | 8.71 | 92.56% | 0 | 0% | 9.41 | 8.74 | 92.88% | 0 | 0%
GNA_152901102_Capacity | North Valley and Sierra | Sierra | OLIVEHURST 1102 | 152901102 | Feeder | None | None | None | 41.72% | 0 | 0% | 10.69 | 4.45 | 41.63% | 0 | 0% | 10.69 | 4.45 | 41.63% | 0 | 0% | 10.69 | 4.46 | 41.72% | 0 | 0% | 10.69 | 4.46 | 41.72% | 0 | 0% | 10.69 | 4.45 | 41.63% | 0 | 0%
GNA_1529002_Capacity | North Valley and Sierra | Sierra | OLIVEHURST BANK 2 | 1529002 | Bank | None | None | None | 76.33% | 0 | 0% | 29.7 | 21.83 | 73.5% | 0 | 0% | 29.7 | 21.85 | 73.57% | 0 | 0% | 29.7 | 22.04 | 74.21% | 0 | 0% | 29.7 | 22.35 | 75.25% | 0 | 0% | 29.7 | 22.67 | 76.33% | 0 | 0%
GNA_152901103_Capacity | North Valley and Sierra | Sierra | OLIVEHURST 1103 | 152901103 | Feeder | Demand Growth | Capacity | 2025 | 106% | 0.74 | 5.987% | 12.36 | 12.19 | 98.62% | 0 | 0% | 12.36 | 12.3 | 99.51% | 0 | 0% | 12.36 | 12.53 | 101.4% | 0.17 | 1.375% | 12.36 | 12.82 | 103.7% | 0.46 | 3.722% | 12.36 | 13.1 | 106% | 0.74 | 5.987%
GNA_152901104_Capacity | North Valley and Sierra | Sierra | OLIVEHURST 1104 | 152901104 | Feeder | None | None | None | 50.67% | 0 | 0% | 10.46 | 5.3 | 50.67% | 0 | 0% | 10.46 | 5.27 | 50.38% | 0 | 0% | 10.46 | 5.25 | 50.19% | 0 | 0% | 10.46 | 5.26 | 50.29% | 0 | 0% | 10.46 | 5.29 | 50.57% | 0 | 0%
GNA_152901105_Capacity | North Valley and Sierra | Sierra | OLIVEHURST 1105 | 152901105 | Feeder | None | None | None | 50% | 0 | 0% | 10.46 | 5.23 | 50% | 0 | 0% | 10.46 | 5.22 | 49.9% | 0 | 0% | 10.46 | 5.22 | 49.9% | 0 | 0% | 10.46 | 5.23 | 50% | 0 | 0% | 10.46 | 5.22 | 49.9% | 0 | 0%
GNA_1522801_Capacity | North Valley and Sierra | Sierra | MOUNTAIN QUARRIES BANK 1 | 1522801 | Bank | None | None | None | 84.09% | 0 | 0% | 15.84 | 13.32 | 84.09% | 0 | 0% | 15.84 | 13.18 | 83.21% | 0 | 0% | 15.84 | 13.1 | 82.7% | 0 | 0% | 15.84 | 13.06 | 82.45% | 0 | 0% | 15.84 | 13.09 | 82.64% | 0 | 0%
GNA_152282101_Capacity | North Valley and Sierra | Sierra | MOUNTAIN QUARRIES 2101 | 152282101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1531301_Capacity | North Valley and Sierra | Sierra | NARROWS BANK 1 | 1531301 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_153132101_Capacity | North Valley and Sierra | Sierra | NARROWS 2101 | 153132101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_153132102_Capacity | North Valley and Sierra | Sierra | NARROWS 2102 | 153132102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1531302_Capacity | North Valley and Sierra | Sierra | NARROWS BANK 2 | 1531302 | Bank | None | None | None | 43.6% | 0 | 0% | 29.7 | 12.95 | 43.6% | 0 | 0% | 29.7 | 12.83 | 43.2% | 0 | 0% | 29.7 | 12.73 | 42.86% | 0 | 0% | 29.7 | 12.69 | 42.73% | 0 | 0% | 29.7 | 12.67 | 42.66% | 0 | 0%
GNA_153132105_Capacity | North Valley and Sierra | Sierra | NARROWS 2105 | 153132105 | Feeder | None | None | None | 58.99% | 0 | 0% | 21.41 | 12.63 | 58.99% | 0 | 0% | 21.41 | 12.52 | 58.48% | 0 | 0% | 21.41 | 12.41 | 57.96% | 0 | 0% | 21.41 | 12.37 | 57.78% | 0 | 0% | 21.41 | 12.35 | 57.68% | 0 | 0%
GNA_1521601_Capacity | North Valley and Sierra | Sierra | AUBURN BANK 1 | 1521601 | Bank | None | None | None | 79.53% | 0 | 0% | 8.11 | 6.45 | 79.53% | 0 | 0% | 8.11 | 6.42 | 79.16% | 0 | 0% | 8.11 | 6.37 | 78.55% | 0 | 0% | 8.11 | 6.34 | 78.18% | 0 | 0% | 8.11 | 6.33 | 78.05% | 0 | 0%
GNA_152161101_Capacity | North Valley and Sierra | Sierra | AUBURN 1101 | 152161101 | Feeder | None | None | None | 19.55% | 0 | 0% | 10.69 | 2.09 | 19.55% | 0 | 0% | 10.69 | 2.08 | 19.46% | 0 | 0% | 10.69 | 2.04 | 19.08% | 0 | 0% | 10.69 | 2.02 | 18.9% | 0 | 0% | 10.69 | 2.01 | 18.8% | 0 | 0%
GNA_152161102_Capacity | North Valley and Sierra | Sierra | AUBURN 1102 | 152161102 | Feeder | None | None | None | 39.1% | 0 | 0% | 10.69 | 4.18 | 39.1% | 0 | 0% | 10.69 | 4.17 | 39.01% | 0 | 0% | 10.69 | 4.15 | 38.82% | 0 | 0% | 10.69 | 4.12 | 38.54% | 0 | 0% | 10.69 | 4.11 | 38.45% | 0 | 0%
GNA_1527002_Capacity | North Valley and Sierra | Sierra | BELL BANK 2 | 1527002 | Bank | None | None | None | 82.59% | 0 | 0% | 29.7 | 24.53 | 82.59% | 0 | 0% | 29.7 | 24.41 | 82.19% | 0 | 0% | 29.7 | 24.31 | 81.85% | 0 | 0% | 29.7 | 24.32 | 81.89% | 0 | 0% | 29.7 | 24.33 | 81.92% | 0 | 0%
GNA_152701107_Capacity | North Valley and Sierra | Sierra | BELL 1107 | 152701107 | Feeder | None | None | None | 82.86% | 0 | 0% | 12.25 | 10.15 | 82.86% | 0 | 0% | 12.25 | 10.11 | 82.53% | 0 | 0% | 12.25 | 10.06 | 82.12% | 0 | 0% | 12.25 | 10.1 | 82.45% | 0 | 0% | 12.25 | 10.11 | 82.53% | 0 | 0%
GNA_152701108_Capacity | North Valley and Sierra | Sierra | BELL 1108 | 152701108 | Feeder | None | None | None | 97.69% | 0 | 0% | 14.26 | 13.93 | 97.69% | 0 | 0% | 14.26 | 13.84 | 97.05% | 0 | 0% | 14.26 | 13.79 | 96.7% | 0 | 0% | 14.26 | 13.77 | 96.56% | 0 | 0% | 14.26 | 13.76 | 96.49% | 0 | 0%
GNA_1527003_Capacity | North Valley and Sierra | Sierra | BELL BANK 3 | 1527003 | Bank | None | None | None | 63.61% | 0 | 0% | 25.5 | 16.04 | 62.9% | 0 | 0% | 25.5 | 16.03 | 62.86% | 0 | 0% | 25.5 | 16.03 | 62.86% | 0 | 0% | 25.5 | 16.13 | 63.25% | 0 | 0% | 25.5 | 16.22 | 63.61% | 0 | 0%
GNA_152701109_Capacity | North Valley and Sierra | Sierra | BELL 1109 | 152701109 | Feeder | None | None | None | 52.91% | 0 | 0% | 12.19 | 6.14 | 50.37% | 0 | 0% | 12.19 | 6.19 | 50.78% | 0 | 0% | 12.19 | 6.25 | 51.27% | 0 | 0% | 12.19 | 6.33 | 51.93% | 0 | 0% | 12.19 | 6.45 | 52.91% | 0 | 0%
GNA_152701110_Capacity | North Valley and Sierra | Sierra | BELL 1110 | 152701110 | Feeder | None | None | None | 87.61% | 0 | 0% | 12.19 | 10.68 | 87.61% | 0 | 0% | 12.19 | 10.62 | 87.12% | 0 | 0% | 12.19 | 10.55 | 86.55% | 0 | 0% | 12.19 | 10.56 | 86.63% | 0 | 0% | 12.19 | 10.56 | 86.63% | 0 | 0%
GNA_1525301_Capacity | North Valley and Sierra | Sierra | FLINT BANK 1 | 1525301 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152531101_Capacity | North Valley and Sierra | Sierra | FLINT 1101 | 152531101 | Feeder | None | None | None | 76.86% | 0 | 0% | 14.26 | 10.92 | 76.58% | 0 | 0% | 14.26 | 10.89 | 76.37% | 0 | 0% | 14.26 | 10.86 | 76.16% | 0 | 0% | 14.26 | 10.9 | 76.44% | 0 | 0% | 14.26 | 10.96 | 76.86% | 0 | 0%
GNA_1522401_Capacity | North Valley and Sierra | Sierra | HALSEY BANK 1 | 1522401 | Bank | None | None | None | 92.1% | 0 | 0% | 18.47 | 17.01 | 92.1% | 0 | 0% | 18.47 | 16.94 | 91.72% | 0 | 0% | 18.47 | 16.92 | 91.61% | 0 | 0% | 18.47 | 16.9 | 91.5% | 0 | 0% | 18.47 | 16.96 | 91.82% | 0 | 0%
GNA_152241101_Capacity | North Valley and Sierra | Sierra | HALSEY 1101 | 152241101 | Feeder | None | None | None | 72.32% | 0 | 0% | 11.67 | 8.44 | 72.32% | 0 | 0% | 11.67 | 8.4 | 71.98% | 0 | 0% | 11.67 | 8.39 | 71.89% | 0 | 0% | 11.67 | 8.39 | 71.89% | 0 | 0% | 11.67 | 8.43 | 72.24% | 0 | 0%
GNA_152241102_Capacity | North Valley and Sierra | Sierra | HALSEY 1102 | 152241102 | Feeder | None | None | None | 82.26% | 0 | 0% | 11.67 | 9.6 | 82.26% | 0 | 0% | 11.67 | 9.55 | 81.83% | 0 | 0% | 11.67 | 9.54 | 81.75% | 0 | 0% | 11.67 | 9.51 | 81.49% | 0 | 0% | 11.67 | 9.52 | 81.58% | 0 | 0%
GNA_1524602_Capacity | North Valley and Sierra | Sierra | PLACER BANK 2 | 1524602 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152461101_Capacity | North Valley and Sierra | Sierra | PLACER 1101 | 152461101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152461102_Capacity | North Valley and Sierra | Sierra | PLACER 1102 | 152461102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152271103_Capacity | North Valley and Sierra | Sierra | WISE 1103 | 152271103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152271101_Capacity | North Valley and Sierra | Sierra | WISE 1101 | 152271101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152271102_Capacity | North Valley and Sierra | Sierra | WISE 1102 | 152271102 | Feeder | None | None | None | 55.22% | 0 | 0% | 15.12 | 8.25 | 54.56% | 0 | 0% | 15.12 | 8.25 | 54.56% | 0 | 0% | 15.12 | 8.24 | 54.5% | 0 | 0% | 15.12 | 8.27 | 54.7% | 0 | 0% | 15.12 | 8.35 | 55.22% | 0 | 0%
GNA_152461103_Capacity | North Valley and Sierra | Sierra | PLACER 1103 | 152461103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1524603_Capacity | North Valley and Sierra | Sierra | PLACER BANK 3 | 1524603 | Bank | None | None | None | 74.62% | 0 | 0% | 15.84 | 11.82 | 74.62% | 0 | 0% | 15.84 | 11.77 | 74.31% | 0 | 0% | 15.84 | 11.74 | 74.12% | 0 | 0% | 15.84 | 11.74 | 74.12% | 0 | 0% | 15.84 | 11.71 | 73.93% | 0 | 0%
GNA_152461104_Capacity | North Valley and Sierra | Sierra | PLACER 1104 | 152461104 | Feeder | None | None | None | 92.28% | 0 | 0% | 12.83 | 11.84 | 92.28% | 0 | 0% | 12.83 | 11.78 | 91.82% | 0 | 0% | 12.83 | 11.76 | 91.66% | 0 | 0% | 12.83 | 11.75 | 91.58% | 0 | 0% | 12.83 | 11.73 | 91.43% | 0 | 0%
GNA_1524901_Capacity | North Valley and Sierra | Sierra | WEIMAR BANK 1 | 1524901 | Bank | None | None | None | 89.57% | 0 | 0% | 8.82 | 7.9 | 89.57% | 0 | 0% | 8.82 | 7.83 | 88.78% | 0 | 0% | 8.82 | 7.79 | 88.32% | 0 | 0% | 8.82 | 7.79 | 88.32% | 0 | 0% | 8.82 | 7.83 | 88.78% | 0 | 0%
GNA_152491101_Capacity | North Valley and Sierra | Sierra | WEIMAR 1101 | 152491101 | Feeder | None | None | None | 63.38% | 0 | 0% | 10.05 | 6.37 | 63.38% | 0 | 0% | 10.05 | 6.31 | 62.79% | 0 | 0% | 10.05 | 6.29 | 62.59% | 0 | 0% | 10.05 | 6.29 | 62.59% | 0 | 0% | 10.05 | 6.33 | 62.99% | 0 | 0%
GNA_152491102_Capacity | North Valley and Sierra | Sierra | WEIMAR 1102 | 152491102 | Feeder | None | None | None | 28.59% | 0 | 0% | 10.46 | 2.99 | 28.59% | 0 | 0% | 10.46 | 2.98 | 28.49% | 0 | 0% | 10.46 | 2.96 | 28.3% | 0 | 0% | 10.46 | 2.96 | 28.3% | 0 | 0% | 10.46 | 2.97 | 28.39% | 0 | 0%
GNA_1522001_Capacity | North Valley and Sierra | Sierra | PIKE CITY BANK 1 | 1522001 | Bank | None | None | None | 21.47% | 0 | 0% | 3.4 | 0.71 | 20.88% | 0 | 0% | 3.4 | 0.7 | 20.59% | 0 | 0% | 3.4 | 0.71 | 20.88% | 0 | 0% | 3.4 | 0.71 | 20.88% | 0 | 0% | 3.4 | 0.73 | 21.47% | 0 | 0%
GNA_152201101_Capacity | North Valley and Sierra | Sierra | PIKE CITY 1101 | 152201101 | Feeder | None | None | None | 25.08% | 0 | 0% | 3.19 | 0.79 | 24.76% | 0 | 0% | 3.19 | 0.78 | 24.45% | 0 | 0% | 3.19 | 0.79 | 24.76% | 0 | 0% | 3.19 | 0.78 | 24.45% | 0 | 0% | 3.19 | 0.8 | 25.08% | 0 | 0%
GNA_152201102_Capacity | North Valley and Sierra | Sierra | PIKE CITY 1102 | 152201102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1525801_Capacity | North Valley and Sierra | Sierra | DEL MAR BANK 1 | 1525801 | Bank | None | None | None | 48.48% | 0 | 0% | 15.84 | 6.92 | 43.69% | 0 | 0% | 15.84 | 7.1 | 44.82% | 0 | 0% | 15.84 | 7.29 | 46.02% | 0 | 0% | 15.84 | 7.48 | 47.22% | 0 | 0% | 15.84 | 7.68 | 48.48% | 0 | 0%
GNA_152581103_Capacity | North Valley and Sierra | Sierra | DEL MAR 1103 | 152581103 | Feeder | None | None | None | 49.81% | 0 | 0% | 10.46 | 4.86 | 46.46% | 0 | 0% | 10.46 | 4.94 | 47.23% | 0 | 0% | 10.46 | 5.03 | 48.09% | 0 | 0% | 10.46 | 5.11 | 48.85% | 0 | 0% | 10.46 | 5.21 | 49.81% | 0 | 0%
GNA_152581104_Capacity | North Valley and Sierra | Sierra | DEL MAR 1104 | 152581104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1525802_Capacity | North Valley and Sierra | Sierra | DEL MAR BANK 2 | 1525802 | Bank | None | None | None | 97.95% | 0 | 0% | 29.7 | 28.49 | 95.93% | 0 | 0% | 29.7 | 28.51 | 95.99% | 0 | 0% | 29.7 | 28.63 | 96.4% | 0 | 0% | 29.7 | 28.81 | 97% | 0 | 0% | 29.7 | 29.09 | 97.95% | 0 | 0%
GNA_152582105_Capacity | North Valley and Sierra | Sierra | DEL MAR 2105 | 152582105 | Feeder | None | None | None | 57.78% | 0 | 0% | 26.22 | 15.11 | 57.63% | 0 | 0% | 26.22 | 14.98 | 57.13% | 0 | 0% | 26.22 | 14.97 | 57.09% | 0 | 0% | 26.22 | 15.02 | 57.28% | 0 | 0% | 26.22 | 15.15 | 57.78% | 0 | 0%
GNA_152582106_Capacity | North Valley and Sierra | Sierra | DEL MAR 2106 | 152582106 | Feeder | None | None | None | 69.6% | 0 | 0% | 21.22 | 14.24 | 67.11% | 0 | 0% | 21.22 | 14.32 | 67.48% | 0 | 0% | 21.22 | 14.46 | 68.14% | 0 | 0% | 21.22 | 14.6 | 68.8% | 0 | 0% | 21.22 | 14.77 | 69.6% | 0 | 0%
GNA_1525803_Capacity | North Valley and Sierra | Sierra | DEL MAR BANK 3 | 1525803 | Bank | None | None | None | 85.43% | 0 | 0% | 44.55 | 37.14 | 83.37% | 0 | 0% | 44.55 | 37.15 | 83.39% | 0 | 0% | 44.55 | 37.24 | 83.59% | 0 | 0% | 44.55 | 37.61 | 84.42% | 0 | 0% | 44.55 | 38.06 | 85.43% | 0 | 0%
GNA_152582109_Capacity | North Valley and Sierra | Sierra | DEL MAR 2109 | 152582109 | Feeder | None | None | None | 89.59% | 0 | 0% | 18.63 | 16.19 | 86.9% | 0 | 0% | 18.63 | 16.21 | 87.01% | 0 | 0% | 18.63 | 16.26 | 87.28% | 0 | 0% | 18.63 | 16.46 | 88.35% | 0 | 0% | 18.63 | 16.69 | 89.59% | 0 | 0%
GNA_152582110_Capacity | North Valley and Sierra | Sierra | DEL MAR 2110 | 152582110 | Feeder | None | None | None | 96.31% | 0 | 0% | 21.41 | 20.37 | 95.14% | 0 | 0% | 21.41 | 20.19 | 94.3% | 0 | 0% | 21.41 | 20.23 | 94.49% | 0 | 0% | 21.41 | 20.41 | 95.33% | 0 | 0% | 21.41 | 20.62 | 96.31% | 0 | 0%
GNA_1525601_Capacity | North Valley and Sierra | Sierra | PENRYN BANK 1 | 1525601 | Bank | None | None | None | 45.52% | 0 | 0% | 15.84 | 7.15 | 45.14% | 0 | 0% | 15.84 | 7.15 | 45.14% | 0 | 0% | 15.84 | 7.15 | 45.14% | 0 | 0% | 15.84 | 7.16 | 45.2% | 0 | 0% | 15.84 | 7.21 | 45.52% | 0 | 0%
GNA_152561103_Capacity | North Valley and Sierra | Sierra | PENRYN 1103 | 152561103 | Feeder | None | None | None | 59.23% | 0 | 0% | 12.19 | 7.16 | 58.74% | 0 | 0% | 12.19 | 7.15 | 58.65% | 0 | 0% | 12.19 | 7.15 | 58.65% | 0 | 0% | 12.19 | 7.17 | 58.82% | 0 | 0% | 12.19 | 7.22 | 59.23% | 0 | 0%
GNA_1525602_Capacity | North Valley and Sierra | Sierra | PENRYN BANK 2 | 1525602 | Bank | None | None | None | 76.04% | 0 | 0% | 44.53 | 31.46 | 70.65% | 0 | 0% | 44.53 | 31.6 | 70.96% | 0 | 0% | 44.53 | 32.68 | 73.39% | 0 | 0% | 44.53 | 33.39 | 74.98% | 0 | 0% | 44.53 | 33.86 | 76.04% | 0 | 0%
GNA_152561105_Capacity | North Valley and Sierra | Sierra | PENRYN 1105 | 152561105 | Feeder | None | None | None | 68.65% | 0 | 0% | 15.12 | 8.68 | 57.41% | 0 | 0% | 15.12 | 8.72 | 57.67% | 0 | 0% | 15.12 | 9.77 | 64.62% | 0 | 0% | 15.12 | 10.27 | 67.92% | 0 | 0% | 15.12 | 10.38 | 68.65% | 0 | 0%
GNA_152561106_Capacity | North Valley and Sierra | Sierra | PENRYN 1106 | 152561106 | Feeder | None | None | None | 82.35% | 0 | 0% | 13.6 | 10.78 | 79.26% | 0 | 0% | 13.6 | 10.87 | 79.93% | 0 | 0% | 13.6 | 10.94 | 80.44% | 0 | 0% | 13.6 | 11.06 | 81.32% | 0 | 0% | 13.6 | 11.2 | 82.35% | 0 | 0%
GNA_152561107_Capacity | North Valley and Sierra | Sierra | PENRYN 1107 | 152561107 | Feeder | None | None | None | 92.79% | 0 | 0% | 15.12 | 13.55 | 89.62% | 0 | 0% | 15.12 | 13.63 | 90.15% | 0 | 0% | 15.12 | 13.71 | 90.67% | 0 | 0% | 15.12 | 13.84 | 91.53% | 0 | 0% | 15.12 | 14.03 | 92.79% | 0 | 0%
GNA_1524401_Capacity | North Valley and Sierra | Sierra | PLEASANT GROVE BANK 1 | 1524401 | Bank | None | None | None | 94.39% | 0 | 0% | 44.55 | 41.24 | 92.57% | 0 | 0% | 44.55 | 41.33 | 92.77% | 0 | 0% | 44.55 | 41.42 | 92.97% | 0 | 0% | 44.55 | 41.67 | 93.54% | 0 | 0% | 44.55 | 42.05 | 94.39% | 0 | 0%
GNA_152442103_Capacity | North Valley and Sierra | Sierra | PLEASANT GROVE 2103 | 152442103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152442104_Capacity | North Valley and Sierra | Sierra | PLEASANT GROVE 2104 | 152442104 | Feeder | Demand Growth | Capacity | 2023 | 112.9% | 3.03 | 12.86% | 23.56 | 26.17 | 111.1% | 2.61 | 11.08% | 23.56 | 26.19 | 111.2% | 2.63 | 11.16% | 23.56 | 26.19 | 111.2% | 2.63 | 11.16% | 23.56 | 26.37 | 111.9% | 2.81 | 11.93% | 23.56 | 26.59 | 112.9% | 3.03 | 12.86%
GNA_1524402_Capacity | North Valley and Sierra | Sierra | PLEASANT GROVE BANK 2 | 1524402 | Bank | None | None | None | 82.24% | 0 | 0% | 44.55 | 36.64 | 82.24% | 0 | 0% | 44.55 | 36.43 | 81.77% | 0 | 0% | 44.55 | 36.33 | 81.55% | 0 | 0% | 44.55 | 36.27 | 81.41% | 0 | 0% | 44.55 | 36.26 | 81.39% | 0 | 0%
GNA_152442107_Capacity | North Valley and Sierra | Sierra | PLEASANT GROVE 2107 | 152442107 | Feeder | None | None | None | 88.77% | 0 | 0% | 21.11 | 18.74 | 88.77% | 0 | 0% | 21.11 | 18.58 | 88.02% | 0 | 0% | 21.11 | 18.49 | 87.59% | 0 | 0% | 21.11 | 18.39 | 87.12% | 0 | 0% | 21.11 | 18.33 | 86.83% | 0 | 0%
GNA_152442108_Capacity | North Valley and Sierra | Sierra | PLEASANT GROVE 2108 | 152442108 | Feeder | None | None | None | 95.14% | 0 | 0% | 21.41 | 19.96 | 93.23% | 0 | 0% | 21.41 | 19.97 | 93.27% | 0 | 0% | 21.41 | 20.05 | 93.65% | 0 | 0% | 21.41 | 20.2 | 94.35% | 0 | 0% | 21.41 | 20.37 | 95.14% | 0 | 0%
GNA_1524403_Capacity | North Valley and Sierra | Sierra | PLEASANT GROVE BANK 3 | 1524403 | Bank | None | None | None | 89.66% | 0 | 0% | 44.6 | 39.11 | 87.69% | 0 | 0% | 44.6 | 39.19 | 87.87% | 0 | 0% | 44.6 | 39.32 | 88.16% | 0 | 0% | 44.6 | 39.64 | 88.88% | 0 | 0% | 44.6 | 39.99 | 89.66% | 0 | 0%
GNA_152442109_Capacity | North Valley and Sierra | Sierra | PLEASANT GROVE 2109 | 152442109 | Feeder | None | None | None | 91.47% | 0 | 0% | 18.63 | 16.74 | 89.86% | 0 | 0% | 18.63 | 16.66 | 89.43% | 0 | 0% | 18.63 | 16.64 | 89.32% | 0 | 0% | 18.63 | 16.84 | 90.39% | 0 | 0% | 18.63 | 17.04 | 91.47% | 0 | 0%
GNA_152442110_Capacity | North Valley and Sierra | Sierra | PLEASANT GROVE 2110 | 152442110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1520601_Capacity | North Valley and Sierra | Sierra | ROCKLIN BANK 1 | 1520601 | Bank | Demand Growth | Capacity | 2023 | 109.6% | 1.52 | 9.596% | 15.84 | 16.78 | 105.9% | 0.94 | 5.934% | 15.84 | 16.83 | 106.2% | 0.99 | 6.25% | 15.84 | 16.95 | 107% | 1.11 | 7.008% | 15.84 | 17.13 | 108.1% | 1.29 | 8.144% | 15.84 | 17.36 | 109.6% | 1.52 | 9.596%
GNA_152061101_Capacity | North Valley and Sierra | Sierra | ROCKLIN 1101 | 152061101 | Feeder | None | None | None | 55.3% | 0 | 0% | 10.76 | 5.83 | 54.18% | 0 | 0% | 10.76 | 5.83 | 54.18% | 0 | 0% | 10.76 | 5.85 | 54.37% | 0 | 0% | 10.76 | 5.87 | 54.55% | 0 | 0% | 10.76 | 5.95 | 55.3% | 0 | 0%
GNA_152061102_Capacity | North Valley and Sierra | Sierra | ROCKLIN 1102 | 152061102 | Feeder | None | None | None | 91.49% | 0 | 0% | 12.1 | 10.69 | 88.35% | 0 | 0% | 12.1 | 10.76 | 88.93% | 0 | 0% | 12.1 | 10.84 | 89.59% | 0 | 0% | 12.1 | 10.96 | 90.58% | 0 | 0% | 12.1 | 11.07 | 91.49% | 0 | 0%
GNA_1520602_Capacity | North Valley and Sierra | Sierra | ROCKLIN BANK 2 | 1520602 | Bank | Demand Growth | Capacity | 2023 | 107.8% | 0.77 | 7.794% | 9.88 | 10.39 | 105.2% | 0.51 | 5.162% | 9.88 | 10.42 | 105.5% | 0.54 | 5.466% | 9.88 | 10.48 | 106.1% | 0.6 | 6.073% | 9.88 | 10.55 | 106.8% | 0.67 | 6.781% | 9.88 | 10.65 | 107.8% | 0.77 | 7.794%
GNA_152061103_Capacity | North Valley and Sierra | Sierra | ROCKLIN 1103 | 152061103 | Feeder | None | None | None | 60.69% | 0 | 0% | 10.76 | 6.53 | 60.69% | 0 | 0% | 10.76 | 6.48 | 60.22% | 0 | 0% | 10.76 | 6.44 | 59.85% | 0 | 0% | 10.76 | 6.43 | 59.76% | 0 | 0% | 10.76 | 6.43 | 59.76% | 0 | 0%
GNA_152061104_Capacity | North Valley and Sierra | Sierra | ROCKLIN 1104 | 152061104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1521101_Capacity | North Valley and Sierra | Sierra | BARRY BANK 1 | 1521101 | Bank | None | None | None | 96.77% | 0 | 0% | 4.95 | 4.74 | 95.76% | 0 | 0% | 4.95 | 4.74 | 95.76% | 0 | 0% | 4.95 | 4.75 | 95.96% | 0 | 0% | 4.95 | 4.76 | 96.16% | 0 | 0% | 4.95 | 4.79 | 96.77% | 0 | 0%
GNA_152111101_Capacity | North Valley and Sierra | Sierra | BARRY 1101 | 152111101 | Feeder | None | None | None | 26.37% | 0 | 0% | 6.41 | 1.68 | 26.21% | 0 | 0% | 6.41 | 1.67 | 26.05% | 0 | 0% | 6.41 | 1.67 | 26.05% | 0 | 0% | 6.41 | 1.68 | 26.21% | 0 | 0% | 6.41 | 1.69 | 26.37% | 0 | 0%
GNA_152111102_Capacity | North Valley and Sierra | Sierra | BARRY 1102 | 152111102 | Feeder | None | None | None | 29.35% | 0 | 0% | 4.94 | 1.42 | 28.74% | 0 | 0% | 4.94 | 1.42 | 28.74% | 0 | 0% | 4.94 | 1.43 | 28.95% | 0 | 0% | 4.94 | 1.43 | 28.95% | 0 | 0% | 4.94 | 1.45 | 29.35% | 0 | 0%
GNA_152111103_Capacity | North Valley and Sierra | Sierra | BARRY 1103 | 152111103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1537801_Capacity | North Valley and Sierra | Sierra | BOGUE BANK 1 | 1537801 | Bank | None | None | None | 88% | 0 | 0% | 44.6 | 39.24 | 87.98% | 0 | 0% | 44.6 | 38.78 | 86.95% | 0 | 0% | 44.6 | 38.8 | 87% | 0 | 0% | 44.6 | 38.17 | 85.58% | 0 | 0% | 44.6 | 39.25 | 88% | 0 | 0%
GNA_153781102_Capacity | North Valley and Sierra | Sierra | BOGUE 1102 | 153781102 | Feeder | None | None | None | 89.23% | 0 | 0% | 15.14 | 13.51 | 89.23% | 0 | 0% | 15.14 | 13.43 | 88.71% | 0 | 0% | 15.14 | 13.37 | 88.31% | 0 | 0% | 15.14 | 13.35 | 88.18% | 0 | 0% | 15.14 | 13.41 | 88.57% | 0 | 0%
GNA_153781103_Capacity | North Valley and Sierra | Sierra | BOGUE 1103 | 153781103 | Feeder | None | None | None | 96.74% | 0 | 0% | 13.21 | 12.78 | 96.74% | 0 | 0% | 13.21 | 12.38 | 93.72% | 0 | 0% | 13.21 | 12.42 | 94.02% | 0 | 0% | 13.21 | 11.73 | 88.8% | 0 | 0% | 13.21 | 12.32 | 93.26% | 0 | 0%
GNA_153781104_Capacity | North Valley and Sierra | Sierra | BOGUE 1104 | 153781104 | Feeder | Demand Growth | Capacity | 2024 | 104.6% | 0.61 | 4.618% | 13.21 | 13.21 | 100% | 0 | 0% | 13.21 | 13.29 | 100.6% | 0.08 | 0.6056% | 13.21 | 13.4 | 101.4% | 0.19 | 1.438% | 13.21 | 13.58 | 102.8% | 0.37 | 2.801% | 13.21 | 13.82 | 104.6% | 0.61 | 4.618%
GNA_1537802_Capacity | North Valley and Sierra | Sierra | BOGUE BANK 2 | 1537802 | Bank | None | None | None | 82% | 0 | 0% | 44.6 | 35.04 | 78.57% | 0 | 0% | 44.6 | 35.33 | 79.22% | 0 | 0% | 44.6 | 35.63 | 79.89% | 0 | 0% | 44.6 | 36.01 | 80.74% | 0 | 0% | 44.6 | 36.57 | 82% | 0 | 0%
GNA_153781105_Capacity | North Valley and Sierra | Sierra | BOGUE 1105 | 153781105 | Feeder | Demand Growth | Capacity | 2023 | 109.2% | 1.31 | 9.187% | 14.26 | 14.98 | 105% | 0.72 | 5.049% | 14.26 | 15.07 | 105.7% | 0.81 | 5.68% | 14.26 | 15.18 | 106.5% | 0.92 | 6.452% | 14.26 | 15.33 | 107.5% | 1.07 | 7.504% | 14.26 | 15.57 | 109.2% | 1.31 | 9.187%
GNA_153781106_Capacity | North Valley and Sierra | Sierra | BOGUE 1106 | 153781106 | Feeder | None | None | None | 88.27% | 0 | 0% | 12.19 | 10.23 | 83.92% | 0 | 0% | 12.19 | 10.33 | 84.74% | 0 | 0% | 12.19 | 10.41 | 85.4% | 0 | 0% | 12.19 | 10.55 | 86.55% | 0 | 0% | 12.19 | 10.76 | 88.27% | 0 | 0%
GNA_153781107_Capacity | North Valley and Sierra | Sierra | BOGUE 1107 | 153781107 | Feeder | None | None | None | 86.58% | 0 | 0% | 11.33 | 9.44 | 83.32% | 0 | 0% | 11.33 | 9.54 | 84.2% | 0 | 0% | 11.33 | 9.63 | 85% | 0 | 0% | 11.33 | 9.71 | 85.7% | 0 | 0% | 11.33 | 9.81 | 86.58% | 0 | 0%
GNA_1528501_Capacity | North Valley and Sierra | Sierra | HARTER BANK 1 | 1528501 | Bank | None | None | None | 67.71% | 0 | 0% | 29.7 | 19.06 | 64.18% | 0 | 0% | 29.7 | 19.85 | 66.84% | 0 | 0% | 29.7 | 19.93 | 67.1% | 0 | 0% | 29.7 | 20 | 67.34% | 0 | 0% | 29.7 | 20.11 | 67.71% | 0 | 0%
GNA_152851102_Capacity | North Valley and Sierra | Sierra | HARTER 1102 | 152851102 | Feeder | None | None | None | 77.28% | 0 | 0% | 13.6 | 10.09 | 74.19% | 0 | 0% | 13.6 | 10.15 | 74.63% | 0 | 0% | 13.6 | 10.26 | 75.44% | 0 | 0% | 13.6 | 10.38 | 76.32% | 0 | 0% | 13.6 | 10.51 | 77.28% | 0 | 0%
GNA_152851104_Capacity | North Valley and Sierra | Sierra | HARTER 1104 | 152851104 | Feeder | None | None | None | 73.9% | 0 | 0% | 13.6 | 9.32 | 68.53% | 0 | 0% | 13.6 | 10.05 | 73.9% | 0 | 0% | 13.6 | 10.02 | 73.68% | 0 | 0% | 13.6 | 9.99 | 73.46% | 0 | 0% | 13.6 | 10 | 73.53% | 0 | 0%
GNA_1528502_Capacity | North Valley and Sierra | Sierra | HARTER BANK 2 | 1528502 | Bank | None | None | None | 94.81% | 0 | 0% | 29.7 | 25.34 | 85.32% | 0 | 0% | 29.7 | 25.96 | 87.41% | 0 | 0% | 29.7 | 26.2 | 88.22% | 0 | 0% | 29.7 | 27.78 | 93.54% | 0 | 0% | 29.7 | 28.16 | 94.81% | 0 | 0%
GNA_152851105_Capacity | North Valley and Sierra | Sierra | HARTER 1105 | 152851105 | Feeder | None | None | None | 88.26% | 0 | 0% | 11.67 | 9.5 | 81.41% | 0 | 0% | 11.67 | 9.9 | 84.83% | 0 | 0% | 11.67 | 10.01 | 85.78% | 0 | 0% | 11.67 | 10.15 | 86.98% | 0 | 0% | 11.67 | 10.3 | 88.26% | 0 | 0%
GNA_152851106_Capacity | North Valley and Sierra | Sierra | HARTER 1106 | 152851106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152851107_Capacity | North Valley and Sierra | Sierra | HARTER 1107 | 152851107 | Feeder | None | None | None | 71.47% | 0 | 0% | 13.6 | 8.18 | 60.15% | 0 | 0% | 13.6 | 8.22 | 60.44% | 0 | 0% | 13.6 | 8.29 | 60.96% | 0 | 0% | 13.6 | 9.64 | 70.88% | 0 | 0% | 13.6 | 9.72 | 71.47% | 0 | 0%
GNA_1537701_Capacity | North Valley and Sierra | Sierra | LIVE OAK BANK 1 | 1537701 | Bank | None | None | None | 97.69% | 0 | 0% | 10.4 | 9.16 | 88.08% | 0 | 0% | 10.4 | 9.28 | 89.23% | 0 | 0% | 10.4 | 9.27 | 89.13% | 0 | 0% | 10.4 | 9.59 | 92.21% | 0 | 0% | 10.4 | 10.16 | 97.69% | 0 | 0%
GNA_153771101_Capacity | North Valley and Sierra | Sierra | LIVE OAK 1101 | 153771101 | Feeder | None | None | None | 54.31% | 0 | 0% | 12.19 | 5.72 | 46.92% | 0 | 0% | 12.19 | 5.84 | 47.91% | 0 | 0% | 12.19 | 5.82 | 47.74% | 0 | 0% | 12.19 | 6.1 | 50.04% | 0 | 0% | 12.19 | 6.62 | 54.31% | 0 | 0%
GNA_153771102_Capacity | North Valley and Sierra | Sierra | LIVE OAK 1102 | 153771102 | Feeder | None | None | None | 33.39% | 0 | 0% | 12.19 | 4.07 | 33.39% | 0 | 0% | 12.19 | 4.05 | 33.22% | 0 | 0% | 12.19 | 4.04 | 33.14% | 0 | 0% | 12.19 | 4.03 | 33.06% | 0 | 0% | 12.19 | 4.01 | 32.9% | 0 | 0%
GNA_1537702_Capacity | North Valley and Sierra | Sierra | LIVE OAK BANK 2 | 1537702 | Bank | None | None | None | 73.67% | 0 | 0% | 15.8 | 11.25 | 71.2% | 0 | 0% | 15.8 | 11.32 | 71.65% | 0 | 0% | 15.8 | 11.42 | 72.28% | 0 | 0% | 15.8 | 11.52 | 72.91% | 0 | 0% | 15.8 | 11.64 | 73.67% | 0 | 0%
GNA_153771104_Capacity | North Valley and Sierra | Sierra | LIVE OAK 1104 | 153771104 | Feeder | None | None | None | 89.87% | 0 | 0% | 12.83 | 11.15 | 86.91% | 0 | 0% | 12.83 | 11.22 | 87.45% | 0 | 0% | 12.83 | 11.31 | 88.15% | 0 | 0% | 12.83 | 11.41 | 88.93% | 0 | 0% | 12.83 | 11.53 | 89.87% | 0 | 0%
GNA_1537501_Capacity | North Valley and Sierra | Sierra | PEASE BANK 1 | 1537501 | Bank | None | None | None | 93.37% | 0 | 0% | 10.4 | 9.33 | 89.71% | 0 | 0% | 10.4 | 9.38 | 90.19% | 0 | 0% | 10.4 | 9.45 | 90.87% | 0 | 0% | 10.4 | 9.56 | 91.92% | 0 | 0% | 10.4 | 9.71 | 93.37% | 0 | 0%
GNA_153751101_Capacity | North Valley and Sierra | Sierra | PEASE 1101 | 153751101 | Feeder | None | None | None | 74.85% | 0 | 0% | 11.33 | 8.11 | 71.58% | 0 | 0% | 11.33 | 8.17 | 72.11% | 0 | 0% | 11.33 | 8.24 | 72.73% | 0 | 0% | 11.33 | 8.33 | 73.52% | 0 | 0% | 11.33 | 8.48 | 74.85% | 0 | 0%
GNA_153751102_Capacity | North Valley and Sierra | Sierra | PEASE 1102 | 153751102 | Feeder | None | None | None | 9.353% | 0 | 0% | 12.83 | 1.18 | 9.197% | 0 | 0% | 12.83 | 1.18 | 9.197% | 0 | 0% | 12.83 | 1.18 | 9.197% | 0 | 0% | 12.83 | 1.2 | 9.353% | 0 | 0% | 12.83 | 1.2 | 9.353% | 0 | 0%
GNA_1537503_Capacity | North Valley and Sierra | Sierra | PEASE BANK 3 | 1537503 | Bank | None | None | None | 90.95% | 0 | 0% | 26.4 | 23.52 | 89.09% | 0 | 0% | 26.4 | 23.58 | 89.32% | 0 | 0% | 26.4 | 23.66 | 89.62% | 0 | 0% | 26.4 | 23.82 | 90.23% | 0 | 0% | 26.4 | 24.01 | 90.95% | 0 | 0%
GNA_153751103_Capacity | North Valley and Sierra | Sierra | PEASE 1103 | 153751103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_153751104_Capacity | North Valley and Sierra | Sierra | PEASE 1104 | 153751104 | Feeder | None | None | None | 93.76% | 0 | 0% | 12.83 | 11.57 | 90.18% | 0 | 0% | 12.83 | 11.65 | 90.8% | 0 | 0% | 12.83 | 11.73 | 91.43% | 0 | 0% | 12.83 | 11.87 | 92.52% | 0 | 0% | 12.83 | 12.03 | 93.76% | 0 | 0%
GNA_1537504_Capacity | North Valley and Sierra | Sierra | PEASE BANK 4 | 1537504 | Bank | None | None | None | 97.02% | 0 | 0% | 12.4 | 11.41 | 92.02% | 0 | 0% | 12.4 | 11.51 | 92.82% | 0 | 0% | 12.4 | 11.64 | 93.87% | 0 | 0% | 12.4 | 11.83 | 95.4% | 0 | 0% | 12.4 | 12.03 | 97.02% | 0 | 0%
GNA_153751105_Capacity | North Valley and Sierra | Sierra | PEASE 1105 | 153751105 | Feeder | None | None | None | 86.04% | 0 | 0% | 13.9 | 11.34 | 81.58% | 0 | 0% | 13.9 | 11.44 | 82.3% | 0 | 0% | 13.9 | 11.57 | 83.24% | 0 | 0% | 13.9 | 11.76 | 84.6% | 0 | 0% | 13.9 | 11.96 | 86.04% | 0 | 0%
GNA_1537101_Capacity | North Valley and Sierra | Sierra | TUDOR BANK 1 | 1537101 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_153711101_Capacity | North Valley and Sierra | Sierra | TUDOR 1101 | 153711101 | Feeder | None | None | None | 35.22% | 0 | 0% | 4.94 | 1.74 | 35.22% | 0 | 0% | 4.94 | 1.74 | 35.22% | 0 | 0% | 4.94 | 1.74 | 35.22% | 0 | 0% | 4.94 | 1.73 | 35.02% | 0 | 0% | 4.94 | 1.73 | 35.02% | 0 | 0%
GNA_153711102_Capacity | North Valley and Sierra | Sierra | TUDOR 1102 | 153711102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1529201_Capacity | North Valley and Sierra | Sierra | BROWNS VALLEY BANK 1 | 1529201 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_152921101_Capacity | North Valley and Sierra | Sierra | BROWNS VALLEY 1101 | 152921101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1537401_Capacity | North Valley and Sierra | Sierra | DOBBINS BANK 1 | 1537401 | Bank | None | None | None | 84.4% | 0 | 0% | 2.82 | 2.31 | 81.91% | 0 | 0% | 2.82 | 2.34 | 82.98% | 0 | 0% | 2.82 | 2.38 | 84.4% | 0 | 0% | 2.82 | 2.37 | 84.04% | 0 | 0% | 2.82 | 2.33 | 82.62% | 0 | 0%
GNA_153741101_Capacity | North Valley and Sierra | Sierra | DOBBINS 1101 | 153741101 | Feeder | None | None | None | 42.8% | 0 | 0% | 5.35 | 2.22 | 41.5% | 0 | 0% | 5.35 | 2.25 | 42.06% | 0 | 0% | 5.35 | 2.29 | 42.8% | 0 | 0% | 5.35 | 2.28 | 42.62% | 0 | 0% | 5.35 | 2.24 | 41.87% | 0 | 0%
GNA_1537901_Capacity | North Valley and Sierra | Sierra | SMARTVILLE BANK 1 | 1537901 | Bank | None | None | None | 10.32% | 0 | 0% | 11.73 | 1.2 | 10.23% | 0 | 0% | 11.73 | 1.2 | 10.23% | 0 | 0% | 11.73 | 1.2 | 10.23% | 0 | 0% | 11.73 | 1.2 | 10.23% | 0 | 0% | 11.73 | 1.21 | 10.32% | 0 | 0%
GNA_153791101_Capacity | North Valley and Sierra | Sierra | SMARTVILLE 1101 | 153791101 | Feeder | None | None | None | 33.74% | 0 | 0% | 4.06 | 1.36 | 33.5% | 0 | 0% | 4.06 | 1.36 | 33.5% | 0 | 0% | 4.06 | 1.36 | 33.5% | 0 | 0% | 4.06 | 1.36 | 33.5% | 0 | 0% | 4.06 | 1.37 | 33.74% | 0 | 0%
GNA_0431801_Capacity | North Coast | Sonoma | BELLEVUE BANK 1 | 431801 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043182103_Capacity | North Coast | Sonoma | BELLEVUE 2103 | 43182103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0431802_Capacity | North Coast | Sonoma | BELLEVUE BANK 2 | 431802 | Bank | None | None | None | 69.75% | 0 | 0% | 15.8 | 11.02 | 69.75% | 0 | 0% | 15.8 | 10.93 | 69.18% | 0 | 0% | 15.8 | 10.83 | 68.54% | 0 | 0% | 15.8 | 10.77 | 68.16% | 0 | 0% | 15.8 | 10.81 | 68.42% | 0 | 0%
GNA_043181102_Capacity | North Coast | Sonoma | BELLEVUE 1102 | 43181102 | Feeder | None | None | None | 96.14% | 0 | 0% | 12.19 | 11.72 | 96.14% | 0 | 0% | 12.19 | 11.63 | 95.41% | 0 | 0% | 12.19 | 11.54 | 94.67% | 0 | 0% | 12.19 | 11.47 | 94.09% | 0 | 0% | 12.19 | 11.51 | 94.42% | 0 | 0%
GNA_0431803_Capacity | North Coast | Sonoma | BELLEVUE BANK 3 | 431803 | Bank | None | None | None | 77.28% | 0 | 0% | 37.1 | 25.3 | 68.19% | 0 | 0% | 37.1 | 25.44 | 68.57% | 0 | 0% | 37.1 | 25.56 | 68.89% | 0 | 0% | 37.1 | 28.27 | 76.2% | 0 | 0% | 37.1 | 28.67 | 77.28% | 0 | 0%
GNA_043181104_Capacity | North Coast | Sonoma | BELLEVUE 1104 | 43181104 | Feeder | Demand Growth | Capacity | 2026 | 112.6% | 1.54 | 12.63% | 12.19 | 10.77 | 88.35% | 0 | 0% | 12.19 | 10.86 | 89.09% | 0 | 0% | 12.19 | 10.96 | 89.91% | 0 | 0% | 12.19 | 13.53 | 111% | 1.34 | 10.99% | 12.19 | 13.73 | 112.6% | 1.54 | 12.63%
GNA_0431804_Capacity | North Coast | Sonoma | BELLEVUE BANK 4 | 431804 | Bank | None | None | None | 37% | 0 | 0% | 29.7 | 10.59 | 35.66% | 0 | 0% | 29.7 | 10.58 | 35.62% | 0 | 0% | 29.7 | 10.6 | 35.69% | 0 | 0% | 29.7 | 10.76 | 36.23% | 0 | 0% | 29.7 | 10.99 | 37% | 0 | 0%
GNA_043182101_Capacity | North Coast | Sonoma | BELLEVUE 2101 | 43182101 | Feeder | None | None | None | 1.61% | 0 | 0% | 18.63 | 0.27 | 1.449% | 0 | 0% | 18.63 | 0.27 | 1.449% | 0 | 0% | 18.63 | 0.27 | 1.449% | 0 | 0% | 18.63 | 0.28 | 1.503% | 0 | 0% | 18.63 | 0.3 | 1.61% | 0 | 0%
GNA_043182105_Capacity | North Coast | Sonoma | BELLEVUE 2105 | 43182105 | Feeder | None | None | None | 57.13% | 0 | 0% | 23.56 | 13.44 | 57.05% | 0 | 0% | 23.56 | 13.39 | 56.83% | 0 | 0% | 23.56 | 13.3 | 56.45% | 0 | 0% | 23.56 | 13.34 | 56.62% | 0 | 0% | 23.56 | 13.46 | 57.13% | 0 | 0%
GNA_0422701_Capacity | North Coast | Sonoma | COTATI BANK 1 | 422701 | Bank | None | None | None | 81.57% | 0 | 0% | 15.95 | 12.34 | 77.37% | 0 | 0% | 15.95 | 12.56 | 78.75% | 0 | 0% | 15.95 | 12.71 | 79.69% | 0 | 0% | 15.95 | 12.85 | 80.56% | 0 | 0% | 15.95 | 13.01 | 81.57% | 0 | 0%
GNA_042271102_Capacity | North Coast | Sonoma | COTATI 1102 | 42271102 | Feeder | None | None | None | 84.82% | 0 | 0% | 12.19 | 9.73 | 79.82% | 0 | 0% | 12.19 | 9.94 | 81.54% | 0 | 0% | 12.19 | 10.09 | 82.77% | 0 | 0% | 12.19 | 10.21 | 83.76% | 0 | 0% | 12.19 | 10.34 | 84.82% | 0 | 0%
GNA_042271103_Capacity | North Coast | Sonoma | COTATI 1103 | 42271103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0422702_Capacity | North Coast | Sonoma | COTATI BANK 2 | 422702 | Bank | Demand Growth | Capacity | 2025 | 104% | 0.4 | 4.049% | 9.88 | 9.57 | 96.86% | 0 | 0% | 9.88 | 9.88 | 100% | 0 | 0% | 9.88 | 9.97 | 100.9% | 0.09 | 0.9109% | 9.88 | 10.07 | 101.9% | 0.19 | 1.923% | 9.88 | 10.28 | 104% | 0.4 | 4.049%
GNA_042271104_Capacity | North Coast | Sonoma | COTATI 1104 | 42271104 | Feeder | None | None | None | 65.56% | 0 | 0% | 8.13 | 4.82 | 59.29% | 0 | 0% | 8.13 | 5.14 | 63.22% | 0 | 0% | 8.13 | 5.27 | 64.82% | 0 | 0% | 8.13 | 5.26 | 64.7% | 0 | 0% | 8.13 | 5.33 | 65.56% | 0 | 0%
GNA_042271105_Capacity | North Coast | Sonoma | COTATI 1105 | 42271105 | Feeder | None | None | None | 50.67% | 0 | 0% | 10.46 | 5.04 | 48.18% | 0 | 0% | 10.46 | 5.07 | 48.47% | 0 | 0% | 10.46 | 5.09 | 48.66% | 0 | 0% | 10.46 | 5.19 | 49.62% | 0 | 0% | 10.46 | 5.3 | 50.67% | 0 | 0%
GNA_0434701_Capacity | North Coast | Sonoma | PENNGROVE BANK 1 | 434701 | Bank | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043471101_Capacity | North Coast | Sonoma | PENNGROVE 1101 | 43471101 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0428201_Capacity | North Coast | Sonoma | CLOVERDALE BANK 1 | 428201 | Bank | Demand Growth | Capacity | 2027 | 100.8% | 0.16 | 0.8155% | 19.62 | 17.76 | 90.52% | 0 | 0% | 19.62 | 17.96 | 91.54% | 0 | 0% | 19.62 | 18.14 | 92.46% | 0 | 0% | 19.62 | 18.92 | 96.43% | 0 | 0% | 19.62 | 19.78 | 100.8% | 0.16 | 0.8155%
GNA_042821101_Capacity | North Coast | Sonoma | CLOVERDALE 1101 | 42821101 | Feeder | None | None | None | 79.68% | 0 | 0% | 11.42 | 8.72 | 76.36% | 0 | 0% | 11.42 | 8.73 | 76.44% | 0 | 0% | 11.42 | 8.81 | 77.15% | 0 | 0% | 11.42 | 8.93 | 78.2% | 0 | 0% | 11.42 | 9.1 | 79.68% | 0 | 0%
GNA_042821102_Capacity | North Coast | Sonoma | CLOVERDALE 1102 | 42821102 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0428901_Capacity | North Coast | Sonoma | GEYSERVILLE BANK 1 | 428901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042891101_Capacity | North Coast | Sonoma | GEYSERVILLE 1101 | 42891101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0428902_Capacity | North Coast | Sonoma | GEYSERVILLE BANK 2 | 428902 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042891102_Capacity | North Coast | Sonoma | GEYSERVILLE 1102 | 42891102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0427501_Capacity | North Coast | Sonoma | FITCH MOUNTAIN BANK 1 | 427501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042751111_Capacity | North Coast | Sonoma | FITCH MOUNTAIN 1111 | 42751111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0427502_Capacity | North Coast | Sonoma | FITCH MOUNTAIN BANK 2 | 427502 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042751113_Capacity | North Coast | Sonoma | FITCH MOUNTAIN 1113 | 42751113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0425605_Capacity | North Coast | Sonoma | FULTON BANK 5 | 425605 | Bank | Demand Growth | Capacity | 2024 | 107% | 2.08 | 7.003% | 29.7 | 28.44 | 95.76% | 0 | 0% | 29.7 | 31.32 | 105.5% | 1.62 | 5.455% | 29.7 | 31.24 | 105.2% | 1.54 | 5.185% | 29.7 | 31.44 | 105.9% | 1.74 | 5.859% | 29.7 | 31.78 | 107% | 2.08 | 7.003%
GNA_042561101_Capacity | North Coast | Sonoma | FULTON 1101 | 42561101 | Feeder | Demand Growth | Capacity | 2024 | 112.4% | 1.51 | 12.39% | 12.19 | 11.28 | 92.53% | 0 | 0% | 12.19 | 13.42 | 110.1% | 1.23 | 10.09% | 12.19 | 13.51 | 110.8% | 1.32 | 10.83% | 12.19 | 13.61 | 111.6% | 1.42 | 11.65% | 12.19 | 13.7 | 112.4% | 1.51 | 12.39%
GNA_042561102_Capacity | North Coast | Sonoma | FULTON 1102 | 42561102 | Feeder | None | None | None | 94.01% | 0 | 0% | 12.19 | 10.15 | 83.26% | 0 | 0% | 12.19 | 10.96 | 89.91% | 0 | 0% | 12.19 | 11.06 | 90.73% | 0 | 0% | 12.19 | 11.24 | 92.21% | 0 | 0% | 12.19 | 11.46 | 94.01% | 0 | 0%
GNA_042561104_Capacity | North Coast | Sonoma | FULTON 1104 | 42561104 | Feeder | None | None | None | 82.03% | 0 | 0% | 12.19 | 10 | 82.03% | 0 | 0% | 12.19 | 9.98 | 81.87% | 0 | 0% | 12.19 | 9.95 | 81.62% | 0 | 0% | 12.19 | 9.91 | 81.3% | 0 | 0% | 12.19 | 9.89 | 81.13% | 0 | 0%
GNA_0425606_Capacity | North Coast | Sonoma | FULTON BANK 6 | 425606 | Bank | Demand Growth | Capacity | 2023 | 110.6% | 3.16 | 10.64% | 29.7 | 31.43 | 105.8% | 1.73 | 5.825% | 29.7 | 32.32 | 108.8% | 2.62 | 8.822% | 29.7 | 32.39 | 109.1% | 2.69 | 9.057% | 29.7 | 32.58 | 109.7% | 2.88 | 9.697% | 29.7 | 32.86 | 110.6% | 3.16 | 10.64%
GNA_042561105_Capacity | North Coast | Sonoma | FULTON 1105 | 42561105 | Feeder | Demand Growth | Capacity | 2023 | 121.3% | 2.63 | 21.28% | 12.36 | 13 | 105.2% | 0.64 | 5.178% | 12.36 | 14.99 | 121.3% | 2.63 | 21.28% | 12.36 | 14.91 | 120.6% | 2.55 | 20.63% | 12.36 | 14.84 | 120.1% | 2.48 | 20.06% | 12.36 | 14.87 | 120.3% | 2.51 | 20.31%
GNA_042561106_Capacity | North Coast | Sonoma | FULTON 1106 | 42561106 | Feeder | None | None | None | 59.31% | 0 | 0% | 12.19 | 7.23 | 59.31% | 0 | 0% | 12.19 | 6.28 | 51.52% | 0 | 0% | 12.19 | 6.4 | 52.5% | 0 | 0% | 12.19 | 6.53 | 53.57% | 0 | 0% | 12.19 | 6.67 | 54.72% | 0 | 0%
GNA_042561107_Capacity | North Coast | Sonoma | FULTON 1107 | 42561107 | Feeder | Demand Growth | Capacity | 2023 | 102.1% | 0.25 | 2.051% | 12.19 | 12.35 | 101.3% | 0.16 | 1.313% | 12.19 | 12.33 | 101.1% | 0.14 | 1.148% | 12.19 | 12.32 | 101.1% | 0.13 | 1.066% | 12.19 | 12.35 | 101.3% | 0.16 | 1.313% | 12.19 | 12.44 | 102.1% | 0.25 | 2.051%
GNA_0435001_Capacity | North Coast | Sonoma | WINDSOR BANK 1 | 435001 | Bank | None | None | None | 83.2% | 0 | 0% | 29.7 | 24.34 | 81.95% | 0 | 0% | 29.7 | 24.71 | 83.2% | 0 | 0% | 29.7 | 24.68 | 83.1% | 0 | 0% | 29.7 | 24.63 | 82.93% | 0 | 0% | 29.7 | 24.58 | 82.76% | 0 | 0%
GNA_043501101_Capacity | North Coast | Sonoma | WINDSOR 1101 | 43501101 | Feeder | None | None | None | 65.22% | 0 | 0% | 12.19 | 7.95 | 65.22% | 0 | 0% | 12.19 | 7.93 | 65.05% | 0 | 0% | 12.19 | 7.92 | 64.97% | 0 | 0% | 12.19 | 7.91 | 64.89% | 0 | 0% | 12.19 | 7.88 | 64.64% | 0 | 0%
GNA_043501102_Capacity | North Coast | Sonoma | WINDSOR 1102 | 43501102 | Feeder | Demand Growth | Capacity | 2023 | 115.3% | 1.87 | 15.34% | 12.19 | 14.06 | 115.3% | 1.87 | 15.34% | 12.19 | 14.06 | 115.3% | 1.87 | 15.34% | 12.19 | 14.06 | 115.3% | 1.87 | 15.34% | 12.19 | 14.05 | 115.3% | 1.86 | 15.26% | 12.19 | 14.04 | 115.2% | 1.85 | 15.18%
GNA_043501103_Capacity | North Coast | Sonoma | WINDSOR 1103 | 43501103 | Feeder | None | None | None | 49.79% | 0 | 0% | 12.19 | 5.68 | 46.6% | 0 | 0% | 12.19 | 6.07 | 49.79% | 0 | 0% | 12.19 | 6.06 | 49.71% | 0 | 0% | 12.19 | 6.03 | 49.47% | 0 | 0% | 12.19 | 6.02 | 49.38% | 0 | 0%
GNA_0434901_Capacity | North Coast | Sonoma | CORONA BANK 1 | 434901 | Bank | None | None | None | 80.94% | 0 | 0% | 29.7 | 24.04 | 80.94% | 0 | 0% | 29.7 | 23.71 | 79.83% | 0 | 0% | 29.7 | 23.44 | 78.92% | 0 | 0% | 29.7 | 23.3 | 78.45% | 0 | 0% | 29.7 | 23.41 | 78.82% | 0 | 0%
GNA_043491101_Capacity | North Coast | Sonoma | CORONA 1101 | 43491101 | Feeder | None | None | None | 68.01% | 0 | 0% | 12.19 | 8.29 | 68.01% | 0 | 0% | 12.19 | 8.17 | 67.02% | 0 | 0% | 12.19 | 8.13 | 66.69% | 0 | 0% | 12.19 | 8.17 | 67.02% | 0 | 0% | 12.19 | 8.26 | 67.76% | 0 | 0%
GNA_043491102_Capacity | North Coast | Sonoma | CORONA 1102 | 43491102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043491103_Capacity | North Coast | Sonoma | CORONA 1103 | 43491103 | Feeder | None | None | None | 66.37% | 0 | 0% | 12.19 | 7.95 | 65.22% | 0 | 0% | 12.19 | 7.9 | 64.81% | 0 | 0% | 12.19 | 7.91 | 64.89% | 0 | 0% | 12.19 | 7.98 | 65.46% | 0 | 0% | 12.19 | 8.09 | 66.37% | 0 | 0%
GNA_0433704_Capacity | North Coast | Sonoma | LAKEVILLE BANK 4 | 433704 | Bank | None | None | None | 61.7% | 0 | 0% | 24.75 | 14.85 | 60% | 0 | 0% | 24.75 | 14.77 | 59.68% | 0 | 0% | 24.75 | 14.88 | 60.12% | 0 | 0% | 24.75 | 15.08 | 60.93% | 0 | 0% | 24.75 | 15.27 | 61.7% | 0 | 0%
GNA_043371101_Capacity | North Coast | Sonoma | LAKEVILLE 1101 | 43371101 | Feeder | None | None | None | 94.42% | 0 | 0% | 12.19 | 11.51 | 94.42% | 0 | 0% | 12.19 | 11.41 | 93.6% | 0 | 0% | 12.19 | 11.33 | 92.95% | 0 | 0% | 12.19 | 11.27 | 92.45% | 0 | 0% | 12.19 | 11.27 | 92.45% | 0 | 0%
GNA_043371102_Capacity | North Coast | Sonoma | LAKEVILLE 1102 | 43371102 | Feeder | None | None | None | 31.58% | 0 | 0% | 12.19 | 3.34 | 27.4% | 0 | 0% | 12.19 | 3.43 | 28.14% | 0 | 0% | 12.19 | 3.55 | 29.12% | 0 | 0% | 12.19 | 3.69 | 30.27% | 0 | 0% | 12.19 | 3.85 | 31.58% | 0 | 0%
GNA_0433706_Capacity | North Coast | Sonoma | LAKEVILLE BANK 6 | 433706 | Bank | None | None | None | 16.7% | 0 | 0% | 44.6 | 7.11 | 15.94% | 0 | 0% | 44.6 | 7.14 | 16.01% | 0 | 0% | 44.6 | 7.17 | 16.08% | 0 | 0% | 44.6 | 7.27 | 16.3% | 0 | 0% | 44.6 | 7.45 | 16.7% | 0 | 0%
GNA_043371105_Capacity | North Coast | Sonoma | LAKEVILLE 1105 | 43371105 | Feeder | None | None | None | 61.36% | 0 | 0% | 12.19 | 7.15 | 58.65% | 0 | 0% | 12.19 | 7.17 | 58.82% | 0 | 0% | 12.19 | 7.21 | 59.15% | 0 | 0% | 12.19 | 7.3 | 59.89% | 0 | 0% | 12.19 | 7.48 | 61.36% | 0 | 0%
GNA_0426302_Capacity | North Coast | Sonoma | PETALUMA C BANK 2 | 426302 | Bank | None | None | None | 92.32% | 0 | 0% | 9.9 | 9.14 | 92.32% | 0 | 0% | 9.9 | 9.07 | 91.62% | 0 | 0% | 9.9 | 9.03 | 91.21% | 0 | 0% | 9.9 | 9.02 | 91.11% | 0 | 0% | 9.9 | 9.01 | 91.01% | 0 | 0%
GNA_042631101_Capacity | North Coast | Sonoma | PETALUMA C 1101 | 42631101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042631102_Capacity | North Coast | Sonoma | PETALUMA C 1102 | 42631102 | Feeder | None | None | None | 80.31% | 0 | 0% | 12.19 | 9.79 | 80.31% | 0 | 0% | 12.19 | 9.73 | 79.82% | 0 | 0% | 12.19 | 9.69 | 79.49% | 0 | 0% | 12.19 | 9.68 | 79.41% | 0 | 0% | 12.19 | 9.67 | 79.33% | 0 | 0%
GNA_0426303_Capacity | North Coast | Sonoma | PETALUMA C BANK 3 | 426303 | Bank | None | None | None | 88.55% | 0 | 0% | 29.7 | 25.3 | 85.19% | 0 | 0% | 29.7 | 25.53 | 85.96% | 0 | 0% | 29.7 | 25.58 | 86.13% | 0 | 0% | 29.7 | 25.88 | 87.14% | 0 | 0% | 29.7 | 26.3 | 88.55% | 0 | 0%
GNA_042631108_Capacity | North Coast | Sonoma | PETALUMA C 1108 | 42631108 | Feeder | None | None | None | 88.51% | 0 | 0% | 12.1 | 10.25 | 84.71% | 0 | 0% | 12.1 | 10.27 | 84.88% | 0 | 0% | 12.1 | 10.32 | 85.29% | 0 | 0% | 12.1 | 10.48 | 86.61% | 0 | 0% | 12.1 | 10.71 | 88.51% | 0 | 0%
GNA_042631105_Capacity | North Coast | Sonoma | PETALUMA C 1105 | 42631105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042631106_Capacity | North Coast | Sonoma | PETALUMA C 1106 | 42631106 | Feeder | None | None | None | 98.88% | 0 | 0% | 10.69 | 10.56 | 98.78% | 0 | 0% | 10.69 | 10.57 | 98.88% | 0 | 0% | 10.69 | 10.47 | 97.94% | 0 | 0% | 10.69 | 10.49 | 98.13% | 0 | 0% | 10.69 | 10.57 | 98.88% | 0 | 0%
GNA_0426304_Capacity | North Coast | Sonoma | PETALUMA C BANK 4 | 426304 | Bank | None | None | None | 66.58% | 0 | 0% | 15.8 | 9.89 | 62.59% | 0 | 0% | 15.8 | 9.88 | 62.53% | 0 | 0% | 15.8 | 10.01 | 63.35% | 0 | 0% | 15.8 | 10.26 | 64.94% | 0 | 0% | 15.8 | 10.52 | 66.58% | 0 | 0%
GNA_042631109_Capacity | North Coast | Sonoma | PETALUMA C 1109 | 42631109 | Feeder | None | None | None | 83.94% | 0 | 0% | 11.33 | 8.88 | 78.38% | 0 | 0% | 11.33 | 8.89 | 78.46% | 0 | 0% | 11.33 | 9.02 | 79.61% | 0 | 0% | 11.33 | 9.26 | 81.73% | 0 | 0% | 11.33 | 9.51 | 83.94% | 0 | 0%
GNA_042631110_Capacity | North Coast | Sonoma | PETALUMA C 1110 | 42631110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0421201_Capacity | North Coast | Sonoma | PETALUMA A BANK 1 | 421201 | Bank | None | None | None | 77.19% | 0 | 0% | 2.85 | 2.2 | 77.19% | 0 | 0% | 2.85 | 2.17 | 76.14% | 0 | 0% | 2.85 | 2.14 | 75.09% | 0 | 0% | 2.85 | 2.14 | 75.09% | 0 | 0% | 2.85 | 2.16 | 75.79% | 0 | 0%
GNA_042120411_Capacity | North Coast | Sonoma | PETALUMA A 0411 | 42120411 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042120413_Capacity | North Coast | Sonoma | PETALUMA A 0413 | 42120413 | Feeder | None | None | None | 41.75% | 0 | 0% | 2.85 | 1.19 | 41.75% | 0 | 0% | 2.85 | 1.17 | 41.05% | 0 | 0% | 2.85 | 1.16 | 40.7% | 0 | 0% | 2.85 | 1.16 | 40.7% | 0 | 0% | 2.85 | 1.16 | 40.7% | 0 | 0%
GNA_0433001_Capacity | North Coast | Sonoma | MONROE BANK 1 | 433001 | Bank | None | None | None | 59.55% | 0 | 0% | 44.55 | 25.65 | 57.58% | 0 | 0% | 44.55 | 26.36 | 59.17% | 0 | 0% | 44.55 | 26.35 | 59.15% | 0 | 0% | 44.55 | 26.34 | 59.12% | 0 | 0% | 44.55 | 26.53 | 59.55% | 0 | 0%
GNA_043302102_Capacity | North Coast | Sonoma | MONROE 2102 | 43302102 | Feeder | None | None | None | 44.36% | 0 | 0% | 18.26 | 7.74 | 42.39% | 0 | 0% | 18.26 | 7.82 | 42.83% | 0 | 0% | 18.26 | 7.91 | 43.32% | 0 | 0% | 18.26 | 7.99 | 43.76% | 0 | 0% | 18.26 | 8.1 | 44.36% | 0 | 0%
GNA_043302103_Capacity | North Coast | Sonoma | MONROE 2103 | 43302103 | Feeder | None | None | None | 90.42% | 0 | 0% | 19.63 | 17.04 | 86.81% | 0 | 0% | 19.63 | 17.75 | 90.42% | 0 | 0% | 19.63 | 17.72 | 90.27% | 0 | 0% | 19.63 | 17.71 | 90.22% | 0 | 0% | 19.63 | 17.71 | 90.22% | 0 | 0%
GNA_0433002_Capacity | North Coast | Sonoma | MONROE BANK 2 | 433002 | Bank | None | None | None | 81.9% | 0 | 0% | 41.22 | 32.81 | 79.6% | 0 | 0% | 41.22 | 33.49 | 81.25% | 0 | 0% | 41.22 | 33.4 | 81.03% | 0 | 0% | 41.22 | 33.51 | 81.3% | 0 | 0% | 41.22 | 33.76 | 81.9% | 0 | 0%
GNA_043301104_Capacity | North Coast | Sonoma | MONROE 1104 | 43301104 | Feeder | None | None | None | 92.1% | 0 | 0% | 10.76 | 9.91 | 92.1% | 0 | 0% | 10.76 | 9.83 | 91.36% | 0 | 0% | 10.76 | 9.77 | 90.8% | 0 | 0% | 10.76 | 9.71 | 90.24% | 0 | 0% | 10.76 | 9.68 | 89.96% | 0 | 0%
GNA_043301105_Capacity | North Coast | Sonoma | MONROE 1105 | 43301105 | Feeder | Demand Growth | Capacity | 2023 | 103.6% | 0.46 | 3.585% | 12.83 | 13.29 | 103.6% | 0.46 | 3.585% | 12.83 | 13.18 | 102.7% | 0.35 | 2.728% | 12.83 | 13.06 | 101.8% | 0.23 | 1.793% | 12.83 | 13.07 | 101.9% | 0.24 | 1.871% | 12.83 | 13.2 | 102.9% | 0.37 | 2.884%
GNA_043301106_Capacity | North Coast | Sonoma | MONROE 1106 | 43301106 | Feeder | Demand Growth | Capacity | 2023 | 122.9% | 2.79 | 22.89% | 12.19 | 13.84 | 113.5% | 1.65 | 13.54% | 12.19 | 14.66 | 120.3% | 2.47 | 20.26% | 12.19 | 14.7 | 120.6% | 2.51 | 20.59% | 12.19 | 14.82 | 121.6% | 2.63 | 21.58% | 12.19 | 14.98 | 122.9% | 2.79 | 22.89%
GNA_0433003_Capacity | North Coast | Sonoma | MONROE BANK 3 | 433003 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_043302107_Capacity | North Coast | Sonoma | MONROE 2107 | 43302107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0433201_Capacity | North Coast | Sonoma | RINCON BANK 1 | 433201 | Bank | None | None | None | 48.04% | 0 | 0% | 44.53 | 21.18 | 47.56% | 0 | 0% | 44.53 | 21.08 | 47.34% | 0 | 0% | 44.53 | 20.97 | 47.09% | 0 | 0% | 44.53 | 21.13 | 47.45% | 0 | 0% | 44.53 | 21.39 | 48.04% | 0 | 0%
GNA_043321101_Capacity | North Coast | Sonoma | RINCON 1101 | 43321101 | Feeder | None | None | None | 93.77% | 0 | 0% | 12.19 | 11.28 | 92.53% | 0 | 0% | 12.19 | 11.24 | 92.21% | 0 | 0% | 12.19 | 11.21 | 91.96% | 0 | 0% | 12.19 | 11.3 | 92.7% | 0 | 0% | 12.19 | 11.43 | 93.77% | 0 | 0%
GNA_043321102_Capacity | North Coast | Sonoma | RINCON 1102 | 43321102 | Feeder | None | None | None | 88.11% | 0 | 0% | 12.19 | 10.51 | 86.22% | 0 | 0% | 12.19 | 10.45 | 85.73% | 0 | 0% | 12.19 | 10.43 | 85.56% | 0 | 0% | 12.19 | 10.56 | 86.63% | 0 | 0% | 12.19 | 10.74 | 88.11% | 0 | 0%
GNA_0433202_Capacity | North Coast | Sonoma | RINCON BANK 2 | 433202 | Bank | Demand Growth | Capacity | 2023 | 134.7% | 5.48 | 34.68% | 15.8 | 20.22 | 128% | 4.42 | 27.97% | 15.8 | 20.33 | 128.7% | 4.53 | 28.67% | 15.8 | 20.57 | 130.2% | 4.77 | 30.19% | 15.8 | 20.87 | 132.1% | 5.07 | 32.09% | 15.8 | 21.28 | 134.7% | 5.48 | 34.68%
GNA_043321103_Capacity | North Coast | Sonoma | RINCON 1103 | 43321103 | Feeder | None | None | None | 74.57% | 0 | 0% | 12.19 | 8.33 | 68.33% | 0 | 0% | 12.19 | 8.48 | 69.57% | 0 | 0% | 12.19 | 8.66 | 71.04% | 0 | 0% | 12.19 | 8.86 | 72.68% | 0 | 0% | 12.19 | 9.09 | 74.57% | 0 | 0%
GNA_043321104_Capacity | North Coast | Sonoma | RINCON 1104 | 43321104 | Feeder | None | None | None | 83.43% | 0 | 0% | 12.19 | 9.74 | 79.9% | 0 | 0% | 12.19 | 9.78 | 80.23% | 0 | 0% | 12.19 | 9.84 | 80.72% | 0 | 0% | 12.19 | 9.96 | 81.71% | 0 | 0% | 12.19 | 10.17 | 83.43% | 0 | 0%
GNA_0421501_Capacity | North Coast | Sonoma | SANTA ROSA A BANK 1 | 421501 | Bank | Demand Growth | Capacity | 2023 | 136% | 15.57 | 36.03% | 43.21 | 44.99 | 104.1% | 1.78 | 4.119% | 43.21 | 53.86 | 124.6% | 10.65 | 24.65% | 43.21 | 58.78 | 136% | 15.57 | 36.03% | 43.21 | 58.39 | 135.1% | 15.18 | 35.13% | 43.21 | 58.5 | 135.4% | 15.29 | 35.39%
GNA_042151101_Capacity | North Coast | Sonoma | SANTA ROSA A 1101 | 42151101 | Feeder | None | None | None | 63.57% | 0 | 0% | 10.76 | 6.84 | 63.57% | 0 | 0% | 10.76 | 6.84 | 63.57% | 0 | 0% | 10.76 | 6.82 | 63.38% | 0 | 0% | 10.76 | 6.8 | 63.2% | 0 | 0% | 10.76 | 6.82 | 63.38% | 0 | 0%
GNA_042151102_Capacity | North Coast | Sonoma | SANTA ROSA A 1102 | 42151102 | Feeder | Demand Growth | Capacity | 2023 | 150% | 6.29 | 50.04% | 12.57 | 14.02 | 111.5% | 1.45 | 11.54% | 12.57 | 15.92 | 126.7% | 3.35 | 26.65% | 12.57 | 18.8 | 149.6% | 6.23 | 49.56% | 12.57 | 18.8 | 149.6% | 6.23 | 49.56% | 12.57 | 18.86 | 150% | 6.29 | 50.04%
GNA_042151103_Capacity | North Coast | Sonoma | SANTA ROSA A 1103 | 42151103 | Feeder | Demand Growth | Capacity | 2023 | 196.2% | 11.73 | 96.23% | 12.19 | 14.12 | 115.8% | 1.93 | 15.83% | 12.19 | 21.71 | 178.1% | 9.52 | 78.1% | 12.19 | 23.92 | 196.2% | 11.73 | 96.23% | 12.19 | 23.85 | 195.7% | 11.66 | 95.65% | 12.19 | 23.73 | 194.7% | 11.54 | 94.67%
GNA_042151104_Capacity | North Coast | Sonoma | SANTA ROSA A 1104 | 42151104 | Feeder | None | None | None | 98.05% | 0 | 0% | 10.76 | 10.55 | 98.05% | 0 | 0% | 10.76 | 10.28 | 95.54% | 0 | 0% | 10.76 | 10.14 | 94.24% | 0 | 0% | 10.76 | 10.3 | 95.72% | 0 | 0% | 10.76 | 10.51 | 97.68% | 0 | 0%
GNA_0421502_Capacity | North Coast | Sonoma | SANTA ROSA A BANK 2 | 421502 | Bank | None | None | None | 90.9% | 0 | 0% | 43.21 | 37.99 | 87.92% | 0 | 0% | 43.21 | 38.58 | 89.28% | 0 | 0% | 43.21 | 39.02 | 90.3% | 0 | 0% | 43.21 | 39.23 | 90.79% | 0 | 0% | 43.21 | 39.28 | 90.9% | 0 | 0%
GNA_042151105_Capacity | North Coast | Sonoma | SANTA ROSA A 1105 | 42151105 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042151106_Capacity | North Coast | Sonoma | SANTA ROSA A 1106 | 42151106 | Feeder | None | None | None | 92.49% | 0 | 0% | 9.45 | 8.74 | 92.49% | 0 | 0% | 9.45 | 8.59 | 90.9% | 0 | 0% | 9.45 | 8.46 | 89.52% | 0 | 0% | 9.45 | 8.34 | 88.25% | 0 | 0% | 9.45 | 8.31 | 87.94% | 0 | 0%
GNA_042151107_Capacity | North Coast | Sonoma | SANTA ROSA A 1107 | 42151107 | Feeder | None | None | None | 51.35% | 0 | 0% | 12.19 | 6.26 | 51.35% | 0 | 0% | 12.19 | 6.22 | 51.03% | 0 | 0% | 12.19 | 6.19 | 50.78% | 0 | 0% | 12.19 | 6.21 | 50.94% | 0 | 0% | 12.19 | 6.22 | 51.03% | 0 | 0%
GNA_042151108_Capacity | North Coast | Sonoma | SANTA ROSA A 1108 | 42151108 | Feeder | Demand Growth | Capacity | 2023 | 126.9% | 2.95 | 26.94% | 10.95 | 12.3 | 112.3% | 1.35 | 12.33% | 10.95 | 12.63 | 115.3% | 1.68 | 15.34% | 10.95 | 13.29 | 121.4% | 2.34 | 21.37% | 10.95 | 13.74 | 125.5% | 2.79 | 25.48% | 10.95 | 13.9 | 126.9% | 2.95 | 26.94%
GNA_0421503_Capacity | North Coast | Sonoma | SANTA ROSA A BANK 3 | 421503 | Bank | None | None | None | 79.35% | 0 | 0% | 44.55 | 33.78 | 75.82% | 0 | 0% | 44.55 | 34.07 | 76.48% | 0 | 0% | 44.55 | 34.21 | 76.79% | 0 | 0% | 44.55 | 34.67 | 77.82% | 0 | 0% | 44.55 | 35.35 | 79.35% | 0 | 0%
GNA_042151109_Capacity | North Coast | Sonoma | SANTA ROSA A 1109 | 42151109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042151110_Capacity | North Coast | Sonoma | SANTA ROSA A 1110 | 42151110 | Feeder | Demand Growth | Capacity | 2023 | 105.4% | 0.57 | 5.449% | 10.46 | 10.65 | 101.8% | 0.19 | 1.816% | 10.46 | 10.61 | 101.4% | 0.15 | 1.434% | 10.46 | 10.62 | 101.5% | 0.16 | 1.53% | 10.46 | 10.77 | 103% | 0.31 | 2.964% | 10.46 | 11.03 | 105.4% | 0.57 | 5.449%
GNA_042151111_Capacity | North Coast | Sonoma | SANTA ROSA A 1111 | 42151111 | Feeder | None | None | None | 92.53% | 0 | 0% | 12.19 | 10.21 | 83.76% | 0 | 0% | 12.19 | 10.61 | 87.04% | 0 | 0% | 12.19 | 10.75 | 88.19% | 0 | 0% | 12.19 | 10.98 | 90.07% | 0 | 0% | 12.19 | 11.28 | 92.53% | 0 | 0%
GNA_042151112_Capacity | North Coast | Sonoma | SANTA ROSA A 1112 | 42151112 | Feeder | None | None | None | 95.45% | 0 | 0% | 10.78 | 10.29 | 95.45% | 0 | 0% | 10.78 | 10.2 | 94.62% | 0 | 0% | 10.78 | 10.12 | 93.88% | 0 | 0% | 10.78 | 10.05 | 93.23% | 0 | 0% | 10.78 | 10.03 | 93.04% | 0 | 0%
GNA_0420901_Capacity | North Coast | Sonoma | MIRABEL BANK 1 | 420901 | Bank | None | None | None | 89.9% | 0 | 0% | 10.4 | 9.35 | 89.9% | 0 | 0% | 10.4 | 9.27 | 89.13% | 0 | 0% | 10.4 | 9.24 | 88.85% | 0 | 0% | 10.4 | 9.25 | 88.94% | 0 | 0% | 10.4 | 9.27 | 89.13% | 0 | 0%
GNA_042091101_Capacity | North Coast | Sonoma | MIRABEL 1101 | 42091101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042091102_Capacity | North Coast | Sonoma | MIRABEL 1102 | 42091102 | Feeder | None | None | None | 54.86% | 0 | 0% | 10.39 | 5.66 | 54.48% | 0 | 0% | 10.39 | 5.65 | 54.38% | 0 | 0% | 10.39 | 5.66 | 54.48% | 0 | 0% | 10.39 | 5.68 | 54.67% | 0 | 0% | 10.39 | 5.7 | 54.86% | 0 | 0%
GNA_0425701_Capacity | North Coast | Sonoma | MOLINO BANK 1 | 425701 | Bank | None | None | None | 88.45% | 0 | 0% | 12.38 | 9.78 | 79% | 0 | 0% | 12.38 | 10.69 | 86.35% | 0 | 0% | 12.38 | 10.72 | 86.59% | 0 | 0% | 12.38 | 10.83 | 87.48% | 0 | 0% | 12.38 | 10.95 | 88.45% | 0 | 0%
GNA_042571101_Capacity | North Coast | Sonoma | MOLINO 1101 | 42571101 | Feeder | None | None | None | 89.66% | 0 | 0% | 12.19 | 9.76 | 80.07% | 0 | 0% | 12.19 | 10.67 | 87.53% | 0 | 0% | 12.19 | 10.7 | 87.78% | 0 | 0% | 12.19 | 10.81 | 88.68% | 0 | 0% | 12.19 | 10.93 | 89.66% | 0 | 0%
GNA_0425702_Capacity | North Coast | Sonoma | MOLINO BANK 2 | 425702 | Bank | Demand Growth | Capacity | 2026 | 102.6% | 0.77 | 2.593% | 29.7 | 28.84 | 97.1% | 0 | 0% | 29.7 | 29.58 | 99.6% | 0 | 0% | 29.7 | 29.84 | 100.5% | 0.14 | 0.4714% | 29.7 | 30.13 | 101.4% | 0.43 | 1.448% | 29.7 | 30.47 | 102.6% | 0.77 | 2.593%
GNA_042571102_Capacity | North Coast | Sonoma | MOLINO 1102 | 42571102 | Feeder | None | None | None | 95.17% | 0 | 0% | 10.76 | 9.49 | 88.2% | 0 | 0% | 10.76 | 10 | 92.94% | 0 | 0% | 10.76 | 10.02 | 93.12% | 0 | 0% | 10.76 | 10.14 | 94.24% | 0 | 0% | 10.76 | 10.24 | 95.17% | 0 | 0%
GNA_042571103_Capacity | North Coast | Sonoma | MOLINO 1103 | 42571103 | Feeder | None | None | None | 80.05% | 0 | 0% | 12.83 | 9.99 | 77.86% | 0 | 0% | 12.83 | 10.02 | 78.1% | 0 | 0% | 12.83 | 10.06 | 78.41% | 0 | 0% | 12.83 | 10.14 | 79.03% | 0 | 0% | 12.83 | 10.27 | 80.05% | 0 | 0%
GNA_042571104_Capacity | North Coast | Sonoma | MOLINO 1104 | 42571104 | Feeder | None | None | None | 86.42% | 0 | 0% | 10.46 | 8.64 | 82.6% | 0 | 0% | 10.46 | 8.8 | 84.13% | 0 | 0% | 10.46 | 9.02 | 86.23% | 0 | 0% | 10.46 | 9.02 | 86.23% | 0 | 0% | 10.46 | 9.04 | 86.42% | 0 | 0%
GNA_0430701_Capacity | North Coast | Sonoma | DUNBAR BANK 1 | 430701 | Bank | None | None | None | 78.59% | 0 | 0% | 20.78 | 16.33 | 78.59% | 0 | 0% | 20.78 | 15.96 | 76.8% | 0 | 0% | 20.78 | 15.57 | 74.93% | 0 | 0% | 20.78 | 15.32 | 73.72% | 0 | 0% | 20.78 | 15.2 | 73.15% | 0 | 0%
GNA_043071102_Capacity | North Coast | Sonoma | DUNBAR 1102 | 43071102 | Feeder | None | None | None | 63% | 0 | 0% | 10.46 | 6.59 | 63% | 0 | 0% | 10.46 | 6.38 | 60.99% | 0 | 0% | 10.46 | 6.2 | 59.27% | 0 | 0% | 10.46 | 6.08 | 58.13% | 0 | 0% | 10.46 | 5.99 | 57.27% | 0 | 0%
GNA_043071103_Capacity | North Coast | Sonoma | DUNBAR 1103 | 43071103 | Feeder | None | None | None | 89.42% | 0 | 0% | 12.19 | 10.9 | 89.42% | 0 | 0% | 12.19 | 10.74 | 88.11% | 0 | 0% | 12.19 | 10.53 | 86.38% | 0 | 0% | 12.19 | 10.4 | 85.32% | 0 | 0% | 12.19 | 10.33 | 84.74% | 0 | 0%
GNA_0430702_Capacity | North Coast | Sonoma | DUNBAR BANK 2 | 430702 | Bank | None | None | None | 81.14% | 0 | 0% | 10.39 | 8.43 | 81.14% | 0 | 0% | 10.39 | 8.27 | 79.6% | 0 | 0% | 10.39 | 8.12 | 78.15% | 0 | 0% | 10.39 | 7.99 | 76.9% | 0 | 0% | 10.39 | 7.91 | 76.13% | 0 | 0%
GNA_043071101_Capacity | North Coast | Sonoma | DUNBAR 1101 | 43071101 | Feeder | None | None | None | 71.04% | 0 | 0% | 10.05 | 7.14 | 71.04% | 0 | 0% | 10.05 | 6.99 | 69.55% | 0 | 0% | 10.05 | 6.83 | 67.96% | 0 | 0% | 10.05 | 6.71 | 66.77% | 0 | 0% | 10.05 | 6.72 | 66.87% | 0 | 0%
GNA_0427201_Capacity | North Coast | Sonoma | SONOMA BANK 1 | 427201 | Bank | None | None | None | 90.51% | 0 | 0% | 29.7 | 26.88 | 90.51% | 0 | 0% | 29.7 | 26.4 | 88.89% | 0 | 0% | 29.7 | 26.28 | 88.48% | 0 | 0% | 29.7 | 25.85 | 87.04% | 0 | 0% | 29.7 | 25.45 | 85.69% | 0 | 0%
GNA_042721102_Capacity | North Coast | Sonoma | SONOMA 1102 | 42721102 | Feeder | None | None | None | 89.58% | 0 | 0% | 12.19 | 10.69 | 87.69% | 0 | 0% | 12.19 | 10.6 | 86.96% | 0 | 0% | 12.19 | 10.92 | 89.58% | 0 | 0% | 12.19 | 10.78 | 88.43% | 0 | 0% | 12.19 | 10.63 | 87.2% | 0 | 0%
GNA_042721103_Capacity | North Coast | Sonoma | SONOMA 1103 | 42721103 | Feeder | None | None | None | 76.39% | 0 | 0% | 10.97 | 8.38 | 76.39% | 0 | 0% | 10.97 | 8.2 | 74.75% | 0 | 0% | 10.97 | 8.03 | 73.2% | 0 | 0% | 10.97 | 7.91 | 72.11% | 0 | 0% | 10.97 | 7.84 | 71.47% | 0 | 0%
GNA_042721104_Capacity | North Coast | Sonoma | SONOMA 1104 | 42721104 | Feeder | None | None | None | 74.9% | 0 | 0% | 12.19 | 9.13 | 74.9% | 0 | 0% | 12.19 | 8.9 | 73.01% | 0 | 0% | 12.19 | 8.65 | 70.96% | 0 | 0% | 12.19 | 8.46 | 69.4% | 0 | 0% | 12.19 | 8.32 | 68.25% | 0 | 0%
GNA_0427202_Capacity | North Coast | Sonoma | SONOMA BANK 2 | 427202 | Bank | None | None | None | 64.6% | 0 | 0% | 44.55 | 28.78 | 64.6% | 0 | 0% | 44.55 | 28.34 | 63.61% | 0 | 0% | 44.55 | 28.4 | 63.75% | 0 | 0% | 44.55 | 28.04 | 62.94% | 0 | 0% | 44.55 | 27.85 | 62.51% | 0 | 0%
GNA_042721105_Capacity | North Coast | Sonoma | SONOMA 1105 | 42721105 | Feeder | None | None | None | 93.72% | 0 | 0% | 12.27 | 11.39 | 92.83% | 0 | 0% | 12.27 | 11.21 | 91.36% | 0 | 0% | 12.27 | 11.5 | 93.72% | 0 | 0% | 12.27 | 11.34 | 92.42% | 0 | 0% | 12.27 | 11.35 | 92.5% | 0 | 0%
GNA_042721106_Capacity | North Coast | Sonoma | SONOMA 1106 | 42721106 | Feeder | None | None | None | 80.76% | 0 | 0% | 12.42 | 10.03 | 80.76% | 0 | 0% | 12.42 | 9.83 | 79.15% | 0 | 0% | 12.42 | 9.69 | 78.02% | 0 | 0% | 12.42 | 9.58 | 77.13% | 0 | 0% | 12.42 | 9.43 | 75.93% | 0 | 0%
GNA_042721107_Capacity | North Coast | Sonoma | SONOMA 1107 | 42721107 | Feeder | None | None | None | 93.06% | 0 | 0% | 7.93 | 7.38 | 93.06% | 0 | 0% | 7.93 | 7.32 | 92.31% | 0 | 0% | 7.93 | 7.24 | 91.3% | 0 | 0% | 7.93 | 7.15 | 90.16% | 0 | 0% | 7.93 | 7.09 | 89.41% | 0 | 0%
GNA_0428501_Capacity | North Coast | Sonoma | FORT ROSS BANK 1 | 428501 | Bank | None | None | None | 56.32% | 0 | 0% | 1.9 | 1 | 52.63% | 0 | 0% | 1.9 | 1.02 | 53.68% | 0 | 0% | 1.9 | 1.04 | 54.74% | 0 | 0% | 1.9 | 1.06 | 55.79% | 0 | 0% | 1.9 | 1.07 | 56.32% | 0 | 0%
GNA_042851121_Capacity | North Coast | Sonoma | FORT ROSS 1121 | 42851121 | Feeder | None | None | None | 39.88% | 0 | 0% | 3.21 | 1.22 | 38.01% | 0 | 0% | 3.21 | 1.24 | 38.63% | 0 | 0% | 3.21 | 1.25 | 38.94% | 0 | 0% | 3.21 | 1.28 | 39.88% | 0 | 0% | 3.21 | 1.28 | 39.88% | 0 | 0%
GNA_0428101_Capacity | North Coast | Sonoma | MONTE RIO BANK 1 | 428101 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_042811111_Capacity | North Coast | Sonoma | MONTE RIO 1111 | 42811111 | Feeder | None | None | None | 25.53% | 0 | 0% | 9.99 | 2.5 | 25.03% | 0 | 0% | 9.99 | 2.5 | 25.03% | 0 | 0% | 9.99 | 2.49 | 24.92% | 0 | 0% | 9.99 | 2.51 | 25.13% | 0 | 0% | 9.99 | 2.55 | 25.53% | 0 | 0%
GNA_042811112_Capacity | North Coast | Sonoma | MONTE RIO 1112 | 42811112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_0428102_Capacity | North Coast | Sonoma | MONTE RIO BANK 2 | 428102 | Bank | None | None | None | 30.37% | 0 | 0% | 15.84 | 4.66 | 29.42% | 0 | 0% | 15.84 | 4.67 | 29.48% | 0 | 0% | 15.84 | 4.67 | 29.48% | 0 | 0% | 15.84 | 4.73 | 29.86% | 0 | 0% | 15.84 | 4.81 | 30.37% | 0 | 0%
GNA_042811113_Capacity | North Coast | Sonoma | MONTE RIO 1113 | 42811113 | Feeder | None | None | None | 45.46% | 0 | 0% | 10.69 | 4.71 | 44.06% | 0 | 0% | 10.69 | 4.72 | 44.15% | 0 | 0% | 10.69 | 4.72 | 44.15% | 0 | 0% | 10.69 | 4.78 | 44.71% | 0 | 0% | 10.69 | 4.86 | 45.46% | 0 | 0%
GNA_0431601_Capacity | North Coast | Sonoma | SALMON CREEK BANK 1 | 431601 | Bank | None | None | None | 40.21% | 0 | 0% | 9.4 | 3.68 | 39.15% | 0 | 0% | 9.4 | 3.57 | 37.98% | 0 | 0% | 9.4 | 3.6 | 38.3% | 0 | 0% | 9.4 | 3.7 | 39.36% | 0 | 0% | 9.4 | 3.78 | 40.21% | 0 | 0%
GNA_043161101_Capacity | North Coast | Sonoma | SALMON CREEK 1101 | 43161101 | Feeder | None | None | None | 53.93% | 0 | 0% | 7.12 | 3.74 | 52.53% | 0 | 0% | 7.12 | 3.64 | 51.12% | 0 | 0% | 7.12 | 3.66 | 51.4% | 0 | 0% | 7.12 | 3.75 | 52.67% | 0 | 0% | 7.12 | 3.84 | 53.93% | 0 | 0%
GNA_1634501_Capacity | Central Valley | Stockton | FROGTOWN BANK 1 | 1634501 | Bank | None | None | None | 85.26% | 0 | 0% | 8.82 | 7.5 | 85.03% | 0 | 0% | 8.82 | 7.46 | 84.58% | 0 | 0% | 8.82 | 7.43 | 84.24% | 0 | 0% | 8.82 | 7.49 | 84.92% | 0 | 0% | 8.82 | 7.52 | 85.26% | 0 | 0%
GNA_163451701_Capacity | Central Valley | Stockton | FROGTOWN 1701 | 163451701 | Feeder | None | None | None | 66.55% | 0 | 0% | 11.21 | 7.45 | 66.46% | 0 | 0% | 11.21 | 7.41 | 66.1% | 0 | 0% | 11.21 | 7.38 | 65.83% | 0 | 0% | 11.21 | 7.43 | 66.28% | 0 | 0% | 11.21 | 7.46 | 66.55% | 0 | 0%
GNA_1634502_Capacity | Central Valley | Stockton | FROGTOWN BANK 2 | 1634502 | Bank | None | None | None | 97.47% | 0 | 0% | 15.82 | 15.42 | 97.47% | 0 | 0% | 15.82 | 15.32 | 96.84% | 0 | 0% | 15.82 | 15.24 | 96.33% | 0 | 0% | 15.82 | 15.19 | 96.02% | 0 | 0% | 15.82 | 15.16 | 95.83% | 0 | 0%
GNA_163451702_Capacity | Central Valley | Stockton | FROGTOWN 1702 | 163451702 | Feeder | None | None | None | 87.57% | 0 | 0% | 16.81 | 14.72 | 87.57% | 0 | 0% | 16.81 | 14.63 | 87.03% | 0 | 0% | 16.81 | 14.55 | 86.56% | 0 | 0% | 16.81 | 14.5 | 86.26% | 0 | 0% | 16.81 | 14.47 | 86.08% | 0 | 0%
GNA_1628202_Capacity | Central Valley | Stockton | STANISLAUS BANK 2 | 1628202 | Bank | Demand Growth | Capacity | 2023 | 100.6% | 0.07 | 0.5952% | 11.76 | 11.83 | 100.6% | 0.07 | 0.5952% | 11.76 | 11.45 | 97.36% | 0 | 0% | 11.76 | 11.3 | 96.09% | 0 | 0% | 11.76 | 11.19 | 95.15% | 0 | 0% | 11.76 | 11.28 | 95.92% | 0 | 0%
GNA_162821701_Capacity | Central Valley | Stockton | STANISLAUS 1701 | 162821701 | Feeder | None | None | None | 52.99% | 0 | 0% | 11.21 | 5.77 | 51.47% | 0 | 0% | 11.21 | 5.8 | 51.74% | 0 | 0% | 11.21 | 5.83 | 52.01% | 0 | 0% | 11.21 | 5.88 | 52.45% | 0 | 0% | 11.21 | 5.94 | 52.99% | 0 | 0%
GNA_162821702_Capacity | Central Valley | Stockton | STANISLAUS 1702 | 162821702 | Feeder | None | None | None | 71.1% | 0 | 0% | 11.21 | 7.97 | 71.1% | 0 | 0% | 11.21 | 7.71 | 68.78% | 0 | 0% | 11.21 | 7.59 | 67.71% | 0 | 0% | 11.21 | 7.6 | 67.8% | 0 | 0% | 11.21 | 7.64 | 68.15% | 0 | 0%
GNA_1633401_Capacity | Central Valley | Stockton | CLAY BANK 1 | 1633401 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163341101_Capacity | Central Valley | Stockton | CLAY 1101 | 163341101 | Feeder | None | None | None | 60.62% | 0 | 0% | 10.69 | 6.48 | 60.62% | 0 | 0% | 10.69 | 6.43 | 60.15% | 0 | 0% | 10.69 | 6.38 | 59.68% | 0 | 0% | 10.69 | 6.37 | 59.59% | 0 | 0% | 10.69 | 6.34 | 59.31% | 0 | 0%
GNA_163341102_Capacity | Central Valley | Stockton | CLAY 1102 | 163341102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1633402_Capacity | Central Valley | Stockton | CLAY BANK 2 | 1633402 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163341103_Capacity | Central Valley | Stockton | CLAY 1103 | 163341103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1638801_Capacity | Central Valley | Stockton | IONE BANK 1 | 1638801 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163881101_Capacity | Central Valley | Stockton | IONE 1101 | 163881101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1629901_Capacity | Central Valley | Stockton | CORRAL BANK 1 | 1629901 | Bank | None | None | None | 78.75% | 0 | 0% | 29.7 | 23.38 | 78.72% | 0 | 0% | 29.7 | 23.36 | 78.65% | 0 | 0% | 29.7 | 23.36 | 78.65% | 0 | 0% | 29.7 | 23.34 | 78.59% | 0 | 0% | 29.7 | 23.39 | 78.75% | 0 | 0%
GNA_162991101_Capacity | Central Valley | Stockton | CORRAL 1101 | 162991101 | Feeder | Demand Growth | Capacity | 2023 | 115.5% | 1.89 | 15.5% | 12.19 | 14.08 | 115.5% | 1.89 | 15.5% | 12.19 | 14.07 | 115.4% | 1.88 | 15.42% | 12.19 | 14.07 | 115.4% | 1.88 | 15.42% | 12.19 | 14.06 | 115.3% | 1.87 | 15.34% | 12.19 | 14.07 | 115.4% | 1.88 | 15.42%
GNA_162991103_Capacity | Central Valley | Stockton | CORRAL 1103 | 162991103 | Feeder | None | None | None | 92.07% | 0 | 0% | 10.46 | 9.62 | 91.97% | 0 | 0% | 10.46 | 9.62 | 91.97% | 0 | 0% | 10.46 | 9.61 | 91.87% | 0 | 0% | 10.46 | 9.61 | 91.87% | 0 | 0% | 10.46 | 9.63 | 92.07% | 0 | 0%
GNA_1629902_Capacity | Central Valley | Stockton | CORRAL BANK 2 | 1629902 | Bank | None | None | None | 90.61% | 0 | 0% | 12.36 | 11.19 | 90.53% | 0 | 0% | 12.36 | 11.18 | 90.45% | 0 | 0% | 12.36 | 11.18 | 90.45% | 0 | 0% | 12.36 | 11.19 | 90.53% | 0 | 0% | 12.36 | 11.2 | 90.61% | 0 | 0%
GNA_162991102_Capacity | Central Valley | Stockton | CORRAL 1102 | 162991102 | Feeder | Demand Growth | Capacity | 2023 | 108.5% | 0.89 | 8.509% | 10.46 | 11.34 | 108.4% | 0.88 | 8.413% | 10.46 | 11.33 | 108.3% | 0.87 | 8.317% | 10.46 | 11.32 | 108.2% | 0.86 | 8.222% | 10.46 | 11.34 | 108.4% | 0.88 | 8.413% | 10.46 | 11.35 | 108.5% | 0.89 | 8.509%
GNA_1622101_Capacity | Central Valley | Stockton | CALAVERAS CEMENT BANK 1 | 1622101 | Bank | None | None | None | 79.77% | 0 | 0% | 17.6 | 13.83 | 78.58% | 0 | 0% | 17.6 | 13.83 | 78.58% | 0 | 0% | 17.6 | 13.84 | 78.64% | 0 | 0% | 17.6 | 13.92 | 79.09% | 0 | 0% | 17.6 | 14.04 | 79.77% | 0 | 0%
GNA_162211101_Capacity | Central Valley | Stockton | CALAVERAS CEMENT 1101 | 162211101 | Feeder | Demand Growth | Capacity | 2027 | 101.1% | 0.15 | 1.052% | 14.26 | 14.2 | 99.58% | 0 | 0% | 14.26 | 14.2 | 99.58% | 0 | 0% | 14.26 | 14.21 | 99.65% | 0 | 0% | 14.26 | 14.29 | 100.2% | 0.03 | 0.2104% | 14.26 | 14.41 | 101.1% | 0.15 | 1.052%
GNA_1621601_Capacity | Central Valley | Stockton | ELECTRA BANK 1 | 1621601 | Bank | None | None | None | 88.11% | 0 | 0% | 12.36 | 10.89 | 88.11% | 0 | 0% | 12.36 | 10.8 | 87.38% | 0 | 0% | 12.36 | 10.72 | 86.73% | 0 | 0% | 12.36 | 10.7 | 86.57% | 0 | 0% | 12.36 | 10.66 | 86.25% | 0 | 0%
GNA_162161101_Capacity | Central Valley | Stockton | ELECTRA 1101 | 162161101 | Feeder | None | None | None | 72.59% | 0 | 0% | 10.69 | 7.76 | 72.59% | 0 | 0% | 10.69 | 7.68 | 71.84% | 0 | 0% | 10.69 | 7.61 | 71.19% | 0 | 0% | 10.69 | 7.59 | 71% | 0 | 0% | 10.69 | 7.54 | 70.53% | 0 | 0%
GNA_162161102_Capacity | Central Valley | Stockton | ELECTRA 1102 | 162161102 | Feeder | None | None | None | 33.75% | 0 | 0% | 10.46 | 3.53 | 33.75% | 0 | 0% | 10.46 | 3.52 | 33.65% | 0 | 0% | 10.46 | 3.51 | 33.56% | 0 | 0% | 10.46 | 3.51 | 33.56% | 0 | 0% | 10.46 | 3.52 | 33.65% | 0 | 0%
GNA_1630101_Capacity | Central Valley | Stockton | MARTELL BANK 1 | 1630101 | Bank | None | None | None | 96.25% | 0 | 0% | 19.73 | 18.99 | 96.25% | 0 | 0% | 19.73 | 18.86 | 95.59% | 0 | 0% | 19.73 | 18.76 | 95.08% | 0 | 0% | 19.73 | 18.72 | 94.88% | 0 | 0% | 19.73 | 18.71 | 94.83% | 0 | 0%
GNA_163011101_Capacity | Central Valley | Stockton | MARTELL 1101 | 163011101 | Feeder | None | None | None | 69.97% | 0 | 0% | 10.69 | 7.48 | 69.97% | 0 | 0% | 10.69 | 7.4 | 69.22% | 0 | 0% | 10.69 | 7.33 | 68.57% | 0 | 0% | 10.69 | 7.31 | 68.38% | 0 | 0% | 10.69 | 7.3 | 68.29% | 0 | 0%
GNA_163011102_Capacity | Central Valley | Stockton | MARTELL 1102 | 163011102 | Feeder | None | None | None | 66.83% | 0 | 0% | 6.09 | 4.07 | 66.83% | 0 | 0% | 6.09 | 4.05 | 66.5% | 0 | 0% | 6.09 | 4.02 | 66.01% | 0 | 0% | 6.09 | 4 | 65.68% | 0 | 0% | 6.09 | 3.98 | 65.35% | 0 | 0%
GNA_163011103_Capacity | Central Valley | Stockton | MARTELL 1103 | 163011103 | Feeder | None | None | None | 65.48% | 0 | 0% | 10.69 | 7 | 65.48% | 0 | 0% | 10.69 | 6.92 | 64.73% | 0 | 0% | 10.69 | 6.88 | 64.36% | 0 | 0% | 10.69 | 6.85 | 64.08% | 0 | 0% | 10.69 | 6.86 | 64.17% | 0 | 0%
GNA_1635401_Capacity | Central Valley | Stockton | OLETA BANK 1 | 1635401 | Bank | None | None | None | 59.84% | 0 | 0% | 12.3 | 7.36 | 59.84% | 0 | 0% | 12.3 | 7.35 | 59.76% | 0 | 0% | 12.3 | 7.35 | 59.76% | 0 | 0% | 12.3 | 7.34 | 59.67% | 0 | 0% | 12.3 | 7.33 | 59.59% | 0 | 0%
GNA_163541101_Capacity | Central Valley | Stockton | OLETA 1101 | 163541101 | Feeder | None | None | None | 60.71% | 0 | 0% | 12.19 | 7.4 | 60.71% | 0 | 0% | 12.19 | 7.39 | 60.62% | 0 | 0% | 12.19 | 7.39 | 60.62% | 0 | 0% | 12.19 | 7.38 | 60.54% | 0 | 0% | 12.19 | 7.37 | 60.46% | 0 | 0%
GNA_1635402_Capacity | Central Valley | Stockton | OLETA BANK 2 | 1635402 | Bank | None | None | None | 79.4% | 0 | 0% | 5.29 | 4.18 | 79.02% | 0 | 0% | 5.29 | 4.17 | 78.83% | 0 | 0% | 5.29 | 4.17 | 78.83% | 0 | 0% | 5.29 | 4.19 | 79.21% | 0 | 0% | 5.29 | 4.2 | 79.4% | 0 | 0%
GNA_163541102_Capacity | Central Valley | Stockton | OLETA 1102 | 163541102 | Feeder | None | None | None | 60.91% | 0 | 0% | 7.01 | 4.26 | 60.77% | 0 | 0% | 7.01 | 4.24 | 60.49% | 0 | 0% | 7.01 | 4.24 | 60.49% | 0 | 0% | 7.01 | 4.26 | 60.77% | 0 | 0% | 7.01 | 4.27 | 60.91% | 0 | 0%
GNA_1637501_Capacity | Central Valley | Stockton | PINE GROVE BANK 1 | 1637501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163751101_Capacity | Central Valley | Stockton | PINE GROVE 1101 | 163751101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1637502_Capacity | Central Valley | Stockton | PINE GROVE BANK 2 | 1637502 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163751102_Capacity | Central Valley | Stockton | PINE GROVE 1102 | 163751102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1632002_Capacity | Central Valley | Stockton | WEST POINT BANK 2 | 1632002 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163201101_Capacity | Central Valley | Stockton | WEST POINT 1101 | 163201101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1632003_Capacity | Central Valley | Stockton | WEST POINT BANK 3 | 1632003 | Bank | None | None | None | 99.57% | 0 | 0% | 6.9 | 6.78 | 98.26% | 0 | 0% | 6.9 | 6.82 | 98.84% | 0 | 0% | 6.9 | 6.83 | 98.99% | 0 | 0% | 6.9 | 6.84 | 99.13% | 0 | 0% | 6.9 | 6.87 | 99.57% | 0 | 0%
GNA_163201102_Capacity | Central Valley | Stockton | WEST POINT 1102 | 163201102 | Feeder | None | None | None | 94.52% | 0 | 0% | 7.48 | 6.98 | 93.32% | 0 | 0% | 7.48 | 7.02 | 93.85% | 0 | 0% | 7.48 | 7.03 | 93.98% | 0 | 0% | 7.48 | 7.03 | 93.98% | 0 | 0% | 7.48 | 7.07 | 94.52% | 0 | 0%
GNA_1620701_Capacity | Central Valley | Stockton | LINDEN BANK 1 | 1620701 | Bank | None | None | None | 91.4% | 0 | 0% | 19.3 | 17.64 | 91.4% | 0 | 0% | 19.3 | 17.61 | 91.24% | 0 | 0% | 19.3 | 17.58 | 91.09% | 0 | 0% | 19.3 | 17.57 | 91.04% | 0 | 0% | 19.3 | 17.6 | 91.19% | 0 | 0%
GNA_162071101_Capacity | Central Valley | Stockton | LINDEN 1101 | 162071101 | Feeder | None | None | None | 57.93% | 0 | 0% | 10.46 | 6.06 | 57.93% | 0 | 0% | 10.46 | 6.06 | 57.93% | 0 | 0% | 10.46 | 6.05 | 57.84% | 0 | 0% | 10.46 | 6.05 | 57.84% | 0 | 0% | 10.46 | 6.06 | 57.93% | 0 | 0%
GNA_162071103_Capacity | Central Valley | Stockton | LINDEN 1103 | 162071103 | Feeder | None | None | None | 85.76% | 0 | 0% | 10.46 | 8.95 | 85.56% | 0 | 0% | 10.46 | 8.95 | 85.56% | 0 | 0% | 10.46 | 8.95 | 85.56% | 0 | 0% | 10.46 | 8.95 | 85.56% | 0 | 0% | 10.46 | 8.97 | 85.76% | 0 | 0%
GNA_162071104_Capacity | Central Valley | Stockton | LINDEN 1104 | 162071104 | Feeder | None | None | None | 68.64% | 0 | 0% | 10.46 | 7.18 | 68.64% | 0 | 0% | 10.46 | 7.15 | 68.36% | 0 | 0% | 10.46 | 7.14 | 68.26% | 0 | 0% | 10.46 | 7.15 | 68.36% | 0 | 0% | 10.46 | 7.16 | 68.45% | 0 | 0%
GNA_1632101_Capacity | Central Valley | Stockton | MORMON BANK 1 | 1632101 | Bank | None | None | None | 91.89% | 0 | 0% | 29.7 | 26.61 | 89.6% | 0 | 0% | 29.7 | 26.76 | 90.1% | 0 | 0% | 29.7 | 26.91 | 90.61% | 0 | 0% | 29.7 | 27.09 | 91.21% | 0 | 0% | 29.7 | 27.29 | 91.89% | 0 | 0%
GNA_163211101_Capacity | Central Valley | Stockton | MORMON 1101 | 163211101 | Feeder | None | None | None | 77.83% | 0 | 0% | 12.36 | 9.62 | 77.83% | 0 | 0% | 12.36 | 9.6 | 77.67% | 0 | 0% | 12.36 | 9.59 | 77.59% | 0 | 0% | 12.36 | 9.59 | 77.59% | 0 | 0% | 12.36 | 9.6 | 77.67% | 0 | 0%
GNA_163211102_Capacity | Central Valley | Stockton | MORMON 1102 | 163211102 | Feeder | Demand Growth | Capacity | 2027 | 100.6% | 0.07 | 0.5663% | 12.36 | 12.12 | 98.06% | 0 | 0% | 12.36 | 12.19 | 98.62% | 0 | 0% | 12.36 | 12.27 | 99.27% | 0 | 0% | 12.36 | 12.34 | 99.84% | 0 | 0% | 12.36 | 12.43 | 100.6% | 0.07 | 0.5663%
GNA_163211103_Capacity | Central Valley | Stockton | MORMON 1103 | 163211103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1622302_Capacity | Central Valley | Stockton | COLONY BANK 2 | 1622302 | Bank | Demand Growth | Capacity | 2023 | 154% | 2.92 | 53.97% | 5.41 | 6.24 | 115.3% | 0.83 | 15.34% | 5.41 | 6.34 | 117.2% | 0.93 | 17.19% | 5.41 | 6.43 | 118.9% | 1.02 | 18.85% | 5.41 | 7.36 | 136% | 1.95 | 36.04% | 5.41 | 8.33 | 154% | 2.92 | 53.97%
GNA_162231101_Capacity | Central Valley | Stockton | COLONY 1101 | 162231101 | Feeder | None | None | None | 38.5% | 0 | 0% | 6.78 | 2.6 | 38.35% | 0 | 0% | 6.78 | 2.61 | 38.5% | 0 | 0% | 6.78 | 2.6 | 38.35% | 0 | 0% | 6.78 | 2.59 | 38.2% | 0 | 0% | 6.78 | 2.6 | 38.35% | 0 | 0%
GNA_162231102_Capacity | Central Valley | Stockton | COLONY 1102 | 162231102 | Feeder | None | None | None | 94.69% | 0 | 0% | 6.78 | 4.25 | 62.68% | 0 | 0% | 6.78 | 4.35 | 64.16% | 0 | 0% | 6.78 | 4.45 | 65.63% | 0 | 0% | 6.78 | 5.43 | 80.09% | 0 | 0% | 6.78 | 6.42 | 94.69% | 0 | 0%
GNA_1636804_Capacity | Central Valley | Stockton | LOCKEFORD BANK 4 | 1636804 | Bank | None | None | None | 99.49% | 0 | 0% | 29.7 | 28.48 | 95.89% | 0 | 0% | 29.7 | 29.16 | 98.18% | 0 | 0% | 29.7 | 29.21 | 98.35% | 0 | 0% | 29.7 | 29.37 | 98.89% | 0 | 0% | 29.7 | 29.55 | 99.49% | 0 | 0%
GNA_163682101_Capacity | Central Valley | Stockton | LOCKEFORD 2101 | 163682101 | Feeder | None | None | None | 62.1% | 0 | 0% | 21.11 | 12.58 | 59.59% | 0 | 0% | 21.11 | 12.66 | 59.97% | 0 | 0% | 21.11 | 12.76 | 60.45% | 0 | 0% | 21.11 | 12.94 | 61.3% | 0 | 0% | 21.11 | 13.11 | 62.1% | 0 | 0%
GNA_163682102_Capacity | Central Valley | Stockton | LOCKEFORD 2102 | 163682102 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1621102_Capacity | Central Valley | Stockton | LODI BANK 2 | 1621102 | Bank | Demand Growth | Capacity | 2023 | 114.6% | 2.88 | 14.58% | 19.75 | 22.03 | 111.5% | 2.28 | 11.54% | 19.75 | 22.17 | 112.3% | 2.42 | 12.25% | 19.75 | 22.3 | 112.9% | 2.55 | 12.91% | 19.75 | 22.47 | 113.8% | 2.72 | 13.77% | 19.75 | 22.63 | 114.6% | 2.88 | 14.58%
GNA_162111101_Capacity | Central Valley | Stockton | LODI 1101 | 162111101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162111102_Capacity | Central Valley | Stockton | LODI 1102 | 162111102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1637003_Capacity | Central Valley | Stockton | METTLER BANK 3 | 1637003 | Bank | None | None | None | 77.88% | 0 | 0% | 10.4 | 8.04 | 77.31% | 0 | 0% | 10.4 | 8.03 | 77.21% | 0 | 0% | 10.4 | 8.02 | 77.12% | 0 | 0% | 10.4 | 8.04 | 77.31% | 0 | 0% | 10.4 | 8.1 | 77.88% | 0 | 0%
GNA_163701109_Capacity | Central Valley | Stockton | METTLER 1109 | 163701109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163701110_Capacity | Central Valley | Stockton | METTLER 1110 | 163701110 | Feeder | None | None | None | 40.95% | 0 | 0% | 10.28 | 4.16 | 40.47% | 0 | 0% | 10.28 | 4.15 | 40.37% | 0 | 0% | 10.28 | 4.15 | 40.37% | 0 | 0% | 10.28 | 4.17 | 40.56% | 0 | 0% | 10.28 | 4.21 | 40.95% | 0 | 0%
GNA_1620801_Capacity | Central Valley | Stockton | NEW HOPE BANK 1 | 1620801 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162081101_Capacity | Central Valley | Stockton | NEW HOPE 1101 | 162081101 | Feeder | None | None | None | 73.39% | 0 | 0% | 3.72 | 2.52 | 67.74% | 0 | 0% | 3.72 | 2.66 | 71.51% | 0 | 0% | 3.72 | 2.65 | 71.24% | 0 | 0% | 3.72 | 2.72 | 73.12% | 0 | 0% | 3.72 | 2.73 | 73.39% | 0 | 0%
GNA_162081102_Capacity | Central Valley | Stockton | NEW HOPE 1102 | 162081102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1630201_Capacity | Central Valley | Stockton | TERMINOUS BANK 1 | 1630201 | Bank | None | None | None | 87.99% | 0 | 0% | 5.41 | 4.76 | 87.99% | 0 | 0% | 5.41 | 4.74 | 87.62% | 0 | 0% | 5.41 | 4.73 | 87.43% | 0 | 0% | 5.41 | 4.72 | 87.25% | 0 | 0% | 5.41 | 4.72 | 87.25% | 0 | 0%
GNA_163021102_Capacity | Central Valley | Stockton | TERMINOUS 1102 | 163021102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163021103_Capacity | Central Valley | Stockton | TERMINOUS 1103 | 163021103 | Feeder | None | None | None | 31.37% | 0 | 0% | 8.13 | 2.54 | 31.24% | 0 | 0% | 8.13 | 2.54 | 31.24% | 0 | 0% | 8.13 | 2.54 | 31.24% | 0 | 0% | 8.13 | 2.55 | 31.37% | 0 | 0% | 8.13 | 2.55 | 31.37% | 0 | 0%
GNA_1632801_Capacity | Central Valley | Stockton | VICTOR BANK 1 | 1632801 | Bank | None | None | None | 45.79% | 0 | 0% | 29.7 | 13.51 | 45.49% | 0 | 0% | 29.7 | 13.5 | 45.45% | 0 | 0% | 29.7 | 13.51 | 45.49% | 0 | 0% | 29.7 | 13.54 | 45.59% | 0 | 0% | 29.7 | 13.6 | 45.79% | 0 | 0%
GNA_163281101_Capacity | Central Valley | Stockton | VICTOR 1101 | 163281101 | Feeder | None | None | None | 73.54% | 0 | 0% | 8.92 | 6.56 | 73.54% | 0 | 0% | 8.92 | 6.54 | 73.32% | 0 | 0% | 8.92 | 6.5 | 72.87% | 0 | 0% | 8.92 | 6.49 | 72.76% | 0 | 0% | 8.92 | 6.51 | 72.98% | 0 | 0%
GNA_163281102_Capacity | Central Valley | Stockton | VICTOR 1102 | 163281102 | Feeder | None | None | None | 68.1% | 0 | 0% | 10.69 | 7.28 | 68.1% | 0 | 0% | 10.69 | 7.27 | 68.01% | 0 | 0% | 10.69 | 7.26 | 67.91% | 0 | 0% | 10.69 | 7.27 | 68.01% | 0 | 0% | 10.69 | 7.28 | 68.1% | 0 | 0%
GNA_1635701_Capacity | Central Valley | Stockton | AVENA BANK 1 | 1635701 | Bank | Demand Growth | Capacity | 2023 | 103.8% | 0.57 | 3.8% | 15 | 15.3 | 102% | 0.3 | 2% | 15 | 15.33 | 102.2% | 0.33 | 2.2% | 15 | 15.38 | 102.5% | 0.38 | 2.533% | 15 | 15.46 | 103.1% | 0.46 | 3.067% | 15 | 15.57 | 103.8% | 0.57 | 3.8%
GNA_163571701_Capacity | Central Valley | Stockton | AVENA 1701 | 163571701 | Feeder | None | None | None | 64.57% | 0 | 0% | 13.86 | 8.66 | 62.48% | 0 | 0% | 13.86 | 8.71 | 62.84% | 0 | 0% | 13.86 | 8.77 | 63.28% | 0 | 0% | 13.86 | 8.85 | 63.85% | 0 | 0% | 13.86 | 8.95 | 64.57% | 0 | 0%
GNA_163571702_Capacity | Central Valley | Stockton | AVENA 1702 | 163571702 | Feeder | None | None | None | 60.46% | 0 | 0% | 13.86 | 8.38 | 60.46% | 0 | 0% | 13.86 | 8.32 | 60.03% | 0 | 0% | 13.86 | 8.28 | 59.74% | 0 | 0% | 13.86 | 8.23 | 59.38% | 0 | 0% | 13.86 | 8.2 | 59.16% | 0 | 0%
GNA_1626105_Capacity | Central Valley | Stockton | MANTECA BANK 5 | 1626105 | Bank | Demand Growth | Capacity | 2023 | 105.6% | 1.48 | 5.598% | 26.44 | 27.51 | 104% | 1.07 | 4.047% | 26.44 | 27.4 | 103.6% | 0.96 | 3.631% | 26.44 | 27.52 | 104.1% | 1.08 | 4.085% | 26.44 | 27.68 | 104.7% | 1.24 | 4.69% | 26.44 | 27.92 | 105.6% | 1.48 | 5.598%
GNA_162611702_Capacity | Central Valley | Stockton | MANTECA 1702 | 162611702 | Feeder | None | None | None | 77.04% | 0 | 0% | 16.81 | 12.95 | 77.04% | 0 | 0% | 16.81 | 12.75 | 75.85% | 0 | 0% | 16.81 | 12.77 | 75.97% | 0 | 0% | 16.81 | 12.78 | 76.03% | 0 | 0% | 16.81 | 12.83 | 76.32% | 0 | 0%
GNA_162611703_Capacity | Central Valley | Stockton | MANTECA 1703 | 162611703 | Feeder | None | None | None | 82.39% | 0 | 0% | 16.81 | 13.35 | 79.42% | 0 | 0% | 16.81 | 13.43 | 79.89% | 0 | 0% | 16.81 | 13.53 | 80.49% | 0 | 0% | 16.81 | 13.67 | 81.32% | 0 | 0% | 16.81 | 13.85 | 82.39% | 0 | 0%
GNA_1626106_Capacity | Central Valley | Stockton | MANTECA BANK 6 | 1626106 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162611704_Capacity | Central Valley | Stockton | MANTECA 1704 | 162611704 | Feeder | None | None | None | 57.94% | 0 | 0% | 16.81 | 9.74 | 57.94% | 0 | 0% | 16.81 | 8.92 | 53.06% | 0 | 0% | 16.81 | 9.01 | 53.6% | 0 | 0% | 16.81 | 9.11 | 54.19% | 0 | 0% | 16.81 | 9.24 | 54.97% | 0 | 0%
GNA_162611705_Capacity | Central Valley | Stockton | MANTECA 1705 | 162611705 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1626107_Capacity | Central Valley | Stockton | MANTECA BANK 7 | 1626107 | Bank | Demand Growth | Capacity | 2023 | 104.8% | 1.44 | 4.848% | 29.7 | 30.21 | 101.7% | 0.51 | 1.717% | 29.7 | 30.29 | 102% | 0.59 | 1.987% | 29.7 | 30.47 | 102.6% | 0.77 | 2.593% | 29.7 | 30.77 | 103.6% | 1.07 | 3.603% | 29.7 | 31.14 | 104.8% | 1.44 | 4.848%
GNA_162611701_Capacity | Central Valley | Stockton | MANTECA 1701 | 162611701 | Feeder | None | None | None | 98.87% | 0 | 0% | 16.81 | 16.45 | 97.86% | 0 | 0% | 16.81 | 16.47 | 97.98% | 0 | 0% | 16.81 | 16.47 | 97.98% | 0 | 0% | 16.81 | 16.53 | 98.33% | 0 | 0% | 16.81 | 16.62 | 98.87% | 0 | 0%
GNA_162611706_Capacity | Central Valley | Stockton | MANTECA 1706 | 162611706 | Feeder | None | None | None | 91.43% | 0 | 0% | 15.63 | 13.76 | 88.04% | 0 | 0% | 15.63 | 13.84 | 88.55% | 0 | 0% | 15.63 | 13.96 | 89.32% | 0 | 0% | 15.63 | 14.11 | 90.28% | 0 | 0% | 15.63 | 14.29 | 91.43% | 0 | 0%
GNA_1626108_Capacity | Central Valley | Stockton | MANTECA BANK 8 | 1626108 | Bank | Demand Growth | Capacity | 2023 | 111.5% | 3.43 | 11.55% | 29.7 | 32.3 | 108.8% | 2.6 | 8.754% | 29.7 | 32.41 | 109.1% | 2.71 | 9.125% | 29.7 | 32.57 | 109.7% | 2.87 | 9.663% | 29.7 | 32.76 | 110.3% | 3.06 | 10.3% | 29.7 | 33.13 | 111.5% | 3.43 | 11.55%
GNA_162611707_Capacity | Central Valley | Stockton | MANTECA 1707 | 162611707 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162611708_Capacity | Central Valley | Stockton | MANTECA 1708 | 162611708 | Feeder | Demand Growth | Capacity | 2023 | 106.9% | 1.29 | 6.876% | 18.76 | 20.05 | 106.9% | 1.29 | 6.876% | 18.76 | 19.95 | 106.3% | 1.19 | 6.343% | 18.76 | 19.87 | 105.9% | 1.11 | 5.917% | 18.76 | 19.87 | 105.9% | 1.11 | 5.917% | 18.76 | 20.04 | 106.8% | 1.28 | 6.823%
GNA_1638001_Capacity | Central Valley | Stockton | RIPON BANK 1 | 1638001 | Bank | None | None | None | 63.42% | 0 | 0% | 44.5 | 27.3 | 61.35% | 0 | 0% | 44.5 | 28.22 | 63.42% | 0 | 0% | 44.5 | 28.05 | 63.03% | 0 | 0% | 44.5 | 27.93 | 62.76% | 0 | 0% | 44.5 | 27.87 | 62.63% | 0 | 0%
GNA_163801701_Capacity | Central Valley | Stockton | RIPON 1701 | 163801701 | Feeder | None | None | None | 96.05% | 0 | 0% | 14.42 | 12.85 | 89.11% | 0 | 0% | 14.42 | 13.85 | 96.05% | 0 | 0% | 14.42 | 13.74 | 95.28% | 0 | 0% | 14.42 | 13.64 | 94.59% | 0 | 0% | 14.42 | 13.57 | 94.11% | 0 | 0%
GNA_163801703_Capacity | Central Valley | Stockton | RIPON 1703 | 163801703 | Feeder | None | None | None | 93.97% | 0 | 0% | 14.42 | 13.55 | 93.97% | 0 | 0% | 14.42 | 13.43 | 93.13% | 0 | 0% | 14.42 | 13.33 | 92.44% | 0 | 0% | 14.42 | 13.28 | 92.09% | 0 | 0% | 14.42 | 13.28 | 92.09% | 0 | 0%
GNA_1638002_Capacity | Central Valley | Stockton | RIPON BANK 2 | 1638002 | Bank | Demand Growth | Capacity | 2025 | 103.6% | 1 | 3.61% | 27.7 | 27.41 | 98.95% | 0 | 0% | 27.7 | 27.65 | 99.82% | 0 | 0% | 27.7 | 27.84 | 100.5% | 0.14 | 0.5054% | 27.7 | 28.22 | 101.9% | 0.52 | 1.877% | 27.7 | 28.7 | 103.6% | 1 | 3.61%
GNA_163801702_Capacity | Central Valley | Stockton | RIPON 1702 | 163801702 | Feeder | None | None | None | 93.28% | 0 | 0% | 15.63 | 13.86 | 88.68% | 0 | 0% | 15.63 | 13.96 | 89.32% | 0 | 0% | 15.63 | 14 | 89.57% | 0 | 0% | 15.63 | 14.25 | 91.17% | 0 | 0% | 15.63 | 14.58 | 93.28% | 0 | 0%
GNA_163801704_Capacity | Central Valley | Stockton | RIPON 1704 | 163801704 | Feeder | Demand Growth | Capacity | 2023 | 115.1% | 2.18 | 15.12% | 14.42 | 15.97 | 110.7% | 1.55 | 10.75% | 14.42 | 16.09 | 111.6% | 1.67 | 11.58% | 14.42 | 16.22 | 112.5% | 1.8 | 12.48% | 14.42 | 16.4 | 113.7% | 1.98 | 13.73% | 14.42 | 16.6 | 115.1% | 2.18 | 15.12%
GNA_1627001_Capacity | Central Valley | Stockton | VIERRA BANK 1 | 1627001 | Bank | None | None | None | 96.43% | 0 | 0% | 44.6 | 40.96 | 91.84% | 0 | 0% | 44.6 | 41.59 | 93.25% | 0 | 0% | 44.6 | 41.91 | 93.97% | 0 | 0% | 44.6 | 42.4 | 95.07% | 0 | 0% | 44.6 | 43.01 | 96.43% | 0 | 0%
GNA_162701701_Capacity | Central Valley | Stockton | VIERRA 1701 | 162701701 | Feeder | None | None | None | 95.25% | 0 | 0% | 17.05 | 15.57 | 91.32% | 0 | 0% | 17.05 | 15.69 | 92.02% | 0 | 0% | 17.05 | 15.8 | 92.67% | 0 | 0% | 17.05 | 16.01 | 93.9% | 0 | 0% | 17.05 | 16.24 | 95.25% | 0 | 0%
GNA_162701702_Capacity | Central Valley | Stockton | VIERRA 1702 | 162701702 | Feeder | Demand Growth | Capacity | 2023 | 107.9% | 1.34 | 7.859% | 17.05 | 17.72 | 103.9% | 0.67 | 3.93% | 17.05 | 18.08 | 106% | 1.03 | 6.041% | 17.05 | 18.16 | 106.5% | 1.11 | 6.51% | 17.05 | 18.26 | 107.1% | 1.21 | 7.097% | 17.05 | 18.39 | 107.9% | 1.34 | 7.859%
GNA_162701703_Capacity | Central Valley | Stockton | VIERRA 1703 | 162701703 | Feeder | None | None | None | 78.09% | 0 | 0% | 18.76 | 14.06 | 74.95% | 0 | 0% | 18.76 | 14.16 | 75.48% | 0 | 0% | 18.76 | 14.28 | 76.12% | 0 | 0% | 18.76 | 14.43 | 76.92% | 0 | 0% | 18.76 | 14.65 | 78.09% | 0 | 0%
GNA_1627002_Capacity | Central Valley | Stockton | VIERRA BANK 2 | 1627002 | Bank | Demand Growth | Capacity | 2024 | 118.8% | 8.35 | 18.75% | 44.53 | 43.45 | 97.57% | 0 | 0% | 44.53 | 48.52 | 109% | 3.99 | 8.96% | 44.53 | 50.65 | 113.7% | 6.12 | 13.74% | 44.53 | 52.5 | 117.9% | 7.97 | 17.9% | 44.53 | 52.88 | 118.8% | 8.35 | 18.75%
GNA_162701706_Capacity | Central Valley | Stockton | VIERRA 1706 | 162701706 | Feeder | Demand Growth | Capacity | 2023 | 164% | 10.82 | 64.02% | 16.9 | 22.95 | 135.8% | 6.05 | 35.8% | 16.9 | 26.31 | 155.7% | 9.41 | 55.68% | 16.9 | 27.44 | 162.4% | 10.54 | 62.37% | 16.9 | 27.56 | 163.1% | 10.66 | 63.08% | 16.9 | 27.72 | 164% | 10.82 | 64.02%
GNA_162701707_Capacity | Central Valley | Stockton | VIERRA 1707 | 162701707 | Feeder | Demand Growth | Capacity | 2027 | 100.8% | 0.13 | 0.7625% | 17.05 | 12.51 | 73.37% | 0 | 0% | 17.05 | 14.23 | 83.46% | 0 | 0% | 17.05 | 15.23 | 89.33% | 0 | 0% | 17.05 | 16.97 | 99.53% | 0 | 0% | 17.05 | 17.18 | 100.8% | 0.13 | 0.7625%
GNA_1620901_Capacity | Central Valley | Stockton | MIDDLE RIVER BANK 1 | 1620901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162091101_Capacity | Central Valley | Stockton | MIDDLE RIVER 1101 | 162091101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162091102_Capacity | Central Valley | Stockton | MIDDLE RIVER 1102 | 162091102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162091103_Capacity | Central Valley | Stockton | MIDDLE RIVER 1103 | 162091103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1630701_Capacity | Central Valley | Stockton | CHANNEL BANK 1 | 1630701 | Bank | None | None | None | 92.07% | 0 | 0% | 12.36 | 11.25 | 91.02% | 0 | 0% | 12.36 | 11.25 | 91.02% | 0 | 0% | 12.36 | 11.23 | 90.86% | 0 | 0% | 12.36 | 11.26 | 91.1% | 0 | 0% | 12.36 | 11.38 | 92.07% | 0 | 0%
GNA_163071101_Capacity | Central Valley | Stockton | CHANNEL 1101 | 163071101 | Feeder | None | None | None | 88.19% | 0 | 0% | 10.16 | 8.79 | 86.52% | 0 | 0% | 10.16 | 8.84 | 87.01% | 0 | 0% | 10.16 | 8.88 | 87.4% | 0 | 0% | 10.16 | 8.93 | 87.89% | 0 | 0% | 10.16 | 8.96 | 88.19% | 0 | 0%
GNA_163071102_Capacity | Central Valley | Stockton | CHANNEL 1102 | 163071102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1636501_Capacity | Central Valley | Stockton | CHEROKEE BANK 1 | 1636501 | Bank | None | None | None | 99.12% | 0 | 0% | 15.84 | 15.59 | 98.42% | 0 | 0% | 15.84 | 15.7 | 99.12% | 0 | 0% | 15.84 | 14.57 | 91.98% | 0 | 0% | 15.84 | 14.7 | 92.8% | 0 | 0% | 15.84 | 14.83 | 93.62% | 0 | 0%
GNA_163651101_Capacity | Central Valley | Stockton | CHEROKEE 1101 | 163651101 | Feeder | None | None | None | 80.61% | 0 | 0% | 10.16 | 8.14 | 80.12% | 0 | 0% | 10.16 | 8.19 | 80.61% | 0 | 0% | 10.16 | 7.03 | 69.19% | 0 | 0% | 10.16 | 7.1 | 69.88% | 0 | 0% | 10.16 | 7.15 | 70.37% | 0 | 0%
GNA_163651102_Capacity | Central Valley | Stockton | CHEROKEE 1102 | 163651102 | Feeder | None | None | None | 84.65% | 0 | 0% | 10.16 | 8.27 | 81.4% | 0 | 0% | 10.16 | 8.35 | 82.19% | 0 | 0% | 10.16 | 8.41 | 82.78% | 0 | 0% | 10.16 | 8.5 | 83.66% | 0 | 0% | 10.16 | 8.6 | 84.65% | 0 | 0%
GNA_1631202_Capacity | Central Valley | Stockton | COUNTRY CLUB BANK 2 | 1631202 | Bank | None | None | None | 85% | 0 | 0% | 10.4 | 8.84 | 85% | 0 | 0% | 10.4 | 8.75 | 84.13% | 0 | 0% | 10.4 | 8.68 | 83.46% | 0 | 0% | 10.4 | 8.69 | 83.56% | 0 | 0% | 10.4 | 8.78 | 84.42% | 0 | 0%
GNA_163121101_Capacity | Central Valley | Stockton | COUNTRY CLUB 1101 | 163121101 | Feeder | None | None | None | 58.37% | 0 | 0% | 10.16 | 5.93 | 58.37% | 0 | 0% | 10.16 | 5.85 | 57.58% | 0 | 0% | 10.16 | 5.79 | 56.99% | 0 | 0% | 10.16 | 5.79 | 56.99% | 0 | 0% | 10.16 | 5.82 | 57.28% | 0 | 0%
GNA_163121102_Capacity | Central Valley | Stockton | COUNTRY CLUB 1102 | 163121102 | Feeder | None | None | None | 49.21% | 0 | 0% | 10.16 | 5 | 49.21% | 0 | 0% | 10.16 | 4.99 | 49.11% | 0 | 0% | 10.16 | 4.98 | 49.02% | 0 | 0% | 10.16 | 4.99 | 49.11% | 0 | 0% | 10.16 | 4.99 | 49.11% | 0 | 0%
GNA_1631203_Capacity | Central Valley | Stockton | COUNTRY CLUB BANK 3 | 1631203 | Bank | None | None | None | 68.85% | 0 | 0% | 10.4 | 6.79 | 65.29% | 0 | 0% | 10.4 | 6.85 | 65.87% | 0 | 0% | 10.4 | 6.93 | 66.63% | 0 | 0% | 10.4 | 7.04 | 67.69% | 0 | 0% | 10.4 | 7.16 | 68.85% | 0 | 0%
GNA_163121103_Capacity | Central Valley | Stockton | COUNTRY CLUB 1103 | 163121103 | Feeder | None | None | None | 59.74% | 0 | 0% | 10.16 | 5.61 | 55.22% | 0 | 0% | 10.16 | 5.71 | 56.2% | 0 | 0% | 10.16 | 5.83 | 57.38% | 0 | 0% | 10.16 | 5.93 | 58.37% | 0 | 0% | 10.16 | 6.07 | 59.74% | 0 | 0%
GNA_163121104_Capacity | Central Valley | Stockton | COUNTRY CLUB 1104 | 163121104 | Feeder | None | None | None | 48.43% | 0 | 0% | 10.16 | 4.92 | 48.43% | 0 | 0% | 10.16 | 4.88 | 48.03% | 0 | 0% | 10.16 | 4.84 | 47.64% | 0 | 0% | 10.16 | 4.85 | 47.74% | 0 | 0% | 10.16 | 4.83 | 47.54% | 0 | 0%
GNA_1631204_Capacity | Central Valley | Stockton | COUNTRY CLUB BANK 4 | 1631204 | Bank | None | None | None | 67.89% | 0 | 0% | 13.86 | 9.41 | 67.89% | 0 | 0% | 13.86 | 9.33 | 67.32% | 0 | 0% | 13.86 | 9.23 | 66.59% | 0 | 0% | 13.86 | 9.23 | 66.59% | 0 | 0% | 13.86 | 9.24 | 66.67% | 0 | 0%
GNA_163121105_Capacity | Central Valley | Stockton | COUNTRY CLUB 1105 | 163121105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163121106_Capacity | Central Valley | Stockton | COUNTRY CLUB 1106 | 163121106 | Feeder | None | None | None | 58.72% | 0 | 0% | 10.95 | 6.43 | 58.72% | 0 | 0% | 10.95 | 6.36 | 58.08% | 0 | 0% | 10.95 | 6.28 | 57.35% | 0 | 0% | 10.95 | 6.29 | 57.44% | 0 | 0% | 10.95 | 6.3 | 57.53% | 0 | 0%
GNA_1633001_Capacity | Central Valley | Stockton | HAMMER BANK 1 | 1633001 | Bank | None | None | None | 62.59% | 0 | 0% | 29.7 | 18.59 | 62.59% | 0 | 0% | 29.7 | 18.54 | 62.42% | 0 | 0% | 29.7 | 18.46 | 62.15% | 0 | 0% | 29.7 | 18.4 | 61.95% | 0 | 0% | 29.7 | 18.38 | 61.89% | 0 | 0%
GNA_163301101_Capacity | Central Valley | Stockton | HAMMER 1101 | 163301101 | Feeder | None | None | None | 58.28% | 0 | 0% | 10.69 | 6.23 | 58.28% | 0 | 0% | 10.69 | 6.21 | 58.09% | 0 | 0% | 10.69 | 6.18 | 57.81% | 0 | 0% | 10.69 | 6.15 | 57.53% | 0 | 0% | 10.69 | 6.14 | 57.44% | 0 | 0%
GNA_163301102_Capacity | Central Valley | Stockton | HAMMER 1102 | 163301102 | Feeder | None | None | None | 75.63% | 0 | 0% | 11.2 | 8.47 | 75.63% | 0 | 0% | 11.2 | 8.45 | 75.45% | 0 | 0% | 11.2 | 8.42 | 75.18% | 0 | 0% | 11.2 | 8.4 | 75% | 0 | 0% | 11.2 | 8.41 | 75.09% | 0 | 0%
GNA_163301103_Capacity | Central Valley | Stockton | HAMMER 1103 | 163301103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1633002_Capacity | Central Valley | Stockton | HAMMER BANK 2 | 1633002 | Bank | None | None | None | 85.2% | 0 | 0% | 25.4 | 21.64 | 85.2% | 0 | 0% | 25.4 | 21.51 | 84.69% | 0 | 0% | 25.4 | 21.39 | 84.21% | 0 | 0% | 25.4 | 21.31 | 83.9% | 0 | 0% | 25.4 | 21.33 | 83.98% | 0 | 0%
GNA_163301104_Capacity | Central Valley | Stockton | HAMMER 1104 | 163301104 | Feeder | None | None | None | 68.49% | 0 | 0% | 10.76 | 7.37 | 68.49% | 0 | 0% | 10.76 | 7.31 | 67.94% | 0 | 0% | 10.76 | 7.25 | 67.38% | 0 | 0% | 10.76 | 7.23 | 67.19% | 0 | 0% | 10.76 | 7.22 | 67.1% | 0 | 0%
GNA_163301105_Capacity | Central Valley | Stockton | HAMMER 1105 | 163301105 | Feeder | None | None | None | 48.01% | 0 | 0% | 12.83 | 6.16 | 48.01% | 0 | 0% | 12.83 | 6.11 | 47.62% | 0 | 0% | 12.83 | 6.07 | 47.31% | 0 | 0% | 12.83 | 6.06 | 47.23% | 0 | 0% | 12.83 | 6.09 | 47.47% | 0 | 0%
GNA_163301106_Capacity | Central Valley | Stockton | HAMMER 1106 | 163301106 | Feeder | None | None | None | 62.36% | 0 | 0% | 10.76 | 6.71 | 62.36% | 0 | 0% | 10.76 | 6.69 | 62.17% | 0 | 0% | 10.76 | 6.66 | 61.9% | 0 | 0% | 10.76 | 6.62 | 61.52% | 0 | 0% | 10.76 | 6.63 | 61.62% | 0 | 0%
GNA_1633003_Capacity | Central Valley | Stockton | HAMMER BANK 3 | 1633003 | Bank | None | None | None | 62.84% | 0 | 0% | 19.7 | 12.38 | 62.84% | 0 | 0% | 19.7 | 12.31 | 62.49% | 0 | 0% | 19.7 | 12.27 | 62.28% | 0 | 0% | 19.7 | 12.26 | 62.23% | 0 | 0% | 19.7 | 12.28 | 62.34% | 0 | 0%
GNA_163301108_Capacity | Central Valley | Stockton | HAMMER 1108 | 163301108 | Feeder | None | None | None | 70.63% | 0 | 0% | 10.76 | 7.6 | 70.63% | 0 | 0% | 10.76 | 7.51 | 69.8% | 0 | 0% | 10.76 | 7.45 | 69.24% | 0 | 0% | 10.76 | 7.41 | 68.87% | 0 | 0% | 10.76 | 7.41 | 68.87% | 0 | 0%
GNA_163301109_Capacity | Central Valley | Stockton | HAMMER 1109 | 163301109 | Feeder | None | None | None | 35.46% | 0 | 0% | 12.83 | 4.55 | 35.46% | 0 | 0% | 12.83 | 4.52 | 35.23% | 0 | 0% | 12.83 | 4.51 | 35.15% | 0 | 0% | 12.83 | 4.5 | 35.07% | 0 | 0% | 12.83 | 4.49 | 35% | 0 | 0%
GNA_1624202_Capacity | Central Valley | Stockton | STAGG BANK 2 | 1624202 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162421101_Capacity | Central Valley | Stockton | STAGG 1101 | 162421101 | Feeder | None | None | None | 80.26% | 0 | 0% | 10.69 | 8.58 | 80.26% | 0 | 0% | 10.69 | 8.48 | 79.33% | 0 | 0% | 10.69 | 8.42 | 78.77% | 0 | 0% | 10.69 | 8.44 | 78.95% | 0 | 0% | 10.69 | 8.5 | 79.51% | 0 | 0%
GNA_162421106_Capacity | Central Valley | Stockton | STAGG 1106 | 162421106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1624203_Capacity | Central Valley | Stockton | STAGG BANK 3 | 1624203 | Bank | None | None | None | 55.89% | 0 | 0% | 24.6 | 13.75 | 55.89% | 0 | 0% | 24.6 | 13.66 | 55.53% | 0 | 0% | 24.6 | 13.56 | 55.12% | 0 | 0% | 24.6 | 13.58 | 55.2% | 0 | 0% | 24.6 | 13.58 | 55.2% | 0 | 0%
GNA_162421103_Capacity | Central Valley | Stockton | STAGG 1103 | 162421103 | Feeder | None | None | None | 63.99% | 0 | 0% | 10.69 | 6.84 | 63.99% | 0 | 0% | 10.69 | 6.82 | 63.8% | 0 | 0% | 10.69 | 6.79 | 63.52% | 0 | 0% | 10.69 | 6.78 | 63.42% | 0 | 0% | 10.69 | 6.77 | 63.33% | 0 | 0%
GNA_162421105_Capacity | Central Valley | Stockton | STAGG 1105 | 162421105 | Feeder | None | None | None | 61.27% | 0 | 0% | 10.69 | 6.55 | 61.27% | 0 | 0% | 10.69 | 6.49 | 60.71% | 0 | 0% | 10.69 | 6.42 | 60.06% | 0 | 0% | 10.69 | 6.44 | 60.24% | 0 | 0% | 10.69 | 6.46 | 60.43% | 0 | 0%
GNA_1631502_Capacity | Central Valley | Stockton | WATERLOO BANK 2 | 1631502 | Bank | None | None | None | 80.67% | 0 | 0% | 10.4 | 8.39 | 80.67% | 0 | 0% | 10.4 | 8.34 | 80.19% | 0 | 0% | 10.4 | 8.33 | 80.1% | 0 | 0% | 10.4 | 8.35 | 80.29% | 0 | 0% | 10.4 | 8.36 | 80.38% | 0 | 0%
GNA_163151101_Capacity | Central Valley | Stockton | WATERLOO 1101 | 163151101 | Feeder | None | None | None | 67.6% | 0 | 0% | 8.55 | 5.78 | 67.6% | 0 | 0% | 8.55 | 5.75 | 67.25% | 0 | 0% | 8.55 | 5.74 | 67.13% | 0 | 0% | 8.55 | 5.73 | 67.02% | 0 | 0% | 8.55 | 5.7 | 66.67% | 0 | 0%
GNA_163151102_Capacity | Central Valley | Stockton | WATERLOO 1102 | 163151102 | Feeder | None | None | None | 33.46% | 0 | 0% | 10.28 | 3.44 | 33.46% | 0 | 0% | 10.28 | 3.43 | 33.37% | 0 | 0% | 10.28 | 3.41 | 33.17% | 0 | 0% | 10.28 | 3.41 | 33.17% | 0 | 0% | 10.28 | 3.44 | 33.46% | 0 | 0%
GNA_1636201_Capacity | Central Valley | Stockton | WEST LANE BANK 1 | 1636201 | Bank | None | None | None | 73.64% | 0 | 0% | 29.7 | 21.3 | 71.72% | 0 | 0% | 29.7 | 21.45 | 72.22% | 0 | 0% | 29.7 | 21.58 | 72.66% | 0 | 0% | 29.7 | 21.69 | 73.03% | 0 | 0% | 29.7 | 21.87 | 73.64% | 0 | 0%
GNA_163621101_Capacity | Central Valley | Stockton | WEST LANE 1101 | 163621101 | Feeder | None | None | None | 65.2% | 0 | 0% | 10.46 | 6.69 | 63.96% | 0 | 0% | 10.46 | 6.72 | 64.24% | 0 | 0% | 10.46 | 6.73 | 64.34% | 0 | 0% | 10.46 | 6.72 | 64.24% | 0 | 0% | 10.46 | 6.82 | 65.2% | 0 | 0%
GNA_163621102_Capacity | Central Valley | Stockton | WEST LANE 1102 | 163621102 | Feeder | None | None | None | 89.48% | 0 | 0% | 10.46 | 9 | 86.04% | 0 | 0% | 10.46 | 9.09 | 86.9% | 0 | 0% | 10.46 | 9.18 | 87.76% | 0 | 0% | 10.46 | 9.26 | 88.53% | 0 | 0% | 10.46 | 9.36 | 89.48% | 0 | 0%
GNA_163621103_Capacity | Central Valley | Stockton | WEST LANE 1103 | 163621103 | Feeder | None | None | None | 61.32% | 0 | 0% | 11.97 | 7.34 | 61.32% | 0 | 0% | 11.97 | 7.32 | 61.15% | 0 | 0% | 11.97 | 7.27 | 60.74% | 0 | 0% | 11.97 | 7.24 | 60.48% | 0 | 0% | 11.97 | 7.21 | 60.23% | 0 | 0%
GNA_1639102_Capacity | Central Valley | Stockton | EIGHT MILE BANK 2 | 1639102 | Bank | None | None | None | 57.76% | 0 | 0% | 44.55 | 24.35 | 54.66% | 0 | 0% | 44.55 | 24.5 | 54.99% | 0 | 0% | 44.55 | 24.64 | 55.31% | 0 | 0% | 44.55 | 25.12 | 56.39% | 0 | 0% | 44.55 | 25.73 | 57.76% | 0 | 0%
GNA_163912104_Capacity | Central Valley | Stockton | EIGHT MILE 2104 | 163912104 | Feeder | None | None | None | 75.41% | 0 | 0% | 21.11 | 15.69 | 74.32% | 0 | 0% | 21.11 | 15.53 | 73.57% | 0 | 0% | 21.11 | 15.49 | 73.38% | 0 | 0% | 21.11 | 15.69 | 74.32% | 0 | 0% | 21.11 | 15.92 | 75.41% | 0 | 0%
GNA_163912105_Capacity | Central Valley | Stockton | EIGHT MILE 2105 | 163912105 | Feeder | None | None | None | 54.71% | 0 | 0% | 21.11 | 10.96 | 51.92% | 0 | 0% | 21.11 | 11.01 | 52.16% | 0 | 0% | 21.11 | 11.06 | 52.39% | 0 | 0% | 21.11 | 11.25 | 53.29% | 0 | 0% | 21.11 | 11.55 | 54.71% | 0 | 0%
GNA_163912106_Capacity | Central Valley | Stockton | EIGHT MILE 2106 | 163912106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1639103_Capacity | Central Valley | Stockton | EIGHT MILE BANK 3 | 1639103 | Bank | None | None | None | 92.53% | 0 | 0% | 44.55 | 39.22 | 88.04% | 0 | 0% | 44.55 | 39.69 | 89.09% | 0 | 0% | 44.55 | 40.21 | 90.26% | 0 | 0% | 44.55 | 40.7 | 91.36% | 0 | 0% | 44.55 | 41.22 | 92.53% | 0 | 0%
GNA_163912101_Capacity | Central Valley | Stockton | EIGHT MILE 2101 | 163912101 | Feeder | None | None | None | 94.67% | 0 | 0% | 18.96 | 17.83 | 94.04% | 0 | 0% | 18.96 | 17.53 | 92.46% | 0 | 0% | 18.96 | 17.47 | 92.14% | 0 | 0% | 18.96 | 17.69 | 93.3% | 0 | 0% | 18.96 | 17.95 | 94.67% | 0 | 0%
GNA_163912102_Capacity | Central Valley | Stockton | EIGHT MILE 2102 | 163912102 | Feeder | None | None | None | 67.04% | 0 | 0% | 18.96 | 12.15 | 64.08% | 0 | 0% | 18.96 | 12.28 | 64.77% | 0 | 0% | 18.96 | 12.41 | 65.45% | 0 | 0% | 18.96 | 12.56 | 66.24% | 0 | 0% | 18.96 | 12.71 | 67.04% | 0 | 0%
GNA_163912103_Capacity | Central Valley | Stockton | EIGHT MILE 2103 | 163912103 | Feeder | None | None | None | 46.1% | 0 | 0% | 18.96 | 7.74 | 40.82% | 0 | 0% | 18.96 | 8.14 | 42.93% | 0 | 0% | 18.96 | 8.57 | 45.2% | 0 | 0% | 18.96 | 8.65 | 45.62% | 0 | 0% | 18.96 | 8.74 | 46.1% | 0 | 0%
GNA_1637201_Capacity | Central Valley | Stockton | MOSHER BANK 1 | 1637201 | Bank | None | None | None | 63.03% | 0 | 0% | 29.7 | 18.72 | 63.03% | 0 | 0% | 29.7 | 18.6 | 62.63% | 0 | 0% | 29.7 | 18.51 | 62.32% | 0 | 0% | 29.7 | 18.54 | 62.42% | 0 | 0% | 29.7 | 18.6 | 62.63% | 0 | 0%
GNA_163722105_Capacity | Central Valley | Stockton | MOSHER 2105 | 163722105 | Feeder | None | None | None | 45.36% | 0 | 0% | 18.63 | 8.09 | 43.42% | 0 | 0% | 18.63 | 8.15 | 43.75% | 0 | 0% | 18.63 | 8.23 | 44.18% | 0 | 0% | 18.63 | 8.33 | 44.71% | 0 | 0% | 18.63 | 8.45 | 45.36% | 0 | 0%
GNA_163722104_Capacity | Central Valley | Stockton | MOSHER 2104 | 163722104 | Feeder | None | None | None | 77.08% | 0 | 0% | 18.63 | 14.36 | 77.08% | 0 | 0% | 18.63 | 14.24 | 76.44% | 0 | 0% | 18.63 | 14.11 | 75.74% | 0 | 0% | 18.63 | 13.99 | 75.09% | 0 | 0% | 18.63 | 13.85 | 74.34% | 0 | 0%
GNA_1637202_Capacity | Central Valley | Stockton | MOSHER BANK 2 | 1637202 | Bank | None | None | None | 79.7% | 0 | 0% | 29.7 | 23.57 | 79.36% | 0 | 0% | 29.7 | 23.54 | 79.26% | 0 | 0% | 29.7 | 23.51 | 79.16% | 0 | 0% | 29.7 | 23.55 | 79.29% | 0 | 0% | 29.7 | 23.67 | 79.7% | 0 | 0%
GNA_163722107_Capacity | Central Valley | Stockton | MOSHER 2107 | 163722107 | Feeder | None | None | None | 48.59% | 0 | 0% | 21.22 | 10.31 | 48.59% | 0 | 0% | 21.22 | 10.27 | 48.4% | 0 | 0% | 21.22 | 10.22 | 48.16% | 0 | 0% | 21.22 | 10.2 | 48.07% | 0 | 0% | 21.22 | 10.17 | 47.93% | 0 | 0%
GNA_163722108_Capacity | Central Valley | Stockton | MOSHER 2108 | 163722108 | Feeder | None | None | None | 77.45% | 0 | 0% | 21.11 | 16.11 | 76.31% | 0 | 0% | 21.11 | 16.12 | 76.36% | 0 | 0% | 21.11 | 16.14 | 76.46% | 0 | 0% | 21.11 | 16.21 | 76.79% | 0 | 0% | 21.11 | 16.35 | 77.45% | 0 | 0%
GNA_1637203_Capacity | Central Valley | Stockton | MOSHER BANK 3 | 1637203 | Bank | None | None | None | 51.8% | 0 | 0% | 44.52 | 21.67 | 48.67% | 0 | 0% | 44.52 | 21.66 | 48.65% | 0 | 0% | 44.52 | 22.88 | 51.39% | 0 | 0% | 44.52 | 22.96 | 51.57% | 0 | 0% | 44.52 | 23.06 | 51.8% | 0 | 0%
GNA_163722110_Capacity | Central Valley | Stockton | MOSHER 2110 | 163722110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163722111_Capacity | Central Valley | Stockton | MOSHER 2111 | 163722111 | Feeder | None | None | None | 77.16% | 0 | 0% | 21.41 | 15.05 | 70.29% | 0 | 0% | 21.41 | 15.07 | 70.39% | 0 | 0% | 21.41 | 16.3 | 76.13% | 0 | 0% | 21.41 | 16.4 | 76.6% | 0 | 0% | 21.41 | 16.52 | 77.16% | 0 | 0%
GNA_1624205_Capacity | Central Valley | Stockton | STAGG BANK 5 | 1624205 | Bank | None | None | None | 57.9% | 0 | 0% | 74.23 | 42.03 | 56.62% | 0 | 0% | 74.23 | 41.34 | 55.69% | 0 | 0% | 74.23 | 41 | 55.23% | 0 | 0% | 74.23 | 41.97 | 56.54% | 0 | 0% | 74.23 | 42.98 | 57.9% | 0 | 0%
GNA_162422103_Capacity | Central Valley | Stockton | STAGG 2103 | 162422103 | Feeder | None | None | None | 52.6% | 0 | 0% | 20 | 10.52 | 52.6% | 0 | 0% | 20 | 10.29 | 51.45% | 0 | 0% | 20 | 10.12 | 50.6% | 0 | 0% | 20 | 10.02 | 50.1% | 0 | 0% | 20 | 10.01 | 50.05% | 0 | 0%
GNA_162422104_Capacity | Central Valley | Stockton | STAGG 2104 | 162422104 | Feeder | None | None | None | 88.6% | 0 | 0% | 21.22 | 17.11 | 80.63% | 0 | 0% | 21.22 | 16.92 | 79.74% | 0 | 0% | 21.22 | 16.91 | 79.69% | 0 | 0% | 21.22 | 17.87 | 84.21% | 0 | 0% | 21.22 | 18.8 | 88.6% | 0 | 0%
GNA_162422105_Capacity | Central Valley | Stockton | STAGG 2105 | 162422105 | Feeder | None | None | None | 66.09% | 0 | 0% | 21.41 | 14.15 | 66.09% | 0 | 0% | 21.41 | 13.91 | 64.97% | 0 | 0% | 21.41 | 13.81 | 64.5% | 0 | 0% | 21.41 | 13.87 | 64.78% | 0 | 0% | 21.41 | 13.96 | 65.2% | 0 | 0%
GNA_1624206_Capacity | Central Valley | Stockton | STAGG BANK 6 | 1624206 | Bank | None | None | None | 62.29% | 0 | 0% | 74.23 | 46.24 | 62.29% | 0 | 0% | 74.23 | 46.05 | 62.04% | 0 | 0% | 74.23 | 45.89 | 61.82% | 0 | 0% | 74.23 | 45.94 | 61.89% | 0 | 0% | 74.23 | 46.15 | 62.17% | 0 | 0%
GNA_162422106_Capacity | Central Valley | Stockton | STAGG 2106 | 162422106 | Feeder | None | None | None | 64.35% | 0 | 0% | 18.96 | 12.2 | 64.35% | 0 | 0% | 18.96 | 12 | 63.29% | 0 | 0% | 18.96 | 11.89 | 62.71% | 0 | 0% | 18.96 | 11.88 | 62.66% | 0 | 0% | 18.96 | 11.91 | 62.82% | 0 | 0%
GNA_162422107_Capacity | Central Valley | Stockton | STAGG 2107 | 162422107 | Feeder | None | None | None | 71.5% | 0 | 0% | 20 | 14.02 | 70.1% | 0 | 0% | 20 | 14.03 | 70.15% | 0 | 0% | 20 | 14.08 | 70.4% | 0 | 0% | 20 | 14.16 | 70.8% | 0 | 0% | 20 | 14.3 | 71.5% | 0 | 0%
GNA_162422108_Capacity | Central Valley | Stockton | STAGG 2108 | 162422108 | Feeder | None | None | None | 45.96% | 0 | 0% | 21.41 | 9.84 | 45.96% | 0 | 0% | 21.41 | 9.73 | 45.45% | 0 | 0% | 21.41 | 9.63 | 44.98% | 0 | 0% | 21.41 | 9.61 | 44.89% | 0 | 0% | 21.41 | 9.65 | 45.07% | 0 | 0%
GNA_1631201_Capacity | Central Valley | Stockton | COUNTRY CLUB BANK 1 | 1631201 | Bank | None | None | None | 86.87% | 0 | 0% | 6.93 | 6.02 | 86.87% | 0 | 0% | 6.93 | 5.96 | 86% | 0 | 0% | 6.93 | 5.9 | 85.14% | 0 | 0% | 6.93 | 5.9 | 85.14% | 0 | 0% | 6.93 | 5.94 | 85.71% | 0 | 0%
GNA_163120401_Capacity | Central Valley | Stockton | COUNTRY CLUB 0401 | 163120401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163120402_Capacity | Central Valley | Stockton | COUNTRY CLUB 0402 | 163120402 | Feeder | None | None | None | 99.63% | 0 | 0% | 2.7 | 2.69 | 99.63% | 0 | 0% | 2.7 | 2.67 | 98.89% | 0 | 0% | 2.7 | 2.65 | 98.15% | 0 | 0% | 2.7 | 2.65 | 98.15% | 0 | 0% | 2.7 | 2.69 | 99.63% | 0 | 0%
GNA_163120403_Capacity | Central Valley | Stockton | COUNTRY CLUB 0403 | 163120403 | Feeder | None | None | None | 65.61% | 0 | 0% | 3.14 | 2.06 | 65.61% | 0 | 0% | 3.14 | 2.05 | 65.29% | 0 | 0% | 3.14 | 2.02 | 64.33% | 0 | 0% | 3.14 | 2.01 | 64.01% | 0 | 0% | 3.14 | 2.02 | 64.33% | 0 | 0%
GNA_1632701_Capacity | Central Valley | Stockton | OAK PARK BANK 1 | 1632701 | Bank | None | None | None | 63.21% | 0 | 0% | 3.86 | 2.44 | 63.21% | 0 | 0% | 3.86 | 2.42 | 62.69% | 0 | 0% | 3.86 | 2.4 | 62.18% | 0 | 0% | 3.86 | 2.37 | 61.4% | 0 | 0% | 3.86 | 2.4 | 62.18% | 0 | 0%
GNA_163270401_Capacity | Central Valley | Stockton | OAK PARK 0401 | 163270401 | Feeder | None | None | None | 70.33% | 0 | 0% | 2.73 | 1.92 | 70.33% | 0 | 0% | 2.73 | 1.91 | 69.96% | 0 | 0% | 2.73 | 1.89 | 69.23% | 0 | 0% | 2.73 | 1.87 | 68.5% | 0 | 0% | 2.73 | 1.9 | 69.6% | 0 | 0%
GNA_163270402_Capacity | Central Valley | Stockton | OAK PARK 0402 | 163270402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1632201_Capacity | Central Valley | Stockton | STOCKTON ACRES BANK 1 | 1632201 | Bank | None | None | None | 65.23% | 0 | 0% | 3.71 | 2.42 | 65.23% | 0 | 0% | 3.71 | 2.38 | 64.15% | 0 | 0% | 3.71 | 2.35 | 63.34% | 0 | 0% | 3.71 | 2.34 | 63.07% | 0 | 0% | 3.71 | 2.33 | 62.8% | 0 | 0%
GNA_163220401_Capacity | Central Valley | Stockton | STOCKTON ACRES 0401 | 163220401 | Feeder | None | None | None | 42.8% | 0 | 0% | 2.71 | 1.16 | 42.8% | 0 | 0% | 2.71 | 1.13 | 41.7% | 0 | 0% | 2.71 | 1.12 | 41.33% | 0 | 0% | 2.71 | 1.12 | 41.33% | 0 | 0% | 2.71 | 1.13 | 41.7% | 0 | 0%
GNA_163220402_Capacity | Central Valley | Stockton | STOCKTON ACRES 0402 | 163220402 | Feeder | None | None | None | 50.18% | 0 | 0% | 2.71 | 1.36 | 50.18% | 0 | 0% | 2.71 | 1.35 | 49.82% | 0 | 0% | 2.71 | 1.33 | 49.08% | 0 | 0% | 2.71 | 1.33 | 49.08% | 0 | 0% | 2.71 | 1.32 | 48.71% | 0 | 0%
GNA_1636901_Capacity | Central Valley | Stockton | SALT SPRINGS BANK 2 | 1636901 | Bank | None | None | None | 22.76% | 0 | 0% | 17.62 | 4.01 | 22.76% | 0 | 0% | 17.62 | 3.94 | 22.36% | 0 | 0% | 17.62 | 3.9 | 22.13% | 0 | 0% | 17.62 | 3.91 | 22.19% | 0 | 0% | 17.62 | 3.96 | 22.47% | 0 | 0%
GNA_163692101_Capacity | Central Valley | Stockton | SALT SPRINGS 2101 | 163692101 | Feeder | None | None | None | 34.6% | 0 | 0% | 4.22 | 1.46 | 34.6% | 0 | 0% | 4.22 | 1.45 | 34.36% | 0 | 0% | 4.22 | 1.44 | 34.12% | 0 | 0% | 4.22 | 1.42 | 33.65% | 0 | 0% | 4.22 | 1.42 | 33.65% | 0 | 0%
GNA_1635601_Capacity | Central Valley | Stockton | ALPINE BANK 1 | 1635601 | Bank | None | None | None | 22.15% | 0 | 0% | 3.25 | 0.72 | 22.15% | 0 | 0% | 3.25 | 0.72 | 22.15% | 0 | 0% | 3.25 | 0.72 | 22.15% | 0 | 0% | 3.25 | 0.72 | 22.15% | 0 | 0% | 3.25 | 0.71 | 21.85% | 0 | 0%
GNA_163561101_Capacity | Central Valley | Stockton | ALPINE 1101 | 163561101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163561102_Capacity | Central Valley | Stockton | ALPINE 1102 | 163561102 | Feeder | None | None | None | 24.67% | 0 | 0% | 1.5 | 0.37 | 24.67% | 0 | 0% | 1.5 | 0.36 | 24% | 0 | 0% | 1.5 | 0.36 | 24% | 0 | 0% | 1.5 | 0.36 | 24% | 0 | 0% | 1.5 | 0.36 | 24% | 0 | 0%
GNA_163692102_Capacity | Central Valley | Stockton | SALT SPRINGS 2102 | 163692102 | Feeder | None | None | None | 60.62% | 0 | 0% | 4.85 | 2.88 | 59.38% | 0 | 0% | 4.85 | 2.87 | 59.18% | 0 | 0% | 4.85 | 2.88 | 59.38% | 0 | 0% | 4.85 | 2.89 | 59.59% | 0 | 0% | 4.85 | 2.94 | 60.62% | 0 | 0%
GNA_1631303_Capacity | Central Valley | Stockton | EAST STOCKTON BANK 3 | 1631303 | Bank | Demand Growth | Capacity | 2023 | 108% | 1.27 | 8.018% | 15.84 | 17 | 107.3% | 1.16 | 7.323% | 15.84 | 17.05 | 107.6% | 1.21 | 7.639% | 15.84 | 17.11 | 108% | 1.27 | 8.018% | 15.84 | 17.11 | 108% | 1.27 | 8.018% | 15.84 | 17.08 | 107.8% | 1.24 | 7.828%
GNA_163131101_Capacity | Central Valley | Stockton | EAST STOCKTON 1101 | 163131101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163131102_Capacity | Central Valley | Stockton | EAST STOCKTON 1102 | 163131102 | Feeder | None | None | None | 65.08% | 0 | 0% | 12.83 | 8.33 | 64.93% | 0 | 0% | 12.83 | 8.33 | 64.93% | 0 | 0% | 12.83 | 8.33 | 64.93% | 0 | 0% | 12.83 | 8.34 | 65% | 0 | 0% | 12.83 | 8.35 | 65.08% | 0 | 0%
GNA_1632901_Capacity | Central Valley | Stockton | FRENCH CAMP BANK 1 | 1632901 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163291101_Capacity | Central Valley | Stockton | FRENCH CAMP 1101 | 163291101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163291102_Capacity | Central Valley | Stockton | FRENCH CAMP 1102 | 163291102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1632902_Capacity | Central Valley | Stockton | FRENCH CAMP BANK 2 | 1632902 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163291103_Capacity | Central Valley | Stockton | FRENCH CAMP 1103 | 163291103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163291104_Capacity | Central Valley | Stockton | FRENCH CAMP 1104 | 163291104 | Feeder | Demand Growth | Capacity | 2023 | 110.1% | 1.25 | 10.11% | 12.36 | 13.44 | 108.7% | 1.08 | 8.738% | 12.36 | 13.34 | 107.9% | 0.98 | 7.929% | 12.36 | 13.32 | 107.8% | 0.96 | 7.767% | 12.36 | 13.42 | 108.6% | 1.06 | 8.576% | 12.36 | 13.61 | 110.1% | 1.25 | 10.11%
GNA_1630801_Capacity | Central Valley | Stockton | ROUGH AND READY BANK 1 | 1630801 | Bank | None | None | None | 83.05% | 0 | 0% | 15.1 | 12.32 | 81.59% | 0 | 0% | 15.1 | 12.35 | 81.79% | 0 | 0% | 15.1 | 12.36 | 81.85% | 0 | 0% | 15.1 | 12.45 | 82.45% | 0 | 0% | 15.1 | 12.54 | 83.05% | 0 | 0%
GNA_163081102_Capacity | Central Valley | Stockton | ROUGH AND READY ISLA 1102 | 163081102 | Feeder | None | None | None | 100% | 0 | 0% | 12.62 | 12.4 | 98.26% | 0 | 0% | 12.62 | 12.43 | 98.49% | 0 | 0% | 12.62 | 12.44 | 98.57% | 0 | 0% | 12.62 | 12.52 | 99.21% | 0 | 0% | 12.62 | 12.62 | 100% | 0 | 0%
GNA_1623703_Capacity | Central Valley | Stockton | STOCKTON A BANK 3 | 1623703 | Bank | None | None | None | 96.5% | 0 | 0% | 36.33 | 35.06 | 96.5% | 0 | 0% | 36.33 | 35.05 | 96.48% | 0 | 0% | 36.33 | 35.03 | 96.42% | 0 | 0% | 36.33 | 35.05 | 96.48% | 0 | 0% | 36.33 | 35.06 | 96.5% | 0 | 0%
GNA_162371101_Capacity | Central Valley | Stockton | STOCKTON A 1101 | 162371101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162371102_Capacity | Central Valley | Stockton | STOCKTON A 1102 | 162371102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162371103_Capacity | Central Valley | Stockton | STOCKTON A 1103 | 162371103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162371104_Capacity | Central Valley | Stockton | STOCKTON A 1104 | 162371104 | Feeder | None | None | None | 95.43% | 0 | 0% | 9.19 | 8.77 | 95.43% | 0 | 0% | 9.19 | 8.76 | 95.32% | 0 | 0% | 9.19 | 8.73 | 94.99% | 0 | 0% | 9.19 | 8.73 | 94.99% | 0 | 0% | 9.19 | 8.68 | 94.45% | 0 | 0%
GNA_162371105_Capacity | Central Valley | Stockton | STOCKTON A 1105 | 162371105 | Feeder | None | None | None | 97.51% | 0 | 0% | 11.67 | 11.03 | 94.52% | 0 | 0% | 11.67 | 11.11 | 95.2% | 0 | 0% | 11.67 | 11.18 | 95.8% | 0 | 0% | 11.67 | 11.27 | 96.57% | 0 | 0% | 11.67 | 11.38 | 97.51% | 0 | 0%
GNA_1623704_Capacity | Central Valley | Stockton | STOCKTON A BANK 4 | 1623704 | Bank | Demand Growth | Capacity | 2024 | 113.1% | 3.9 | 13.13% | 29.7 | 27.78 | 93.54% | 0 | 0% | 29.7 | 30.02 | 101.1% | 0.32 | 1.077% | 29.7 | 30.72 | 103.4% | 1.02 | 3.434% | 29.7 | 31.79 | 107% | 2.09 | 7.037% | 29.7 | 33.6 | 113.1% | 3.9 | 13.13%
GNA_162371106_Capacity | Central Valley | Stockton | STOCKTON A 1106 | 162371106 | Feeder | None | None | None | 89.87% | 0 | 0% | 9.77 | 8.78 | 89.87% | 0 | 0% | 9.77 | 8.75 | 89.56% | 0 | 0% | 9.77 | 8.72 | 89.25% | 0 | 0% | 9.77 | 8.7 | 89.05% | 0 | 0% | 9.77 | 8.67 | 88.74% | 0 | 0%
GNA_162371107_Capacity | Central Valley | Stockton | STOCKTON A 1107 | 162371107 | Feeder | Demand Growth | Capacity | 2023 | 134.1% | 4.16 | 34.13% | 12.19 | 12.52 | 102.7% | 0.33 | 2.707% | 12.19 | 12.84 | 105.3% | 0.65 | 5.332% | 12.19 | 13.47 | 110.5% | 1.28 | 10.5% | 12.19 | 14.47 | 118.7% | 2.28 | 18.7% | 12.19 | 16.35 | 134.1% | 4.16 | 34.13%
GNA_162371108_Capacity | Central Valley | Stockton | STOCKTON A 1108 | 162371108 | Feeder | None | None | None | 84.99% | 0 | 0% | 10.46 | 6.62 | 63.29% | 0 | 0% | 10.46 | 8.73 | 83.46% | 0 | 0% | 10.46 | 8.78 | 83.94% | 0 | 0% | 10.46 | 8.85 | 84.61% | 0 | 0% | 10.46 | 8.89 | 84.99% | 0 | 0%
GNA_1623705_Capacity | Central Valley | Stockton | STOCKTON A BANK 5 | 1623705 | Bank | None | None | None | 91.25% | 0 | 0% | 29.7 | 27.1 | 91.25% | 0 | 0% | 29.7 | 26.94 | 90.71% | 0 | 0% | 29.7 | 26.78 | 90.17% | 0 | 0% | 29.7 | 26.73 | 90% | 0 | 0% | 29.7 | 26.78 | 90.17% | 0 | 0%
GNA_162371109_Capacity | Central Valley | Stockton | STOCKTON A 1109 | 162371109 | Feeder | None | None | None | 91.83% | 0 | 0% | 10.16 | 9.33 | 91.83% | 0 | 0% | 10.16 | 9.27 | 91.24% | 0 | 0% | 10.16 | 9.22 | 90.75% | 0 | 0% | 10.16 | 9.21 | 90.65% | 0 | 0% | 10.16 | 9.25 | 91.04% | 0 | 0%
GNA_162371110_Capacity | Central Valley | Stockton | STOCKTON A 1110 | 162371110 | Feeder | None | None | None | 99.75% | 0 | 0% | 12.19 | 12.05 | 98.85% | 0 | 0% | 12.19 | 12.02 | 98.61% | 0 | 0% | 12.19 | 11.99 | 98.36% | 0 | 0% | 12.19 | 12.04 | 98.77% | 0 | 0% | 12.19 | 12.16 | 99.75% | 0 | 0%
GNA_162371111_Capacity | Central Valley | Stockton | STOCKTON A 1111 | 162371111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1634803_Capacity | Central Valley | Stockton | WEBER BANK 3 | 1634803 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163481101_Capacity | Central Valley | Stockton | WEBER 1101 | 163481101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163481105_Capacity | Central Valley | Stockton | WEBER 1105 | 163481105 | Feeder | None | None | None | 93.36% | 0 | 0% | 12.19 | 10.88 | 89.25% | 0 | 0% | 12.19 | 11.32 | 92.86% | 0 | 0% | 12.19 | 11.36 | 93.19% | 0 | 0% | 12.19 | 11.38 | 93.36% | 0 | 0% | 12.19 | 11.35 | 93.11% | 0 | 0%
GNA_1634804_Capacity | Central Valley | Stockton | WEBER BANK 4 | 1634804 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163481113_Capacity | Central Valley | Stockton | WEBER 1113 | 163481113 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163481114_Capacity | Central Valley | Stockton | WEBER 1114 | 163481114 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1634805_Capacity | Central Valley | Stockton | WEBER BANK 5 | 1634805 | Bank | None | None | None | 73.5% | 0 | 0% | 44.6 | 31.33 | 70.25% | 0 | 0% | 44.6 | 32.47 | 72.8% | 0 | 0% | 44.6 | 32.29 | 72.4% | 0 | 0% | 44.6 | 32.5 | 72.87% | 0 | 0% | 44.6 | 32.78 | 73.5% | 0 | 0%
GNA_163481102_Capacity | Central Valley | Stockton | WEBER 1102 | 163481102 | Feeder | Demand Growth | Capacity | 2023 | 105.1% | 0.55 | 5.112% | 10.76 | 11.1 | 103.2% | 0.34 | 3.16% | 10.76 | 11.12 | 103.3% | 0.36 | 3.346% | 10.76 | 11.16 | 103.7% | 0.4 | 3.717% | 10.76 | 11.22 | 104.3% | 0.46 | 4.275% | 10.76 | 11.31 | 105.1% | 0.55 | 5.112%
GNA_163481103_Capacity | Central Valley | Stockton | WEBER 1103 | 163481103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163481107_Capacity | Central Valley | Stockton | WEBER 1107 | 163481107 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163481108_Capacity | Central Valley | Stockton | WEBER 1108 | 163481108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1634806_Capacity | Central Valley | Stockton | WEBER BANK 6 | 1634806 | Bank | Demand Growth | Capacity | 2024 | 145.1% | 20.09 | 45.1% | 44.55 | 44.14 | 99.08% | 0 | 0% | 44.55 | 47.98 | 107.7% | 3.43 | 7.699% | 44.55 | 61.85 | 138.8% | 17.3 | 38.83% | 44.55 | 64.64 | 145.1% | 20.09 | 45.1% | 44.55 | 64.61 | 145% | 20.06 | 45.03%
GNA_163481109_Capacity | Central Valley | Stockton | WEBER 1109 | 163481109 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163481110_Capacity | Central Valley | Stockton | WEBER 1110 | 163481110 | Feeder | Demand Growth | Capacity | 2023 | 275.3% | 21.37 | 175.3% | 12.19 | 15.04 | 123.4% | 2.85 | 23.38% | 12.19 | 18.24 | 149.6% | 6.05 | 49.63% | 12.19 | 30.64 | 251.4% | 18.45 | 151.4% | 12.19 | 33.46 | 274.5% | 21.27 | 174.5% | 12.19 | 33.56 | 275.3% | 21.37 | 175.3%
GNA_163481111_Capacity | Central Valley | Stockton | WEBER NEW 1111 | 163481111 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_164381115_Capacity | Central Valley | Stockton | WEBER NEW 1115 | 164381115 | Feeder | None | None | None | 85.52% | 0 | 0% | 12.36 | 8.8 | 71.2% | 0 | 0% | 12.36 | 8.8 | 71.2% | 0 | 0% | 12.36 | 10.57 | 85.52% | 0 | 0% | 12.36 | 10.57 | 85.52% | 0 | 0% | 12.36 | 10.57 | 85.52% | 0 | 0%
GNA_1631301_Capacity | Central Valley | Stockton | EAST STOCKTON BANK 1 | 1631301 | Bank | None | None | None | 94.23% | 0 | 0% | 8.32 | 7.83 | 94.11% | 0 | 0% | 8.32 | 7.84 | 94.23% | 0 | 0% | 8.32 | 7.83 | 94.11% | 0 | 0% | 8.32 | 7.81 | 93.87% | 0 | 0% | 8.32 | 7.79 | 93.63% | 0 | 0%
GNA_163130401_Capacity | Central Valley | Stockton | EAST STOCKTON 0401 | 163130401 | Feeder | None | None | None | 91.99% | 0 | 0% | 4.12 | 3.78 | 91.75% | 0 | 0% | 4.12 | 3.79 | 91.99% | 0 | 0% | 4.12 | 3.78 | 91.75% | 0 | 0% | 4.12 | 3.77 | 91.5% | 0 | 0% | 4.12 | 3.75 | 91.02% | 0 | 0%
GNA_163130402_Capacity | Central Valley | Stockton | EAST STOCKTON 0402 | 163130402 | Feeder | None | None | None | 96.49% | 0 | 0% | 3.7 | 3.57 | 96.49% | 0 | 0% | 3.7 | 3.56 | 96.22% | 0 | 0% | 3.7 | 3.56 | 96.22% | 0 | 0% | 3.7 | 3.56 | 96.22% | 0 | 0% | 3.7 | 3.57 | 96.49% | 0 | 0%
GNA_1633101_Capacity | Central Valley | Stockton | HARDING BANK 1 | 1633101 | Bank | None | None | None | 86.27% | 0 | 0% | 6.19 | 5.34 | 86.27% | 0 | 0% | 6.19 | 5.29 | 85.46% | 0 | 0% | 6.19 | 5.26 | 84.98% | 0 | 0% | 6.19 | 5.24 | 84.65% | 0 | 0% | 6.19 | 5.21 | 84.17% | 0 | 0%
GNA_163310401_Capacity | Central Valley | Stockton | HARDING 0401 | 163310401 | Feeder | None | None | None | 46.33% | 0 | 0% | 2.18 | 1.01 | 46.33% | 0 | 0% | 2.18 | 1 | 45.87% | 0 | 0% | 2.18 | 1 | 45.87% | 0 | 0% | 2.18 | 0.99 | 45.41% | 0 | 0% | 2.18 | 0.98 | 44.95% | 0 | 0%
GNA_163310402_Capacity | Central Valley | Stockton | HARDING 0402 | 163310402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163310403_Capacity | Central Valley | Stockton | HARDING 0403 | 163310403 | Feeder | None | None | None | 58.06% | 0 | 0% | 2.48 | 1.44 | 58.06% | 0 | 0% | 2.48 | 1.43 | 57.66% | 0 | 0% | 2.48 | 1.42 | 57.26% | 0 | 0% | 2.48 | 1.42 | 57.26% | 0 | 0% | 2.48 | 1.41 | 56.85% | 0 | 0%
GNA_1633102_Capacity | Central Valley | Stockton | HARDING BANK 2 | 1633102 | Bank | None | None | None | 99.52% | 0 | 0% | 6.19 | 6.16 | 99.52% | 0 | 0% | 6.19 | 6.14 | 99.19% | 0 | 0% | 6.19 | 6.1 | 98.55% | 0 | 0% | 6.19 | 6.09 | 98.38% | 0 | 0% | 6.19 | 6.08 | 98.22% | 0 | 0%
GNA_163310404_Capacity | Central Valley | Stockton | HARDING 0404 | 163310404 | Feeder | None | None | None | 79.82% | 0 | 0% | 2.18 | 1.71 | 78.44% | 0 | 0% | 2.18 | 1.72 | 78.9% | 0 | 0% | 2.18 | 1.72 | 78.9% | 0 | 0% | 2.18 | 1.73 | 79.36% | 0 | 0% | 2.18 | 1.74 | 79.82% | 0 | 0%
GNA_163310405_Capacity | Central Valley | Stockton | HARDING 0405 | 163310405 | Feeder | None | None | None | 67.7% | 0 | 0% | 2.91 | 1.97 | 67.7% | 0 | 0% | 2.91 | 1.95 | 67.01% | 0 | 0% | 2.91 | 1.94 | 66.67% | 0 | 0% | 2.91 | 1.93 | 66.32% | 0 | 0% | 2.91 | 1.92 | 65.98% | 0 | 0%
GNA_163310406_Capacity | Central Valley | Stockton | HARDING 0406 | 163310406 | Feeder | None | None | None | 96.37% | 0 | 0% | 2.48 | 2.39 | 96.37% | 0 | 0% | 2.48 | 2.38 | 95.97% | 0 | 0% | 2.48 | 2.35 | 94.76% | 0 | 0% | 2.48 | 2.33 | 93.95% | 0 | 0% | 2.48 | 2.33 | 93.95% | 0 | 0%
GNA_1623002_Capacity | Central Valley | Stockton | MONARCH BANK 2 | 1623002 | Bank | None | None | None | 97.66% | 0 | 0% | 6.84 | 6.68 | 97.66% | 0 | 0% | 6.84 | 6.65 | 97.22% | 0 | 0% | 6.84 | 6.63 | 96.93% | 0 | 0% | 6.84 | 6.59 | 96.35% | 0 | 0% | 6.84 | 6.59 | 96.35% | 0 | 0%
GNA_162300401_Capacity | Central Valley | Stockton | MONARCH 0401 | 162300401 | Feeder | None | None | None | 88.46% | 0 | 0% | 2.34 | 2.07 | 88.46% | 0 | 0% | 2.34 | 2.07 | 88.46% | 0 | 0% | 2.34 | 2.07 | 88.46% | 0 | 0% | 2.34 | 2.06 | 88.03% | 0 | 0% | 2.34 | 2.05 | 87.61% | 0 | 0%
GNA_162300402_Capacity | Central Valley | Stockton | MONARCH 0402 | 162300402 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162300403_Capacity | Central Valley | Stockton | MONARCH 0403 | 162300403 | Feeder | None | None | None | 79.65% | 0 | 0% | 2.85 | 2.27 | 79.65% | 0 | 0% | 2.85 | 2.26 | 79.3% | 0 | 0% | 2.85 | 2.26 | 79.3% | 0 | 0% | 2.85 | 2.26 | 79.3% | 0 | 0% | 2.85 | 2.27 | 79.65% | 0 | 0%
GNA_1623701_Capacity | Central Valley | Stockton | STOCKTON A BANK 1 | 1623701 | Bank | None | None | None | 26.52% | 0 | 0% | 10.52 | 2.79 | 26.52% | 0 | 0% | 10.52 | 2.76 | 26.24% | 0 | 0% | 10.52 | 2.75 | 26.14% | 0 | 0% | 10.52 | 2.73 | 25.95% | 0 | 0% | 10.52 | 2.71 | 25.76% | 0 | 0%
GNA_162370404_Capacity | Central Valley | Stockton | STOCKTON A 0404 | 162370404 | Feeder | None | None | None | 80.7% | 0 | 0% | 2.85 | 2.3 | 80.7% | 0 | 0% | 2.85 | 2.29 | 80.35% | 0 | 0% | 2.85 | 2.29 | 80.35% | 0 | 0% | 2.85 | 2.29 | 80.35% | 0 | 0% | 2.85 | 2.27 | 79.65% | 0 | 0%
GNA_162370405_Capacity | Central Valley | Stockton | STOCKTON A 0405 | 162370405 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1623702_Capacity | Central Valley | Stockton | STOCKTON A BANK 2 | 1623702 | Bank | None | None | None | 26.14% | 0 | 0% | 10.52 | 2.75 | 26.14% | 0 | 0% | 10.52 | 2.72 | 25.86% | 0 | 0% | 10.52 | 2.71 | 25.76% | 0 | 0% | 10.52 | 2.71 | 25.76% | 0 | 0% | 10.52 | 2.69 | 25.57% | 0 | 0%
GNA_162370406_Capacity | Central Valley | Stockton | STOCKTON A 0406 | 162370406 | Feeder | None | None | None | 69.96% | 0 | 0% | 2.33 | 1.63 | 69.96% | 0 | 0% | 2.33 | 1.62 | 69.53% | 0 | 0% | 2.33 | 1.61 | 69.1% | 0 | 0% | 2.33 | 1.61 | 69.1% | 0 | 0% | 2.33 | 1.59 | 68.24% | 0 | 0%
GNA_162370410_Capacity | Central Valley | Stockton | STOCKTON A 0410 | 162370410 | Feeder | None | None | None | 57.82% | 0 | 0% | 2.94 | 1.7 | 57.82% | 0 | 0% | 2.94 | 1.69 | 57.48% | 0 | 0% | 2.94 | 1.67 | 56.8% | 0 | 0% | 2.94 | 1.68 | 57.14% | 0 | 0% | 2.94 | 1.68 | 57.14% | 0 | 0%
GNA_1624701_Capacity | Central Valley | Stockton | BANTA BANK 1 | 1624701 | Bank | Demand Growth | Capacity | 2023 | 100.9% | 0.08 | 0.907% | 8.82 | 8.9 | 100.9% | 0.08 | 0.907% | 8.82 | 8.87 | 100.6% | 0.05 | 0.5669% | 8.82 | 8.84 | 100.2% | 0.02 | 0.2268% | 8.82 | 8.83 | 100.1% | 0.01 | 0.1134% | 8.82 | 8.82 | 100% | 0 | 0%
GNA_162471101_Capacity | Central Valley | Stockton | BANTA 1101 | 162471101 | Feeder | None | None | None | 17.25% | 0 | 0% | 8.81 | 1.52 | 17.25% | 0 | 0% | 8.81 | 1.52 | 17.25% | 0 | 0% | 8.81 | 1.51 | 17.14% | 0 | 0% | 8.81 | 1.52 | 17.25% | 0 | 0% | 8.81 | 1.52 | 17.25% | 0 | 0%
GNA_162471102_Capacity | Central Valley | Stockton | BANTA 1102 | 162471102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162471103_Capacity | Central Valley | Stockton | BANTA 1103 | 162471103 | Feeder | None | None | None | 86.43% | 0 | 0% | 6.41 | 5.54 | 86.43% | 0 | 0% | 6.41 | 5.53 | 86.27% | 0 | 0% | 6.41 | 5.51 | 85.96% | 0 | 0% | 6.41 | 5.5 | 85.8% | 0 | 0% | 6.41 | 5.49 | 85.65% | 0 | 0%
GNA_1630901_Capacity | Central Valley | Stockton | CARBONA BANK 1 | 1630901 | Bank | Demand Growth | Capacity | 2023 | 270.5% | 25.34 | 170.5% | 29.7 | 48.68 | 163.9% | 18.98 | 63.91% | 14.86 | 38.2 | 257.1% | 23.34 | 157.1% | 14.86 | 38.82 | 261.2% | 23.96 | 161.2% | 14.86 | 39.87 | 268.3% | 25.01 | 168.3% | 14.86 | 40.2 | 270.5% | 25.34 | 170.5%
GNA_163091101_Capacity | Central Valley | Stockton | CARBONA 1101 | 163091101 | Feeder | Demand Growth | Capacity | 2024 | 113.6% | 1.74 | 13.56% | 12.83 | 9.49 | 73.97% | 0 | 0% | 12.83 | 12.95 | 100.9% | 0.12 | 0.9353% | 12.83 | 13.55 | 105.6% | 0.72 | 5.612% | 12.83 | 14.46 | 112.7% | 1.63 | 12.7% | 12.83 | 14.57 | 113.6% | 1.74 | 13.56%
GNA_163091103_Capacity | Central Valley | Stockton | CARBONA 1103 | 163091103 | Feeder | Demand Growth | Capacity | 2024 | 140.2% | 4.99 | 40.18% | 12.42 | 10.27 | 82.69% | 0 | 0% | 12.42 | 17.03 | 137.1% | 4.61 | 37.12% | 12.42 | 17.1 | 137.7% | 4.68 | 37.68% | 12.42 | 17.25 | 138.9% | 4.83 | 38.89% | 12.42 | 17.41 | 140.2% | 4.99 | 40.18%
GNA_163091104_Capacity | Central Valley | Stockton | CARBONA 1104 | 163091104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1630902_Capacity | Central Valley | Stockton | CARBONA BANK 2 | 1630902 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163091102_Capacity | Central Valley | Stockton | CARBONA 1102 | 163091102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1637401_Capacity | Central Valley | Stockton | HERDLYN BANK 1 | 1637401 | Bank | None | None | None | 83.15% | 0 | 0% | 12.4 | 9.95 | 80.24% | 0 | 0% | 12.4 | 10.03 | 80.89% | 0 | 0% | 12.4 | 10.11 | 81.53% | 0 | 0% | 12.4 | 10.2 | 82.26% | 0 | 0% | 12.4 | 10.31 | 83.15% | 0 | 0%
GNA_163741102_Capacity | Central Valley | Stockton | HERDLYN 1102 | 163741102 | Feeder | None | None | None | 93.19% | 0 | 0% | 12.19 | 10.95 | 89.83% | 0 | 0% | 12.19 | 11.04 | 90.57% | 0 | 0% | 12.19 | 11.14 | 91.39% | 0 | 0% | 12.19 | 11.25 | 92.29% | 0 | 0% | 12.19 | 11.36 | 93.19% | 0 | 0%
GNA_163741103_Capacity | Central Valley | Stockton | HERDLYN 1103 | 163741103 | Feeder | Demand Growth | Capacity | 2023 | 130.9% | 1.15 | 30.91% | 3.72 | 4.87 | 130.9% | 1.15 | 30.91% | 3.72 | 4.86 | 130.6% | 1.14 | 30.65% | 3.72 | 4.84 | 130.1% | 1.12 | 30.11% | 3.72 | 4.81 | 129.3% | 1.09 | 29.3% | 3.72 | 4.8 | 129% | 1.08 | 29.03%
GNA_1627701_Capacity | Central Valley | Stockton | LAMMERS BANK 1 | 1627701 | Bank | None | None | None | 89.26% | 0 | 0% | 44.6 | 37.73 | 84.6% | 0 | 0% | 44.6 | 38.85 | 87.11% | 0 | 0% | 44.6 | 39.07 | 87.6% | 0 | 0% | 44.6 | 39.43 | 88.41% | 0 | 0% | 44.6 | 39.81 | 89.26% | 0 | 0%
GNA_162771101_Capacity | Central Valley | Stockton | LAMMERS 1101 | 162771101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162771102_Capacity | Central Valley | Stockton | LAMMERS 1102 | 162771102 | Feeder | None | None | None | 100.1% | 0.01 | 0.08091% | 12.36 | 12.32 | 99.68% | 0 | 0% | 12.36 | 11.85 | 95.87% | 0 | 0% | 12.36 | 11.96 | 96.76% | 0 | 0% | 12.36 | 12.16 | 98.38% | 0 | 0% | 12.36 | 12.37 | 100.1% | 0.01 | 0.08091%
GNA_162771103_Capacity | Central Valley | Stockton | LAMMERS 1103 | 162771103 | Feeder | Demand Growth | Capacity | 2023 | 125.6% | 3.16 | 25.57% | 12.36 | 15.43 | 124.8% | 3.07 | 24.84% | 12.36 | 15.42 | 124.8% | 3.06 | 24.76% | 12.36 | 15.42 | 124.8% | 3.06 | 24.76% | 12.36 | 15.47 | 125.2% | 3.11 | 25.16% | 12.36 | 15.52 | 125.6% | 3.16 | 25.57%
GNA_1627702_Capacity | Central Valley | Stockton | LAMMERS BANK 2 | 1627702 | Bank | None | None | None | 99.48% | 0 | 0% | 44.6 | 39.5 | 88.57% | 0 | 0% | 44.6 | 39.74 | 89.1% | 0 | 0% | 44.6 | 43.44 | 97.4% | 0 | 0% | 44.6 | 43.85 | 98.32% | 0 | 0% | 44.6 | 44.37 | 99.48% | 0 | 0%
GNA_162771105_Capacity | Central Valley | Stockton | LAMMERS 1105 | 162771105 | Feeder | None | None | None | 97.25% | 0 | 0% | 12.36 | 11.44 | 92.56% | 0 | 0% | 12.36 | 11.52 | 93.2% | 0 | 0% | 12.36 | 11.63 | 94.09% | 0 | 0% | 12.36 | 11.8 | 95.47% | 0 | 0% | 12.36 | 12.02 | 97.25% | 0 | 0%
GNA_162771106_Capacity | Central Valley | Stockton | LAMMERS 1106 | 162771106 | Feeder | None | None | None | 96.44% | 0 | 0% | 12.36 | 11.85 | 95.87% | 0 | 0% | 12.36 | 11.92 | 96.44% | 0 | 0% | 12.36 | 8.38 | 67.8% | 0 | 0% | 12.36 | 8.5 | 68.77% | 0 | 0% | 12.36 | 8.66 | 70.06% | 0 | 0%
GNA_162771107_Capacity | Central Valley | Stockton | LAMMERS 1107 | 162771107 | Feeder | Demand Growth | Capacity | 2025 | 152.8% | 6.53 | 52.83% | 12.36 | 11.7 | 94.66% | 0 | 0% | 12.36 | 11.74 | 94.98% | 0 | 0% | 12.36 | 18.71 | 151.4% | 6.35 | 51.38% | 12.36 | 18.8 | 152.1% | 6.44 | 52.1% | 12.36 | 18.89 | 152.8% | 6.53 | 52.83%
GNA_162771108_Capacity | Central Valley | Stockton | LAMMERS 1108 | 162771108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1628801_Capacity | Central Valley | Stockton | TRACY BANK 1 | 1628801 | Bank | Demand Growth | Capacity | 2023 | 118.5% | 5.5 | 18.52% | 29.7 | 32.17 | 108.3% | 2.47 | 8.316% | 29.7 | 34.86 | 117.4% | 5.16 | 17.37% | 29.7 | 35.09 | 118.1% | 5.39 | 18.15% | 29.7 | 35.12 | 118.2% | 5.42 | 18.25% | 29.7 | 35.2 | 118.5% | 5.5 | 18.52%
GNA_162881102_Capacity | Central Valley | Stockton | TRACY 1102 | 162881102 | Feeder | Demand Growth | Capacity | 2023 | 156.2% | 6.88 | 56.16% | 12.25 | 15.73 | 128.4% | 3.48 | 28.41% | 12.25 | 18.53 | 151.3% | 6.28 | 51.27% | 12.25 | 19 | 155.1% | 6.75 | 55.1% | 12.25 | 19.05 | 155.5% | 6.8 | 55.51% | 12.25 | 19.13 | 156.2% | 6.88 | 56.16%
GNA_162881103_Capacity | Central Valley | Stockton | TRACY 1103 | 162881103 | Feeder | Demand Growth | Capacity | 2023 | 109.9% | 1.21 | 9.926% | 12.19 | 13.4 | 109.9% | 1.21 | 9.926% | 12.19 | 13.37 | 109.7% | 1.18 | 9.68% | 12.19 | 13.3 | 109.1% | 1.11 | 9.106% | 12.19 | 13.28 | 108.9% | 1.09 | 8.942% | 12.19 | 13.32 | 109.3% | 1.13 | 9.27%
GNA_162881104_Capacity | Central Valley | Stockton | TRACY 1104 | 162881104 | Feeder | None | None | None | 56.71% | 0 | 0% | 10.95 | 6.21 | 56.71% | 0 | 0% | 10.95 | 6.2 | 56.62% | 0 | 0% | 10.95 | 6.19 | 56.53% | 0 | 0% | 10.95 | 6.19 | 56.53% | 0 | 0% | 10.95 | 6.17 | 56.35% | 0 | 0%
GNA_1628802_Capacity | Central Valley | Stockton | TRACY BANK 2 | 1628802 | Bank | None | None | None | 86.4% | 0 | 0% | 44.55 | 37.5 | 84.18% | 0 | 0% | 44.55 | 37.49 | 84.15% | 0 | 0% | 44.55 | 37.5 | 84.18% | 0 | 0% | 44.55 | 38.36 | 86.11% | 0 | 0% | 44.55 | 38.49 | 86.4% | 0 | 0%
GNA_162881105_Capacity | Central Valley | Stockton | TRACY 1105 | 162881105 | Feeder | None | None | None | 94.7% | 0 | 0% | 10.95 | 10.36 | 94.61% | 0 | 0% | 10.95 | 10.31 | 94.16% | 0 | 0% | 10.95 | 10.3 | 94.06% | 0 | 0% | 10.95 | 10.33 | 94.34% | 0 | 0% | 10.95 | 10.37 | 94.7% | 0 | 0%
GNA_162881106_Capacity | Central Valley | Stockton | TRACY 1106 | 162881106 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162881107_Capacity | Central Valley | Stockton | TRACY 1107 | 162881107 | Feeder | Demand Growth | Capacity | 2026 | 101.9% | 0.23 | 1.887% | 12.19 | 11.22 | 92.04% | 0 | 0% | 12.19 | 11.31 | 92.78% | 0 | 0% | 12.19 | 11.39 | 93.44% | 0 | 0% | 12.19 | 12.3 | 100.9% | 0.11 | 0.9024% | 12.19 | 12.42 | 101.9% | 0.23 | 1.887%
GNA_1628803_Capacity | Central Valley | Stockton | TRACY BANK 3 | 1628803 | Bank | None | None | None | 99.53% | 0 | 0% | 29.69 | 29.55 | 99.53% | 0 | 0% | 29.69 | 26.94 | 90.74% | 0 | 0% | 29.69 | 25.19 | 84.84% | 0 | 0% | 29.69 | 25.44 | 85.69% | 0 | 0% | 29.69 | 25.74 | 86.7% | 0 | 0%
GNA_162881109_Capacity | Central Valley | Stockton | TRACY 1109 | 162881109 | Feeder | None | None | None | 82.94% | 0 | 0% | 12.19 | 10.11 | 82.94% | 0 | 0% | 12.19 | 7.44 | 61.03% | 0 | 0% | 12.19 | 7.53 | 61.77% | 0 | 0% | 12.19 | 7.69 | 63.08% | 0 | 0% | 12.19 | 7.85 | 64.4% | 0 | 0%
GNA_162881110_Capacity | Central Valley | Stockton | TRACY 1110 | 162881110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162881111_Capacity | Central Valley | Stockton | TRACY 1111 | 162881111 | Feeder | None | None | None | 75.14% | 0 | 0% | 12.19 | 9.16 | 75.14% | 0 | 0% | 12.19 | 9.11 | 74.73% | 0 | 0% | 12.19 | 7.13 | 58.49% | 0 | 0% | 12.19 | 7.14 | 58.57% | 0 | 0% | 12.19 | 7.18 | 58.9% | 0 | 0%
GNA_1628804_Capacity | Central Valley | Stockton | TRACY BANK 4 | 1628804 | Bank | None | None | None | 68.37% | 0 | 0% | 15.84 | 10.4 | 65.66% | 0 | 0% | 15.84 | 10.47 | 66.1% | 0 | 0% | 15.84 | 10.56 | 66.67% | 0 | 0% | 15.84 | 10.67 | 67.36% | 0 | 0% | 15.84 | 10.83 | 68.37% | 0 | 0%
GNA_162881112_Capacity | Central Valley | Stockton | TRACY 1112 | 162881112 | Feeder | None | None | None | 85.45% | 0 | 0% | 15.12 | 12.49 | 82.61% | 0 | 0% | 15.12 | 12.56 | 83.07% | 0 | 0% | 15.12 | 12.65 | 83.66% | 0 | 0% | 15.12 | 12.76 | 84.39% | 0 | 0% | 15.12 | 12.92 | 85.45% | 0 | 0%
GNA_2536101_Capacity | Central Valley | Yosemite | ATWATER BANK 1 | 2536101 | Bank | None | None | None | 95.45% | 0 | 0% | 44.6 | 40.99 | 91.91% | 0 | 0% | 44.6 | 41.22 | 92.42% | 0 | 0% | 44.6 | 41.38 | 92.78% | 0 | 0% | 44.6 | 41.91 | 93.97% | 0 | 0% | 44.6 | 42.57 | 95.45% | 0 | 0%
GNA_253611105_Capacity | Central Valley | Yosemite | ATWATER 1105 | 253611105 | Feeder | None | None | None | 84.57% | 0 | 0% | 12.25 | 10.32 | 84.24% | 0 | 0% | 12.25 | 10.35 | 84.49% | 0 | 0% | 12.25 | 10.36 | 84.57% | 0 | 0% | 12.25 | 10.36 | 84.57% | 0 | 0% | 12.25 | 10.34 | 84.41% | 0 | 0%
GNA_253611106_Capacity | Central Valley | Yosemite | ATWATER 1106 | 253611106 | Feeder | None | None | None | 93.47% | 0 | 0% | 14.86 | 13.89 | 93.47% | 0 | 0% | 14.86 | 13.83 | 93.07% | 0 | 0% | 14.86 | 13.75 | 92.53% | 0 | 0% | 14.86 | 13.79 | 92.8% | 0 | 0% | 14.86 | 13.86 | 93.27% | 0 | 0%
GNA_253611107_Capacity | Central Valley | Yosemite | ATWATER 1107 | 253611107 | Feeder | None | None | None | 81.54% | 0 | 0% | 13.6 | 10.47 | 76.99% | 0 | 0% | 13.6 | 10.58 | 77.79% | 0 | 0% | 13.6 | 10.71 | 78.75% | 0 | 0% | 13.6 | 10.88 | 80% | 0 | 0% | 13.6 | 11.09 | 81.54% | 0 | 0%
GNA_253611108_Capacity | Central Valley | Yosemite | ATWATER 1108 | 253611108 | Feeder | None | None | None | 54.71% | 0 | 0% | 14.97 | 7.81 | 52.17% | 0 | 0% | 14.97 | 7.89 | 52.71% | 0 | 0% | 14.97 | 7.95 | 53.11% | 0 | 0% | 14.97 | 8.06 | 53.84% | 0 | 0% | 14.97 | 8.19 | 54.71% | 0 | 0%
GNA_2536102_Capacity | Central Valley | Yosemite | ATWATER BANK 2 | 2536102 | Bank | None | None | None | 97.95% | 0 | 0% | 28.74 | 26.88 | 93.53% | 0 | 0% | 28.74 | 27.13 | 94.4% | 0 | 0% | 28.74 | 27.38 | 95.27% | 0 | 0% | 28.74 | 27.76 | 96.59% | 0 | 0% | 28.74 | 28.15 | 97.95% | 0 | 0%
GNA_253611102_Capacity | Central Valley | Yosemite | ATWATER 1102 | 253611102 | Feeder | None | None | None | 94.68% | 0 | 0% | 14.86 | 13.71 | 92.26% | 0 | 0% | 14.86 | 13.79 | 92.8% | 0 | 0% | 14.86 | 13.88 | 93.41% | 0 | 0% | 14.86 | 13.98 | 94.08% | 0 | 0% | 14.86 | 14.07 | 94.68% | 0 | 0%
GNA_253611103_Capacity | Central Valley | Yosemite | ATWATER 1103 | 253611103 | Feeder | None | None | None | 87.38% | 0 | 0% | 10.46 | 9.08 | 86.81% | 0 | 0% | 10.46 | 9.14 | 87.38% | 0 | 0% | 10.46 | 7.28 | 69.6% | 0 | 0% | 10.46 | 7.39 | 70.65% | 0 | 0% | 10.46 | 7.51 | 71.8% | 0 | 0%
GNA_253611104_Capacity | Central Valley | Yosemite | ATWATER 1104 | 253611104 | Feeder | None | None | None | 83.57% | 0 | 0% | 14.97 | 10.09 | 67.4% | 0 | 0% | 14.97 | 10.16 | 67.87% | 0 | 0% | 14.97 | 12.17 | 81.3% | 0 | 0% | 14.97 | 12.33 | 82.36% | 0 | 0% | 14.97 | 12.51 | 83.57% | 0 | 0%
GNA_2547001_Capacity | Central Valley | Yosemite | CRESSEY BANK 1 | 2547001 | Bank | None | None | None | 87.29% | 0 | 0% | 29.67 | 25.9 | 87.29% | 0 | 0% | 29.67 | 25.86 | 87.16% | 0 | 0% | 29.67 | 25.84 | 87.09% | 0 | 0% | 29.67 | 25.81 | 86.99% | 0 | 0% | 29.67 | 25.8 | 86.96% | 0 | 0%
GNA_254702103_Capacity | Central Valley | Yosemite | CRESSEY 2103 | 254702103 | Feeder | None | None | None | 88.8% | 0 | 0% | 19.74 | 17.53 | 88.8% | 0 | 0% | 19.74 | 17.52 | 88.75% | 0 | 0% | 19.74 | 17.51 | 88.7% | 0 | 0% | 19.74 | 17.48 | 88.55% | 0 | 0% | 19.74 | 17.47 | 88.5% | 0 | 0%
GNA_254702104_Capacity | Central Valley | Yosemite | CRESSEY 2104 | 254702104 | Feeder | None | None | None | 72.28% | 0 | 0% | 22.22 | 16.06 | 72.28% | 0 | 0% | 22.22 | 16.04 | 72.19% | 0 | 0% | 22.22 | 16.02 | 72.1% | 0 | 0% | 22.22 | 16.03 | 72.14% | 0 | 0% | 22.22 | 16.05 | 72.23% | 0 | 0%
GNA_2522601_Capacity | Central Valley | Yosemite | LIVINGSTON BANK 1 | 2522601 | Bank | None | None | None | 73.43% | 0 | 0% | 44.53 | 31.91 | 71.66% | 0 | 0% | 44.53 | 32.01 | 71.88% | 0 | 0% | 44.53 | 32.12 | 72.13% | 0 | 0% | 44.53 | 32.36 | 72.67% | 0 | 0% | 44.53 | 32.7 | 73.43% | 0 | 0%
GNA_252261101_Capacity | Central Valley | Yosemite | LIVINGSTON 1101 | 252261101 | Feeder | None | None | None | 72.84% | 0 | 0% | 11.67 | 8.5 | 72.84% | 0 | 0% | 11.67 | 8.48 | 72.66% | 0 | 0% | 11.67 | 8.47 | 72.58% | 0 | 0% | 11.67 | 8.46 | 72.49% | 0 | 0% | 11.67 | 8.46 | 72.49% | 0 | 0%
GNA_252261102_Capacity | Central Valley | Yosemite | LIVINGSTON 1102 | 252261102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252261104_Capacity | Central Valley | Yosemite | LIVINGSTON 1104 | 252261104 | Feeder | None | None | None | 71.89% | 0 | 0% | 11.67 | 8.01 | 68.64% | 0 | 0% | 11.67 | 8.08 | 69.24% | 0 | 0% | 11.67 | 8.16 | 69.92% | 0 | 0% | 11.67 | 8.26 | 70.78% | 0 | 0% | 11.67 | 8.39 | 71.89% | 0 | 0%
GNA_252261105_Capacity | Central Valley | Yosemite | LIVINGSTON 1105 | 252261105 | Feeder | None | None | None | 60.09% | 0 | 0% | 12.83 | 7.71 | 60.09% | 0 | 0% | 12.83 | 7.7 | 60.02% | 0 | 0% | 12.83 | 7.67 | 59.78% | 0 | 0% | 12.83 | 7.68 | 59.86% | 0 | 0% | 12.83 | 7.71 | 60.09% | 0 | 0%
GNA_252261106_Capacity | Central Valley | Yosemite | LIVINGSTON 1106 | 252261106 | Feeder | None | None | None | 87.86% | 0 | 0% | 12.19 | 10.35 | 84.91% | 0 | 0% | 12.19 | 10.38 | 85.15% | 0 | 0% | 12.19 | 10.4 | 85.32% | 0 | 0% | 12.19 | 10.54 | 86.46% | 0 | 0% | 12.19 | 10.71 | 87.86% | 0 | 0%
GNA_2520901_Capacity | Central Valley | Yosemite | CANAL BANK 1 | 2520901 | Bank | Demand Growth | Capacity | 2023 | 130.9% | 9.18 | 30.91% | 29.7 | 36.43 | 122.7% | 6.73 | 22.66% | 29.7 | 37.65 | 126.8% | 7.95 | 26.77% | 29.7 | 38.46 | 129.5% | 8.76 | 29.49% | 29.7 | 38.65 | 130.1% | 8.95 | 30.13% | 29.7 | 38.88 | 130.9% | 9.18 | 30.91%
GNA_252091101_Capacity | Central Valley | Yosemite | CANAL 1101 | 252091101 | Feeder | Demand Growth | Capacity | 2023 | 117.1% | 2.08 | 17.06% | 12.19 | 12.3 | 100.9% | 0.11 | 0.9024% | 12.19 | 13.42 | 110.1% | 1.23 | 10.09% | 12.19 | 14.13 | 115.9% | 1.94 | 15.91% | 12.19 | 14.17 | 116.2% | 1.98 | 16.24% | 12.19 | 14.27 | 117.1% | 2.08 | 17.06%
GNA_252091104_Capacity | Central Valley | Yosemite | CANAL 1104 | 252091104 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252091106_Capacity | Central Valley | Yosemite | CANAL 1106 | 252091106 | Feeder | Demand Growth | Capacity | 2023 | 120.5% | 2.14 | 20.46% | 10.46 | 12.41 | 118.6% | 1.95 | 18.64% | 10.46 | 12.42 | 118.7% | 1.96 | 18.74% | 10.46 | 12.47 | 119.2% | 2.01 | 19.22% | 10.46 | 12.54 | 119.9% | 2.08 | 19.89% | 10.46 | 12.6 | 120.5% | 2.14 | 20.46%
GNA_2520902_Capacity | Central Valley | Yosemite | CANAL BANK 2 | 2520902 | Bank | Demand Growth | Capacity | 2023 | 115.9% | 4.73 | 15.93% | 29.69 | 33.79 | 113.8% | 4.1 | 13.81% | 29.69 | 33.92 | 114.2% | 4.23 | 14.25% | 29.69 | 34.07 | 114.8% | 4.38 | 14.75% | 29.69 | 34.21 | 115.2% | 4.52 | 15.22% | 29.69 | 34.42 | 115.9% | 4.73 | 15.93%
GNA_252091102_Capacity | Central Valley | Yosemite | CANAL 1102 | 252091102 | Feeder | None | None | None | 100.4% | 0.05 | 0.3676% | 13.6 | 13.4 | 98.53% | 0 | 0% | 13.6 | 13.45 | 98.9% | 0 | 0% | 13.6 | 13.51 | 99.34% | 0 | 0% | 13.6 | 13.57 | 99.78% | 0 | 0% | 13.6 | 13.65 | 100.4% | 0.05 | 0.3676%
GNA_252091103_Capacity | Central Valley | Yosemite | CANAL 1103 | 252091103 | Feeder | None | None | None | 99.26% | 0 | 0% | 12.19 | 11.95 | 98.03% | 0 | 0% | 12.19 | 11.97 | 98.2% | 0 | 0% | 12.19 | 12.01 | 98.52% | 0 | 0% | 12.19 | 12.03 | 98.69% | 0 | 0% | 12.19 | 12.1 | 99.26% | 0 | 0%
GNA_252091105_Capacity | Central Valley | Yosemite | CANAL 1105 | 252091105 | Feeder | None | None | None | 80.72% | 0 | 0% | 12.19 | 9.6 | 78.75% | 0 | 0% | 12.19 | 9.67 | 79.33% | 0 | 0% | 12.19 | 9.72 | 79.74% | 0 | 0% | 12.19 | 9.77 | 80.15% | 0 | 0% | 12.19 | 9.84 | 80.72% | 0 | 0%
GNA_2543101_Capacity | Central Valley | Yosemite | ORTIGA BANK 1 | 2543101 | Bank | Demand Growth | Capacity | 2023 | 140.3% | 6.39 | 40.34% | 15.84 | 21.14 | 133.5% | 5.3 | 33.46% | 15.84 | 21.52 | 135.9% | 5.68 | 35.86% | 15.84 | 21.74 | 137.2% | 5.9 | 37.25% | 15.84 | 21.97 | 138.7% | 6.13 | 38.7% | 15.84 | 22.23 | 140.3% | 6.39 | 40.34%
GNA_254311105_Capacity | Central Valley | Yosemite | ORTIGA 1105 | 254311105 | Feeder | Demand Growth | Capacity | 2023 | 113.1% | 1.41 | 13.08% | 10.78 | 11.43 | 106% | 0.65 | 6.03% | 10.78 | 11.75 | 109% | 0.97 | 8.998% | 10.78 | 11.9 | 110.4% | 1.12 | 10.39% | 10.78 | 12.03 | 111.6% | 1.25 | 11.6% | 10.78 | 12.19 | 113.1% | 1.41 | 13.08%
GNA_254311106_Capacity | Central Valley | Yosemite | ORTIGA 1106 | 254311106 | Feeder | Demand Growth | Capacity | 2023 | 120.5% | 2.14 | 20.46% | 10.46 | 12.17 | 116.3% | 1.71 | 16.35% | 10.46 | 12.26 | 117.2% | 1.8 | 17.21% | 10.46 | 12.35 | 118.1% | 1.89 | 18.07% | 10.46 | 12.48 | 119.3% | 2.02 | 19.31% | 10.46 | 12.6 | 120.5% | 2.14 | 20.46%
GNA_2540501_Capacity | Central Valley | Yosemite | SANTA NELLA BANK 1 | 2540501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254051101_Capacity | Central Valley | Yosemite | SANTA NELLA 1101 | 254051101 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2540502_Capacity | Central Valley | Yosemite | SANTA NELLA BANK 2 | 2540502 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254051104_Capacity | Central Valley | Yosemite | SANTA NELLA 1104 | 254051104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2546403_Capacity | Central Valley | Yosemite | WRIGHT BANK 3 | 2546403 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254641110_Capacity | Central Valley | Yosemite | WRIGHT 1110 | 254641110 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2541001_Capacity | Central Valley | Yosemite | CHOWCHILLA BANK 1 | 2541001 | Bank | Demand Growth | Capacity | 2026 | 101.5% | 0.68 | 1.526% | 44.55 | 44.24 | 99.3% | 0 | 0% | 44.55 | 44.38 | 99.62% | 0 | 0% | 44.55 | 44.58 | 100.1% | 0.03 | 0.06734% | 44.55 | 44.87 | 100.7% | 0.32 | 0.7183% | 44.55 | 45.23 | 101.5% | 0.68 | 1.526%
GNA_254101101_Capacity | Central Valley | Yosemite | CHOWCHILLA 1101 | 254101101 | Feeder | None | None | None | 99.47% | 0 | 0% | 13.19 | 12.53 | 95% | 0 | 0% | 13.19 | 12.88 | 97.65% | 0 | 0% | 13.19 | 12.92 | 97.95% | 0 | 0% | 13.19 | 13.02 | 98.71% | 0 | 0% | 13.19 | 13.12 | 99.47% | 0 | 0%
GNA_254101102_Capacity | Central Valley | Yosemite | CHOWCHILLA 1102 | 254101102 | Feeder | None | None | None | 85.27% | 0 | 0% | 12.83 | 10.46 | 81.53% | 0 | 0% | 12.83 | 10.53 | 82.07% | 0 | 0% | 12.83 | 10.63 | 82.85% | 0 | 0% | 12.83 | 10.75 | 83.79% | 0 | 0% | 12.83 | 10.94 | 85.27% | 0 | 0%
GNA_254101103_Capacity | Central Valley | Yosemite | CHOWCHILLA 1103 | 254101103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254101104_Capacity | Central Valley | Yosemite | CHOWCHILLA 1104 | 254101104 | Feeder | Demand Growth | Capacity | 2024 | 109.3% | 1.19 | 9.275% | 12.83 | 12.64 | 98.52% | 0 | 0% | 12.83 | 14 | 109.1% | 1.17 | 9.119% | 12.83 | 13.98 | 109% | 1.15 | 8.963% | 12.83 | 14 | 109.1% | 1.17 | 9.119% | 12.83 | 14.02 | 109.3% | 1.19 | 9.275%
GNA_2541002_Capacity | Central Valley | Yosemite | CHOWCHILLA BANK 2 | 2541002 | Bank | None | None | None | 90.21% | 0 | 0% | 15.84 | 14.11 | 89.08% | 0 | 0% | 15.84 | 14.17 | 89.46% | 0 | 0% | 15.84 | 14.25 | 89.96% | 0 | 0% | 15.84 | 14.29 | 90.21% | 0 | 0% | 15.84 | 14.29 | 90.21% | 0 | 0%
GNA_254101105_Capacity | Central Valley | Yosemite | CHOWCHILLA 1105 | 254101105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254101106_Capacity | Central Valley | Yosemite | CHOWCHILLA 1106 | 254101106 | Feeder | None | None | None | 81.38% | 0 | 0% | 12.19 | 9.57 | 78.51% | 0 | 0% | 12.19 | 9.66 | 79.25% | 0 | 0% | 12.19 | 9.73 | 79.82% | 0 | 0% | 12.19 | 9.82 | 80.56% | 0 | 0% | 12.19 | 9.92 | 81.38% | 0 | 0%
GNA_2524201_Capacity | Central Valley | Yosemite | DAIRYLAND BANK 1 | 2524201 | Bank | None | None | None | 95.29% | 0 | 0% | 29.7 | 28.3 | 95.29% | 0 | 0% | 29.7 | 28.25 | 95.12% | 0 | 0% | 29.7 | 28.21 | 94.98% | 0 | 0% | 29.7 | 28.19 | 94.92% | 0 | 0% | 29.7 | 28.17 | 94.85% | 0 | 0%
GNA_252421102_Capacity | Central Valley | Yosemite | DAIRYLAND 1102 | 252421102 | Feeder | None | None | None | 88.1% | 0 | 0% | 13.19 | 11.62 | 88.1% | 0 | 0% | 13.19 | 11.62 | 88.1% | 0 | 0% | 13.19 | 11.62 | 88.1% | 0 | 0% | 13.19 | 11.62 | 88.1% | 0 | 0% | 13.19 | 11.62 | 88.1% | 0 | 0%
GNA_252421105_Capacity | Central Valley | Yosemite | DAIRYLAND 1105 | 252421105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252421109_Capacity | Central Valley | Yosemite | DAIRYLAND 1109 | 252421109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2524202_Capacity | Central Valley | Yosemite | DAIRYLAND BANK 2 | 2524202 | Bank | Demand Growth | Capacity | 2023 | 103.9% | 1.16 | 3.906% | 29.7 | 30.76 | 103.6% | 1.06 | 3.569% | 29.7 | 30.86 | 103.9% | 1.16 | 3.906% | 29.7 | 30.78 | 103.6% | 1.08 | 3.636% | 29.7 | 30.72 | 103.4% | 1.02 | 3.434% | 29.7 | 30.65 | 103.2% | 0.95 | 3.199%
GNA_252421110_Capacity | Central Valley | Yosemite | DAIRYLAND NEW 1110 | 252421110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252421111_Capacity | Central Valley | Yosemite | DAIRYLAND 1111 | 252421111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252421112_Capacity | Central Valley | Yosemite | DAIRYLAND 1112 | 252421112 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252421113_Capacity | Central Valley | Yosemite | DAIRYLAND 1113 | 252421113 | Feeder | Demand Growth | Capacity | 2023 | 102.3% | 0.3 | 2.262% | 13.26 | 13.56 | 102.3% | 0.3 | 2.262% | 13.26 | 13.56 | 102.3% | 0.3 | 2.262% | 13.26 | 13.56 | 102.3% | 0.3 | 2.262% | 13.26 | 13.56 | 102.3% | 0.3 | 2.262% | 13.26 | 13.56 | 102.3% | 0.3 | 2.262%
GNA_2524501_Capacity | Central Valley | Yosemite | EL NIDO BANK 1 | 2524501 | Bank | None | None | None | 72.52% | 0 | 0% | 29.69 | 21.53 | 72.52% | 0 | 0% | 29.69 | 21.53 | 72.52% | 0 | 0% | 29.69 | 21.53 | 72.52% | 0 | 0% | 29.69 | 21.53 | 72.52% | 0 | 0% | 29.69 | 21.53 | 72.52% | 0 | 0%
GNA_252451102_Capacity | Central Valley | Yosemite | EL NIDO 1102 | 252451102 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252451104_Capacity | Central Valley | Yosemite | EL NIDO 1104 | 252451104 | Feeder | Demand Growth | Capacity | 2023 | 119.2% | 2.01 | 19.22% | 10.46 | 12.47 | 119.2% | 2.01 | 19.22% | 10.46 | 12.47 | 119.2% | 2.01 | 19.22% | 10.46 | 12.47 | 119.2% | 2.01 | 19.22% | 10.46 | 12.47 | 119.2% | 2.01 | 19.22% | 10.46 | 12.47 | 119.2% | 2.01 | 19.22%
GNA_252451106_Capacity | Central Valley | Yosemite | EL NIDO NEW 1106 | 252451106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2524502_Capacity | Central Valley | Yosemite | EL NIDO BANK 2 | 2524502 | Bank | Demand Growth | Capacity | 2023 | 101.1% | 0.18 | 1.136% | 15.84 | 15.97 | 100.8% | 0.13 | 0.8207% | 15.84 | 16.02 | 101.1% | 0.18 | 1.136% | 15.84 | 15.94 | 100.6% | 0.1 | 0.6313% | 15.84 | 15.89 | 100.3% | 0.05 | 0.3157% | 15.84 | 15.86 | 100.1% | 0.02 | 0.1263%
GNA_252451101_Capacity | Central Valley | Yosemite | EL NIDO 1101 | 252451101 | Feeder | None | None | None | 77.55% | 0 | 0% | 10.11 | 7.74 | 76.56% | 0 | 0% | 10.11 | 7.84 | 77.55% | 0 | 0% | 10.11 | 7.83 | 77.45% | 0 | 0% | 10.11 | 7.81 | 77.25% | 0 | 0% | 10.11 | 7.81 | 77.25% | 0 | 0%
GNA_252451103_Capacity | Central Valley | Yosemite | EL NIDO 1103 | 252451103 | Feeder | None | None | None | 89.2% | 0 | 0% | 10.46 | 9.33 | 89.2% | 0 | 0% | 10.46 | 9.31 | 89.01% | 0 | 0% | 10.46 | 9.26 | 88.53% | 0 | 0% | 10.46 | 9.24 | 88.34% | 0 | 0% | 10.46 | 9.23 | 88.24% | 0 | 0%
GNA_2553601_Capacity | Central Valley | Yosemite | LE GRAND BANK 1 | 2553601 | Bank | None | None | None | 69.72% | 0 | 0% | 44.55 | 31.06 | 69.72% | 0 | 0% | 44.55 | 31.01 | 69.61% | 0 | 0% | 44.55 | 30.95 | 69.47% | 0 | 0% | 44.55 | 30.94 | 69.45% | 0 | 0% | 44.55 | 30.92 | 69.41% | 0 | 0%
GNA_255361104_Capacity | Central Valley | Yosemite | LE GRAND 1104 | 255361104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_255361112_Capacity | Central Valley | Yosemite | LE GRAND 1112 (old 1106) | 255361112 | Feeder | None | None | None | 79.61% | 0 | 0% | 10.69 | 8.51 | 79.61% | 0 | 0% | 10.69 | 8.51 | 79.61% | 0 | 0% | 10.69 | 8.51 | 79.61% | 0 | 0% | 10.69 | 8.51 | 79.61% | 0 | 0% | 10.69 | 8.51 | 79.61% | 0 | 0%
GNA_255361110_Capacity | Central Valley | Yosemite | LE GRAND 1110 | 255361110 | Feeder | None | None | None | 97.37% | 0 | 0% | 12.19 | 11.87 | 97.37% | 0 | 0% | 12.19 | 11.87 | 97.37% | 0 | 0% | 12.19 | 11.87 | 97.37% | 0 | 0% | 12.19 | 11.87 | 97.37% | 0 | 0% | 12.19 | 11.87 | 97.37% | 0 | 0%
GNA_255361106_Capacity | Central Valley | Yosemite | LE GRAND 1106 | 255361106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2526901_Capacity | Central Valley | Yosemite | INDIAN FLAT BANK 1 | 2526901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252691104_Capacity | Central Valley | Yosemite | INDIAN FLAT 1104 | 252691104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2521901_Capacity | Central Valley | Yosemite | BEAR VALLEY BANK 1 | 2521901 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252192101_Capacity | Central Valley | Yosemite | BEAR VALLEY 2101 | 252192101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252192105_Capacity | Central Valley | Yosemite | BEAR VALLEY 2105 | 252192105 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2544501_Capacity | Central Valley | Yosemite | MARIPOSA BANK 1 | 2544501 | Bank | None | None | None | 62.09% | 0 | 0% | 15.8 | 9.81 | 62.09% | 0 | 0% | 15.8 | 9.7 | 61.39% | 0 | 0% | 15.8 | 9.56 | 60.51% | 0 | 0% | 15.8 | 9.49 | 60.06% | 0 | 0% | 15.8 | 9.44 | 59.75% | 0 | 0%
GNA_254452101_Capacity | Central Valley | Yosemite | MARIPOSA 2101 | 254452101 | Feeder | None | None | None | 70.72% | 0 | 0% | 14.07 | 9.95 | 70.72% | 0 | 0% | 14.07 | 9.84 | 69.94% | 0 | 0% | 14.07 | 9.7 | 68.94% | 0 | 0% | 14.07 | 9.63 | 68.44% | 0 | 0% | 14.07 | 9.58 | 68.09% | 0 | 0%
GNA_2544502_Capacity | Central Valley | Yosemite | MARIPOSA BANK 2 | 2544502 | Bank | None | None | None | 58.43% | 0 | 0% | 15.83 | 9.25 | 58.43% | 0 | 0% | 15.83 | 8.92 | 56.35% | 0 | 0% | 15.83 | 8.75 | 55.27% | 0 | 0% | 15.83 | 8.67 | 54.77% | 0 | 0% | 15.83 | 8.65 | 54.64% | 0 | 0%
GNA_254452102_Capacity | Central Valley | Yosemite | MARIPOSA 2102 | 254452102 | Feeder | None | None | None | 69.01% | 0 | 0% | 14.81 | 10.22 | 69.01% | 0 | 0% | 14.81 | 9.88 | 66.71% | 0 | 0% | 14.81 | 9.67 | 65.29% | 0 | 0% | 14.81 | 9.59 | 64.75% | 0 | 0% | 14.81 | 9.57 | 64.62% | 0 | 0%
GNA_2534701_Capacity | Central Valley | Yosemite | FIREBAUGH BANK 1 | 2534701 | Bank | None | None | None | 77.91% | 0 | 0% | 29.7 | 23.14 | 77.91% | 0 | 0% | 29.7 | 23.11 | 77.81% | 0 | 0% | 29.7 | 23.08 | 77.71% | 0 | 0% | 29.7 | 23.1 | 77.78% | 0 | 0% | 29.7 | 23.09 | 77.74% | 0 | 0%
GNA_253471101_Capacity | Central Valley | Yosemite | FIREBAUGH 1101 | 253471101 | Feeder | None | None | None | 70.27% | 0 | 0% | 10.46 | 7.35 | 70.27% | 0 | 0% | 10.46 | 7.32 | 69.98% | 0 | 0% | 10.46 | 7.31 | 69.89% | 0 | 0% | 10.46 | 7.32 | 69.98% | 0 | 0% | 10.46 | 7.34 | 70.17% | 0 | 0%
GNA_253471102_Capacity | Central Valley | Yosemite | FIREBAUGH 1102 | 253471102 | Feeder | None | None | None | 81.14% | 0 | 0% | 12.83 | 10.41 | 81.14% | 0 | 0% | 12.83 | 10.39 | 80.98% | 0 | 0% | 12.83 | 10.36 | 80.75% | 0 | 0% | 12.83 | 10.32 | 80.44% | 0 | 0% | 12.83 | 10.3 | 80.28% | 0 | 0%
GNA_253471103_Capacity | Central Valley | Yosemite | FIREBAUGH 1103 | 253471103 | Feeder | None | None | None | 68.26% | 0 | 0% | 10.46 | 7.14 | 68.26% | 0 | 0% | 10.46 | 7.14 | 68.26% | 0 | 0% | 10.46 | 7.12 | 68.07% | 0 | 0% | 10.46 | 7.12 | 68.07% | 0 | 0% | 10.46 | 7.11 | 67.97% | 0 | 0%
GNA_2534001_Capacity | Central Valley | Yosemite | HAMMONDS BANK 1 | 2534001 | Bank | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253401101_Capacity | Central Valley | Yosemite | HAMMONDS 1101 | 253401101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253401102_Capacity | Central Valley | Yosemite | HAMMONDS 1102 | 253401102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253401104_Capacity | Central Valley | Yosemite | HAMMONDS 1104 | 253401104 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2523102_Capacity | Central Valley | Yosemite | MENDOTA BANK 2 | 2523102 | Bank | Demand Growth | Capacity | 2023 | 108% | 2.38 | 8.013% | 29.7 | 32.08 | 108% | 2.38 | 8.013% | 29.7 | 31.12 | 104.8% | 1.42 | 4.781% | 29.7 | 31.3 | 105.4% | 1.6 | 5.387% | 29.7 | 31.55 | 106.2% | 1.85 | 6.229% | 29.7 | 31.88 | 107.3% | 2.18 | 7.34%
GNA_252311101_Capacity | Central Valley | Yosemite | MENDOTA 1101 | 252311101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252311102_Capacity | Central Valley | Yosemite | MENDOTA 1102 | 252311102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252311103_Capacity | Central Valley | Yosemite | MENDOTA 1103 | 252311103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252311104_Capacity | Central Valley | Yosemite | MENDOTA 1104 | 252311104 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2536703_Capacity | Central Valley | Yosemite | PANOCHE BANK 3 | 2536703 | Bank | Demand Growth | Capacity | 2024 | 192.3% | 27.4 | 92.26% | 29.7 | 26.13 | 87.98% | 0 | 0% | 29.7 | 36.19 | 121.9% | 6.49 | 21.85% | 29.7 | 44.43 | 149.6% | 14.73 | 49.6% | 29.7 | 48.64 | 163.8% | 18.94 | 63.77% | 29.7 | 57.1 | 192.3% | 27.4 | 92.26%
GNA_253671101_Capacity | Central Valley | Yosemite | PANOCHE 1101 | 253671101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253671102_Capacity | Central Valley | Yosemite | PANOCHE 1102 | 253671102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253671103_Capacity | Central Valley | Yosemite | PANOCHE 1103 | 253671103 | Feeder | Demand Growth | Capacity | 2024 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2538801_Capacity | Central Valley | Yosemite | EL CAPITAN BANK 1 | 2538801 | Bank | None | None | None | 60.64% | 0 | 0% | 25.1 | 14.4 | 57.37% | 0 | 0% | 25.1 | 14.57 | 58.05% | 0 | 0% | 25.1 | 14.76 | 58.8% | 0 | 0% | 25.1 | 14.98 | 59.68% | 0 | 0% | 25.1 | 15.22 | 60.64% | 0 | 0%
GNA_253881103_Capacity | Central Valley | Yosemite | EL CAPITAN 1103 | 253881103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253881104_Capacity | Central Valley | Yosemite | EL CAPITAN 1104 | 253881104 | Feeder | None | None | None | 89.66% | 0 | 0% | 12.19 | 10.5 | 86.14% | 0 | 0% | 12.19 | 10.57 | 86.71% | 0 | 0% | 12.19 | 10.66 | 87.45% | 0 | 0% | 12.19 | 10.78 | 88.43% | 0 | 0% | 12.19 | 10.93 | 89.66% | 0 | 0%
GNA_2538802_Capacity | Central Valley | Yosemite | EL CAPITAN BANK 2 | 2538802 | Bank | Demand Growth | Capacity | 2023 | 108.4% | 2.49 | 8.384% | 29.7 | 31.38 | 105.7% | 1.68 | 5.657% | 29.7 | 31.53 | 106.2% | 1.83 | 6.162% | 29.7 | 31.65 | 106.6% | 1.95 | 6.566% | 29.7 | 31.92 | 107.5% | 2.22 | 7.475% | 29.7 | 32.19 | 108.4% | 2.49 | 8.384%
GNA_253881102_Capacity | Central Valley | Yosemite | EL CAPITAN 1102 | 253881102 | Feeder | Demand Growth | Capacity | 2023 | 121.6% | 2.63 | 21.58% | 12.19 | 14.17 | 116.2% | 1.98 | 16.24% | 12.19 | 14.3 | 117.3% | 2.11 | 17.31% | 12.19 | 14.41 | 118.2% | 2.22 | 18.21% | 12.19 | 14.62 | 119.9% | 2.43 | 19.93% | 12.19 | 14.82 | 121.6% | 2.63 | 21.58%
GNA_253881105_Capacity | Central Valley | Yosemite | EL CAPITAN 1105 | 253881105 | Feeder | None | None | None | 59.15% | 0 | 0% | 12.19 | 7.21 | 59.15% | 0 | 0% | 12.19 | 7.18 | 58.9% | 0 | 0% | 12.19 | 7.15 | 58.65% | 0 | 0% | 12.19 | 7.12 | 58.41% | 0 | 0% | 12.19 | 7.08 | 58.08% | 0 | 0%
GNA_253881106_Capacity | Central Valley | Yosemite | EL CAPITAN 1106 | 253881106 | Feeder | None | None | None | 97.37% | 0 | 0% | 12.19 | 11.87 | 97.37% | 0 | 0% | 12.19 | 11.72 | 96.14% | 0 | 0% | 12.19 | 11.61 | 95.24% | 0 | 0% | 12.19 | 11.55 | 94.75% | 0 | 0% | 12.19 | 11.5 | 94.34% | 0 | 0%
GNA_2528003_Capacity | Central Valley | Yosemite | MERCED BANK 3 | 2528003 | Bank | None | None | None | 60.63% | 0 | 0% | 44.53 | 27 | 60.63% | 0 | 0% | 44.53 | 26.95 | 60.52% | 0 | 0% | 44.53 | 26.92 | 60.45% | 0 | 0% | 44.53 | 26.97 | 60.57% | 0 | 0% | 44.53 | 26.99 | 60.61% | 0 | 0%
GNA_252801108_Capacity | Central Valley | Yosemite | MERCED 1108 | 252801108 | Feeder | None | None | None | 88.52% | 0 | 0% | 11.67 | 10.33 | 88.52% | 0 | 0% | 11.67 | 10.27 | 88% | 0 | 0% | 11.67 | 10.22 | 87.57% | 0 | 0% | 11.67 | 10.22 | 87.57% | 0 | 0% | 11.67 | 10.19 | 87.32% | 0 | 0%
GNA_252801114_Capacity | Central Valley | Yosemite | MERCED 1114 | 252801114 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252801116_Capacity | Central Valley | Yosemite | MERCED 1116 | 252801116 | Feeder | None | None | None | 90.65% | 0 | 0% | 10.69 | 9.68 | 90.55% | 0 | 0% | 10.69 | 9.67 | 90.46% | 0 | 0% | 10.69 | 9.65 | 90.27% | 0 | 0% | 10.69 | 9.67 | 90.46% | 0 | 0% | 10.69 | 9.69 | 90.65% | 0 | 0%
GNA_2543003_Capacity | Central Valley | Yosemite | WILSON BANK 3 | 2543003 | Bank | None | None | None | 97.3% | 0 | 0% | 19.28 | 18.32 | 95.02% | 0 | 0% | 19.28 | 18.39 | 95.38% | 0 | 0% | 19.28 | 18.47 | 95.8% | 0 | 0% | 19.28 | 18.58 | 96.37% | 0 | 0% | 19.28 | 18.76 | 97.3% | 0 | 0%
GNA_254301101_Capacity | Central Valley | Yosemite | WILSON 1101 | 254301101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254301102_Capacity | Central Valley | Yosemite | WILSON 1102 | 254301102 | Feeder | None | None | None | 72.65% | 0 | 0% | 6.18 | 4.48 | 72.49% | 0 | 0% | 6.18 | 4.48 | 72.49% | 0 | 0% | 6.18 | 4.47 | 72.33% | 0 | 0% | 6.18 | 4.47 | 72.33% | 0 | 0% | 6.18 | 4.49 | 72.65% | 0 | 0%
GNA_254301103_Capacity | Central Valley | Yosemite | WILSON 1103 | 254301103 | Feeder | None | None | None | 97.87% | 0 | 0% | 12.19 | 11.92 | 97.79% | 0 | 0% | 12.19 | 11.91 | 97.7% | 0 | 0% | 12.19 | 11.9 | 97.62% | 0 | 0% | 12.19 | 11.89 | 97.54% | 0 | 0% | 12.19 | 11.93 | 97.87% | 0 | 0%
GNA_2538803_Capacity | Central Valley | Yosemite | EL CAPITAN BANK 3 | 2538803 | Bank | None | None | None | 79.9% | 0 | 0% | 44.52 | 35.44 | 79.6% | 0 | 0% | 44.52 | 35.31 | 79.31% | 0 | 0% | 44.52 | 35.25 | 79.18% | 0 | 0% | 44.52 | 35.32 | 79.34% | 0 | 0% | 44.52 | 35.57 | 79.9% | 0 | 0%
GNA_253882109_Capacity | Central Valley | Yosemite | EL CAPITAN 2109 | 253882109 | Feeder | None | None | None | 76.22% | 0 | 0% | 21.11 | 16 | 75.79% | 0 | 0% | 21.11 | 15.98 | 75.7% | 0 | 0% | 21.11 | 16.01 | 75.84% | 0 | 0% | 21.11 | 16.02 | 75.89% | 0 | 0% | 21.11 | 16.09 | 76.22% | 0 | 0%
GNA_253882110_Capacity | Central Valley | Yosemite | EL CAPITAN 2110 | 253882110 | Feeder | None | None | None | 94.27% | 0 | 0% | 21.11 | 19.9 | 94.27% | 0 | 0% | 21.11 | 19.75 | 93.56% | 0 | 0% | 21.11 | 19.66 | 93.13% | 0 | 0% | 21.11 | 19.72 | 93.42% | 0 | 0% | 21.11 | 19.9 | 94.27% | 0 | 0%
GNA_2528001_Capacity | Central Valley | Yosemite | MERCED BANK 1 | 2528001 | Bank | None | None | None | 86.1% | 0 | 0% | 44.52 | 35.92 | 80.68% | 0 | 0% | 44.52 | 35.79 | 80.39% | 0 | 0% | 44.52 | 36.52 | 82.03% | 0 | 0% | 44.52 | 37.21 | 83.58% | 0 | 0% | 44.52 | 38.33 | 86.1% | 0 | 0%
GNA_252802101_Capacity | Central Valley | Yosemite | MERCED 2101 | 252802101 | Feeder | None | None | None | 84.23% | 0 | 0% | 21.11 | 17.78 | 84.23% | 0 | 0% | 21.11 | 17.49 | 82.85% | 0 | 0% | 21.11 | 17.46 | 82.71% | 0 | 0% | 21.11 | 17.56 | 83.18% | 0 | 0% | 21.11 | 17.69 | 83.8% | 0 | 0%
GNA_252802102_Capacity | Central Valley | Yosemite | MERCED 2102 | 252802102 | Feeder | None | None | None | 99.38% | 0 | 0% | 21.11 | 18.42 | 87.26% | 0 | 0% | 21.11 | 18.64 | 88.3% | 0 | 0% | 21.11 | 19.4 | 91.9% | 0 | 0% | 21.11 | 20 | 94.74% | 0 | 0% | 21.11 | 20.98 | 99.38% | 0 | 0%
GNA_2528102_Capacity | Central Valley | Yosemite | MERCED FALLS BANK 2 | 2528102 | Bank | Demand Growth | Capacity | 2027 | 100.8% | 0.08 | 0.7526% | 10.63 | 10.62 | 99.91% | 0 | 0% | 10.63 | 10.62 | 99.91% | 0 | 0% | 10.63 | 10.62 | 99.91% | 0 | 0% | 10.63 | 10.65 | 100.2% | 0.02 | 0.1881% | 10.63 | 10.71 | 100.8% | 0.08 | 0.7526%
GNA_252811102_Capacity | Central Valley | Yosemite | MERCED FALLS 1102 | 252811102 | Feeder | None | None | None | 94.67% | 0 | 0% | 12.19 | 11.46 | 94.01% | 0 | 0% | 12.19 | 11.46 | 94.01% | 0 | 0% | 12.19 | 11.46 | 94.01% | 0 | 0% | 12.19 | 11.49 | 94.26% | 0 | 0% | 12.19 | 11.54 | 94.67% | 0 | 0%
GNA_2544602_Capacity | Central Valley | Yosemite | NEWHALL BANK 2 | 2544602 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254461111_Capacity | Central Valley | Yosemite | NEWHALL 1111 | 254461111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2544603_Capacity | Central Valley | Yosemite | NEWHALL BANK 3 | 2544603 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_254461109_Capacity | Central Valley | Yosemite | NEWHALL 1109 | 254461109 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1632501_Capacity | Central Valley | Yosemite | CROWS LANDING BANK 1 | 1632501 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163251101_Capacity | Central Valley | Yosemite | CROWS LANDING 1101 | 163251101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163251102_Capacity | Central Valley | Yosemite | CROWS LANDING 1102 | 163251102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1631101_Capacity | Central Valley | Yosemite | GUSTINE BANK 1 | 1631101 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163111101_Capacity | Central Valley | Yosemite | GUSTINE 1101 | 163111101 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1631102_Capacity | Central Valley | Yosemite | GUSTINE BANK 2 | 1631102 | Bank | None | None | None | 97.98% | 0 | 0% | 10.4 | 9.69 | 93.17% | 0 | 0% | 10.4 | 9.77 | 93.94% | 0 | 0% | 10.4 | 9.87 | 94.9% | 0 | 0% | 10.4 | 10.03 | 96.44% | 0 | 0% | 10.4 | 10.19 | 97.98% | 0 | 0%
GNA_163111102_Capacity | Central Valley | Yosemite | GUSTINE 1102 | 163111102 | Feeder | None | None | None | 99.43% | 0 | 0% | 10.46 | 9.9 | 94.65% | 0 | 0% | 10.46 | 9.98 | 95.41% | 0 | 0% | 10.46 | 10.08 | 96.37% | 0 | 0% | 10.46 | 10.23 | 97.8% | 0 | 0% | 10.46 | 10.4 | 99.43% | 0 | 0%
GNA_1627401_Capacity | Central Valley | Yosemite | NEWMAN BANK 1 | 1627401 | Bank | None | None | None | 98.88% | 0 | 0% | 9.8 | 9.01 | 91.94% | 0 | 0% | 9.8 | 9.34 | 95.31% | 0 | 0% | 9.8 | 9.44 | 96.33% | 0 | 0% | 9.8 | 9.57 | 97.65% | 0 | 0% | 9.8 | 9.69 | 98.88% | 0 | 0%
GNA_162741101_Capacity | Central Valley | Yosemite | NEWMAN 1101 | 162741101 | Feeder | None | None | None | 62.98% | 0 | 0% | 8.13 | 5.12 | 62.98% | 0 | 0% | 8.13 | 5.1 | 62.73% | 0 | 0% | 8.13 | 5.07 | 62.36% | 0 | 0% | 8.13 | 5.05 | 62.12% | 0 | 0% | 8.13 | 5.03 | 61.87% | 0 | 0%
GNA_162741102_Capacity | Central Valley | Yosemite | NEWMAN 1102 | 162741102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1627402_Capacity | Central Valley | Yosemite | NEWMAN BANK 2 | 1627402 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162741105_Capacity | Central Valley | Yosemite | NEWMAN 1105 | 162741105 | Feeder | None | None | None | 74.2% | 0 | 0% | 12.83 | 9.52 | 74.2% | 0 | 0% | 12.83 | 9.5 | 74.05% | 0 | 0% | 12.83 | 9.48 | 73.89% | 0 | 0% | 12.83 | 9.48 | 73.89% | 0 | 0% | 12.83 | 9.49 | 73.97% | 0 | 0%
GNA_162741106_Capacity | Central Valley | Yosemite | NEWMAN 1106 | 162741106 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1637101_Capacity | Central Valley | Yosemite | COTTLE BANK 1 | 1637101 | Bank | None | None | None | 44.46% | 0 | 0% | 44.53 | 18.72 | 42.04% | 0 | 0% | 44.53 | 18.92 | 42.49% | 0 | 0% | 44.53 | 19.14 | 42.98% | 0 | 0% | 44.53 | 19.46 | 43.7% | 0 | 0% | 44.53 | 19.8 | 44.46% | 0 | 0%
GNA_163711701_Capacity | Central Valley | Yosemite | COTTLE 1701 | 163711701 | Feeder | None | None | None | 83.16% | 0 | 0% | 18.76 | 15 | 79.96% | 0 | 0% | 18.76 | 15.09 | 80.44% | 0 | 0% | 18.76 | 15.21 | 81.08% | 0 | 0% | 18.76 | 15.4 | 82.09% | 0 | 0% | 18.76 | 15.6 | 83.16% | 0 | 0%
GNA_163711703_Capacity | Central Valley | Yosemite | COTTLE 1703 | 163711703 | Feeder | None | None | None | 21.8% | 0 | 0% | 18.76 | 3.6 | 19.19% | 0 | 0% | 18.76 | 3.71 | 19.78% | 0 | 0% | 18.76 | 3.81 | 20.31% | 0 | 0% | 18.76 | 3.94 | 21% | 0 | 0% | 18.76 | 4.09 | 21.8% | 0 | 0%
GNA_1637102_Capacity | Central Valley | Yosemite | COTTLE BANK 2 | 1637102 | Bank | None | None | None | 76.24% | 0 | 0% | 39.6 | 30.19 | 76.24% | 0 | 0% | 39.6 | 30.08 | 75.96% | 0 | 0% | 39.6 | 30 | 75.76% | 0 | 0% | 39.6 | 29.99 | 75.73% | 0 | 0% | 39.6 | 30.05 | 75.88% | 0 | 0%
GNA_163711702_Capacity | Central Valley | Yosemite | COTTLE 1702 | 163711702 | Feeder | None | None | None | 76.12% | 0 | 0% | 18.76 | 14.1 | 75.16% | 0 | 0% | 18.76 | 13.98 | 74.52% | 0 | 0% | 18.76 | 14 | 74.63% | 0 | 0% | 18.76 | 14.11 | 75.21% | 0 | 0% | 18.76 | 14.28 | 76.12% | 0 | 0%
GNA_163711704_Capacity | Central Valley | Yosemite | COTTLE 1704 | 163711704 | Feeder | None | None | None | 71.53% | 0 | 0% | 17.7 | 12.66 | 71.53% | 0 | 0% | 17.7 | 12.64 | 71.41% | 0 | 0% | 17.7 | 12.62 | 71.3% | 0 | 0% | 17.7 | 12.6 | 71.19% | 0 | 0% | 17.7 | 12.57 | 71.02% | 0 | 0%
GNA_163711707_Capacity | Central Valley | Yosemite | COTTLE 1707 | 163711707 | Feeder | None | None | None | 56.87% | 0 | 0% | 16.81 | 9.56 | 56.87% | 0 | 0% | 16.81 | 9.56 | 56.87% | 0 | 0% | 16.81 | 9.54 | 56.75% | 0 | 0% | 16.81 | 9.55 | 56.81% | 0 | 0% | 16.81 | 9.55 | 56.81% | 0 | 0%
GNA_163711708_Capacity | Central Valley | Yosemite | COTTLE 1708 | 163711708 | Feeder | None | None | None | 80.73% | 0 | 0% | 16.81 | 13.57 | 80.73% | 0 | 0% | 16.81 | 13.55 | 80.61% | 0 | 0% | 16.81 | 13.55 | 80.61% | 0 | 0% | 16.81 | 13.54 | 80.55% | 0 | 0% | 16.81 | 13.55 | 80.61% | 0 | 0%
GNA_1631901_Capacity | Central Valley | Yosemite | RIVERBANK BANK 1 | 1631901 | Bank | None | None | None | 84.17% | 0 | 0% | 27.85 | 21.95 | 78.82% | 0 | 0% | 27.85 | 22.24 | 79.86% | 0 | 0% | 27.85 | 22.53 | 80.9% | 0 | 0% | 27.85 | 22.93 | 82.33% | 0 | 0% | 27.85 | 23.44 | 84.17% | 0 | 0%
GNA_163191711_Capacity | Central Valley | Yosemite | RIVERBANK 1711 | 163191711 | Feeder | None | None | None | 54.31% | 0 | 0% | 12.98 | 6.58 | 50.69% | 0 | 0% | 12.98 | 6.66 | 51.31% | 0 | 0% | 12.98 | 6.74 | 51.93% | 0 | 0% | 12.98 | 6.88 | 53% | 0 | 0% | 12.98 | 7.05 | 54.31% | 0 | 0%
GNA_163191712_Capacity | Central Valley | Yosemite | RIVERBANK 1712 | 163191712 | Feeder | None | None | None | 65.97% | 0 | 0% | 9.08 | 5.51 | 60.68% | 0 | 0% | 9.08 | 5.59 | 61.56% | 0 | 0% | 9.08 | 5.68 | 62.56% | 0 | 0% | 9.08 | 5.82 | 64.1% | 0 | 0% | 9.08 | 5.99 | 65.97% | 0 | 0%
GNA_163191714_Capacity | Central Valley | Yosemite | RIVERBANK 1714 | 163191714 | Feeder | None | None | None | 53.79% | 0 | 0% | 16.1 | 8.23 | 51.12% | 0 | 0% | 16.1 | 8.31 | 51.61% | 0 | 0% | 16.1 | 8.38 | 52.05% | 0 | 0% | 16.1 | 8.5 | 52.8% | 0 | 0% | 16.1 | 8.66 | 53.79% | 0 | 0%
GNA_1631902_Capacity | Central Valley | Yosemite | RIVERBANK BANK 2 | 1631902 | Bank | None | None | None | 82.19% | 0 | 0% | 44.53 | 35.07 | 78.76% | 0 | 0% | 44.53 | 35.29 | 79.25% | 0 | 0% | 44.53 | 35.5 | 79.72% | 0 | 0% | 44.53 | 36 | 80.84% | 0 | 0% | 44.53 | 36.6 | 82.19% | 0 | 0%
GNA_163191713_Capacity | Central Valley | Yosemite | RIVERBANK 1713 | 163191713 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163191715_Capacity | Central Valley | Yosemite | RIVERBANK 1715 | 163191715 | Feeder | None | None | None | 82.18% | 0 | 0% | 14.42 | 11.27 | 78.16% | 0 | 0% | 14.42 | 11.39 | 78.99% | 0 | 0% | 14.42 | 11.48 | 79.61% | 0 | 0% | 14.42 | 11.65 | 80.79% | 0 | 0% | 14.42 | 11.85 | 82.18% | 0 | 0%
GNA_163191716_Capacity | Central Valley | Yosemite | RIVERBANK 1716 | 163191716 | Feeder | None | None | None | 81.32% | 0 | 0% | 16.81 | 13.66 | 81.26% | 0 | 0% | 16.81 | 13.56 | 80.67% | 0 | 0% | 16.81 | 13.53 | 80.49% | 0 | 0% | 16.81 | 13.6 | 80.9% | 0 | 0% | 16.81 | 13.67 | 81.32% | 0 | 0%
GNA_1629801_Capacity | Central Valley | Yosemite | VALLEY HOME BANK 1 | 1629801 | Bank | None | None | None | 76.07% | 0 | 0% | 5.39 | 4.1 | 76.07% | 0 | 0% | 43.39 | 4.08 | 9.403% | 0 | 0% | 43.39 | 4.07 | 9.38% | 0 | 0% | 43.39 | 4.08 | 9.403% | 0 | 0% | 43.39 | 4.11 | 9.472% | 0 | 0%
GNA_162981702_Capacity | Central Valley | Yosemite | VALLEY HOME 1702 | 162981702 | Feeder | None | None | None | 73.22% | 0 | 0% | 5.49 | 4.01 | 73.04% | 0 | 0% | 5.49 | 3.99 | 72.68% | 0 | 0% | 5.49 | 3.98 | 72.5% | 0 | 0% | 5.49 | 3.99 | 72.68% | 0 | 0% | 5.49 | 4.02 | 73.22% | 0 | 0%
GNA_1629802_Capacity | Central Valley | Yosemite | VALLEY HOME BANK 2 | 1629802 | Bank | None | None | None | 78.04% | 0 | 0% | 23.27 | 17.85 | 76.71% | 0 | 0% | 23.27 | 17.83 | 76.62% | 0 | 0% | 23.27 | 17.82 | 76.58% | 0 | 0% | 23.27 | 17.93 | 77.05% | 0 | 0% | 23.27 | 18.16 | 78.04% | 0 | 0%
GNA_162981704_Capacity | Central Valley | Yosemite | VALLEY HOME 1704 | 162981704 | Feeder | None | None | None | 61.12% | 0 | 0% | 9.08 | 5.53 | 60.9% | 0 | 0% | 9.08 | 5.52 | 60.79% | 0 | 0% | 9.08 | 5.51 | 60.68% | 0 | 0% | 9.08 | 5.53 | 60.9% | 0 | 0% | 9.08 | 5.55 | 61.12% | 0 | 0%
GNA_162981703_Capacity | Central Valley | Yosemite | VALLEY HOME 1703 | 162981703 | Feeder | None | None | None | 95.51% | 0 | 0% | 14.24 | 13.32 | 93.54% | 0 | 0% | 14.24 | 13.31 | 93.47% | 0 | 0% | 14.24 | 13.3 | 93.4% | 0 | 0% | 14.24 | 13.4 | 94.1% | 0 | 0% | 14.24 | 13.6 | 95.51% | 0 | 0%
GNA_2544301_Capacity | Central Valley | Yosemite | COARSEGOLD BANK 1 | 2544301 | Bank | None | None | None | 33.67% | 0 | 0% | 15.8 | 5.32 | 33.67% | 0 | 0% | 15.8 | 5.27 | 33.35% | 0 | 0% | 15.8 | 5.25 | 33.23% | 0 | 0% | 15.8 | 5.26 | 33.29% | 0 | 0% | 15.8 | 5.29 | 33.48% | 0 | 0%
GNA_254432102_Capacity | Central Valley | Yosemite | COARSEGOLD 2102 | 254432102 | Feeder | None | None | None | 56.54% | 0 | 0% | 8.56 | 4.84 | 56.54% | 0 | 0% | 8.56 | 4.79 | 55.96% | 0 | 0% | 8.56 | 4.78 | 55.84% | 0 | 0% | 8.56 | 4.79 | 55.96% | 0 | 0% | 8.56 | 4.82 | 56.31% | 0 | 0%
GNA_2544302_Capacity | Central Valley | Yosemite | COARSEGOLD BANK 2 | 2544302 | Bank | None | None | None | 66.13% | 0 | 0% | 41.6 | 27.51 | 66.13% | 0 | 0% | 41.6 | 27.27 | 65.55% | 0 | 0% | 41.6 | 26.97 | 64.83% | 0 | 0% | 41.6 | 26.86 | 64.57% | 0 | 0% | 41.6 | 26.92 | 64.71% | 0 | 0%
GNA_254432103_Capacity | Central Valley | Yosemite | COARSEGOLD 2103 | 254432103 | Feeder | None | None | None | 75.05% | 0 | 0% | 18.52 | 13.79 | 74.46% | 0 | 0% | 18.52 | 13.8 | 74.51% | 0 | 0% | 18.52 | 13.8 | 74.51% | 0 | 0% | 18.52 | 13.85 | 74.78% | 0 | 0% | 18.52 | 13.9 | 75.05% | 0 | 0%
GNA_254432104_Capacity | Central Valley | Yosemite | COARSEGOLD 2104 | 254432104 | Feeder | None | None | None | 70.57% | 0 | 0% | 22.22 | 15.68 | 70.57% | 0 | 0% | 22.22 | 15.5 | 69.76% | 0 | 0% | 22.22 | 15.3 | 68.86% | 0 | 0% | 22.22 | 15.21 | 68.45% | 0 | 0% | 22.22 | 15.26 | 68.68% | 0 | 0%
GNA_2544202_Capacity | Central Valley | Yosemite | OAKHURST BANK 2 | 2544202 | Bank | None | None | None | 39.9% | 0 | 0% | 29.6 | 11.81 | 39.9% | 0 | 0% | 29.6 | 11.52 | 38.92% | 0 | 0% | 29.6 | 11.26 | 38.04% | 0 | 0% | 29.6 | 11.17 | 37.74% | 0 | 0% | 29.6 | 11.14 | 37.64% | 0 | 0%
GNA_254421103_Capacity | Central Valley | Yosemite | OAKHURST 1103 | 254421103 | Feeder | None | None | None | 87.64% | 0 | 0% | 13.19 | 11.56 | 87.64% | 0 | 0% | 13.19 | 11.28 | 85.52% | 0 | 0% | 13.19 | 11.02 | 83.55% | 0 | 0% | 13.19 | 10.94 | 82.94% | 0 | 0% | 13.19 | 10.91 | 82.71% | 0 | 0%
GNA_2525202_Capacity | Central Valley | Yosemite | SAN JOAQUIN POWER HOUSE NO 2 BANK 2 | 2525202 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252521103_Capacity | Central Valley | Yosemite | SAN JOAQUIN POWER HOUSE NO 2 1103 | 252521103 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2525302_Capacity | Central Valley | Yosemite | SAN JOAQUIN POWER HOUSE NO 3 BANK 2 | 2525302 | Bank | None | None | None | 72.17% | 0 | 0% | 6.9 | 4.98 | 72.17% | 0 | 0% | 6.9 | 4.93 | 71.45% | 0 | 0% | 6.9 | 4.89 | 70.87% | 0 | 0% | 6.9 | 4.85 | 70.29% | 0 | 0% | 6.9 | 4.81 | 69.71% | 0 | 0%
GNA_252531101_Capacity | Central Valley | Yosemite | SAN JOAQUIN #3 PH 1101 | 252531101 | Feeder | None | None | None | 45.11% | 0 | 0% | 6.14 | 2.77 | 45.11% | 0 | 0% | 6.14 | 2.74 | 44.63% | 0 | 0% | 6.14 | 2.72 | 44.3% | 0 | 0% | 6.14 | 2.7 | 43.97% | 0 | 0% | 6.14 | 2.69 | 43.81% | 0 | 0%
GNA_252531102_Capacity | Central Valley | Yosemite | SAN JOAQUIN #3 PH 1102 | 252531102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252531103_Capacity | Central Valley | Yosemite | SAN JOAQUIN #3 PH 1103 | 252531103 | Feeder | None | None | None | 57.84% | 0 | 0% | 3.7 | 2.12 | 57.3% | 0 | 0% | 3.7 | 2.12 | 57.3% | 0 | 0% | 3.7 | 2.12 | 57.3% | 0 | 0% | 3.7 | 2.13 | 57.57% | 0 | 0% | 3.7 | 2.14 | 57.84% | 0 | 0%
GNA_254421101_Capacity | Central Valley | Yosemite | OAKHURST 1101 | 254421101 | Feeder | None | None | None | 65.39% | 0 | 0% | 10.69 | 6.99 | 65.39% | 0 | 0% | 10.69 | 6.89 | 64.45% | 0 | 0% | 10.69 | 6.81 | 63.7% | 0 | 0% | 10.69 | 6.77 | 63.33% | 0 | 0% | 10.69 | 6.76 | 63.24% | 0 | 0%
GNA_254421102_Capacity | Central Valley | Yosemite | OAKHURST 1102 | 254421102 | Feeder | None | None | None | 34.42% | 0 | 0% | 10.69 | 3.68 | 34.42% | 0 | 0% | 10.69 | 3.65 | 34.14% | 0 | 0% | 10.69 | 3.58 | 33.49% | 0 | 0% | 10.69 | 3.54 | 33.12% | 0 | 0% | 10.69 | 3.53 | 33.02% | 0 | 0%
GNA_2540401_Capacity | Central Valley | Yosemite | DOS PALOS BANK 1 | 2540401 | Bank | None | None | None | 77.38% | 0 | 0% | 12.38 | 9.22 | 74.47% | 0 | 0% | 12.38 | 9.3 | 75.12% | 0 | 0% | 12.38 | 9.39 | 75.85% | 0 | 0% | 12.38 | 9.47 | 76.49% | 0 | 0% | 12.38 | 9.58 | 77.38% | 0 | 0%
GNA_254041101_Capacity | Central Valley | Yosemite | DOS PALOS 1101 | 254041101 | Feeder | None | None | None | 79% | 0 | 0% | 12.19 | 9.27 | 76.05% | 0 | 0% | 12.19 | 9.35 | 76.7% | 0 | 0% | 12.19 | 9.44 | 77.44% | 0 | 0% | 12.19 | 9.52 | 78.1% | 0 | 0% | 12.19 | 9.63 | 79% | 0 | 0%
GNA_2553701_Capacity | Central Valley | Yosemite | ORO LOMA BANK 1 | 2553701 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_255371106_Capacity | Central Valley | Yosemite | ORO LOMA 1106 | 255371106 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_255371108_Capacity | Central Valley | Yosemite | ORO LOMA 1108 | 255371108 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_255371110_Capacity | Central Valley | Yosemite | ORO LOMA 1110 | 255371110 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2553703_Capacity | Central Valley | Yosemite | ORO LOMA BANK 3 | 2553703 | Bank | None | None | None | 43.16% | 0 | 0% | 44.6 | 19.04 | 42.69% | 0 | 0% | 44.6 | 19.09 | 42.8% | 0 | 0% | 44.6 | 19.13 | 42.89% | 0 | 0% | 44.6 | 19.19 | 43.03% | 0 | 0% | 44.6 | 19.25 | 43.16% | 0 | 0%
GNA_255371115_Capacity | Central Valley | Yosemite | ORO LOMA 1115 | 255371115 | Feeder | None | None | None | 66.14% | 0 | 0% | 10.69 | 7.07 | 66.14% | 0 | 0% | 10.69 | 7.02 | 65.67% | 0 | 0% | 10.69 | 6.96 | 65.11% | 0 | 0% | 10.69 | 6.92 | 64.73% | 0 | 0% | 10.69 | 6.87 | 64.27% | 0 | 0%
GNA_255371116_Capacity | Central Valley | Yosemite | ORO LOMA 1116 | 255371116 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_255371117_Capacity | Central Valley | Yosemite | ORO LOMA 1117 | 255371117 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_255371118_Capacity | Central Valley | Yosemite | ORO LOMA 1118 | 255371118 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2535401_Capacity | Central Valley | Yosemite | SANTA RITA BANK 1 | 2535401 | Bank | None | None | None | 82.23% | 0 | 0% | 19.19 | 15.78 | 82.23% | 0 | 0% | 19.19 | 15.75 | 82.07% | 0 | 0% | 19.19 | 15.72 | 81.92% | 0 | 0% | 19.19 | 15.69 | 81.76% | 0 | 0% | 19.19 | 15.69 | 81.76% | 0 | 0%
GNA_253541102_Capacity | Central Valley | Yosemite | SANTA RITA 1102 | 253541102 | Feeder | Demand Growth | Capacity | 2023 | 106.4% | 0.54 | 6.391% | 8.45 | 8.99 | 106.4% | 0.54 | 6.391% | 8.45 | 8.98 | 106.3% | 0.53 | 6.272% | 8.45 | 8.96 | 106% | 0.51 | 6.036% | 8.45 | 8.95 | 105.9% | 0.5 | 5.917% | 8.45 | 8.95 | 105.9% | 0.5 | 5.917%
GNA_253541105_Capacity | Central Valley | Yosemite | SANTA RITA 1105 | 253541105 | Feeder | None | None | None | 98.65% | 0 | 0% | 8.13 | 8.02 | 98.65% | 0 | 0% | 8.13 | 7.98 | 98.15% | 0 | 0% | 8.13 | 7.96 | 97.91% | 0 | 0% | 8.13 | 7.94 | 97.66% | 0 | 0% | 8.13 | 7.93 | 97.54% | 0 | 0%
GNA_2542702_Capacity | Central Valley | Yosemite | CASSIDY BANK 2 | 2542702 | Bank | None | None | None | 68.85% | 0 | 0% | 44.97 | 27.5 | 61.15% | 0 | 0% | 44.97 | 30.45 | 67.71% | 0 | 0% | 44.97 | 30.58 | 68% | 0 | 0% | 44.97 | 30.74 | 68.36% | 0 | 0% | 44.97 | 30.96 | 68.85% | 0 | 0%
GNA_254272107_Capacity | Central Valley | Yosemite | CASSIDY 2107 | 254272107 | Feeder | None | None | None | 96.9% | 0 | 0% | 10.63 | 10.08 | 94.83% | 0 | 0% | 10.63 | 10.11 | 95.11% | 0 | 0% | 10.63 | 10.15 | 95.48% | 0 | 0% | 10.63 | 10.2 | 95.95% | 0 | 0% | 10.63 | 10.3 | 96.9% | 0 | 0%
GNA_254272108_Capacity | Central Valley | Yosemite | CASSIDY 2108 | 254272108 | Feeder | Demand Growth | Capacity | 2023 | 204.5% | 11.11 | 104.5% | 10.63 | 18.81 | 177% | 8.18 | 76.95% | 10.63 | 21.64 | 203.6% | 11.01 | 103.6% | 10.63 | 21.66 | 203.8% | 11.03 | 103.8% | 10.63 | 21.69 | 204% | 11.06 | 104% | 10.63 | 21.74 | 204.5% | 11.11 | 104.5%
GNA_1633501_Capacity | Central Valley | Yosemite | CURTIS BANK 1 | 1633501 | Bank | None | None | None | 94.87% | 0 | 0% | 44.6 | 42.31 | 94.87% | 0 | 0% | 44.6 | 41.64 | 93.36% | 0 | 0% | 44.6 | 41.05 | 92.04% | 0 | 0% | 44.6 | 40.85 | 91.59% | 0 | 0% | 44.6 | 40.91 | 91.73% | 0 | 0%
GNA_163351701_Capacity | Central Valley | Yosemite | CURTIS 1701 | 163351701 | Feeder | None | None | None | 82.88% | 0 | 0% | 17.7 | 14.67 | 82.88% | 0 | 0% | 17.7 | 14.52 | 82.03% | 0 | 0% | 17.7 | 14.36 | 81.13% | 0 | 0% | 17.7 | 14.3 | 80.79% | 0 | 0% | 17.7 | 14.25 | 80.51% | 0 | 0%
GNA_1632401_Capacity | Central Valley | Yosemite | TAR FLAT BANK 1 | 1632401 | Bank | None | None | None | 51.5% | 0 | 0% | 4 | 2.06 | 51.5% | 0 | 0% | 4 | 2.05 | 51.25% | 0 | 0% | 4 | 2.02 | 50.5% | 0 | 0% | 4 | 2.01 | 50.25% | 0 | 0% | 4 | 2 | 50% | 0 | 0%
GNA_163240401_Capacity | Central Valley | Yosemite | TAR FLAT 0401 | 163240401 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163240402_Capacity | Central Valley | Yosemite | TAR FLAT 0402 | 163240402 | Feeder | None | None | None | 52.63% | 0 | 0% | 1.9 | 1 | 52.63% | 0 | 0% | 1.9 | 0.99 | 52.11% | 0 | 0% | 1.9 | 0.98 | 51.58% | 0 | 0% | 1.9 | 0.97 | 51.05% | 0 | 0% | 1.9 | 0.97 | 51.05% | 0 | 0%
GNA_163351702_Capacity | Central Valley | Yosemite | CURTIS 1702 | 163351702 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163351703_Capacity | Central Valley | Yosemite | CURTIS 1703 | 163351703 | Feeder | None | None | None | 83.87% | 0 | 0% | 17.67 | 14.82 | 83.87% | 0 | 0% | 17.67 | 14.5 | 82.06% | 0 | 0% | 17.67 | 14.22 | 80.48% | 0 | 0% | 17.67 | 14.11 | 79.85% | 0 | 0% | 17.67 | 14.16 | 80.14% | 0 | 0%
GNA_1633502_Capacity | Central Valley | Yosemite | CURTIS BANK 2 | 1633502 | Bank | None | None | None | 53.95% | 0 | 0% | 34.9 | 18.67 | 53.5% | 0 | 0% | 34.9 | 18.65 | 53.44% | 0 | 0% | 34.9 | 18.64 | 53.41% | 0 | 0% | 34.9 | 18.7 | 53.58% | 0 | 0% | 34.9 | 18.83 | 53.95% | 0 | 0%
GNA_163351704_Capacity | Central Valley | Yosemite | CURTIS 1704 | 163351704 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163351705_Capacity | Central Valley | Yosemite | CURTIS 1705 | 163351705 | Feeder | None | None | None | 56.63% | 0 | 0% | 16.81 | 9.4 | 55.92% | 0 | 0% | 16.81 | 9.4 | 55.92% | 0 | 0% | 16.81 | 9.39 | 55.86% | 0 | 0% | 16.81 | 9.44 | 56.16% | 0 | 0% | 16.81 | 9.52 | 56.63% | 0 | 0%
GNA_1636601_Capacity | Central Valley | Yosemite | MIWUK BANK 1 | 1636601 | Bank | None | None | None | 81.09% | 0 | 0% | 13.17 | 10.68 | 81.09% | 0 | 0% | 13.17 | 10.53 | 79.95% | 0 | 0% | 13.17 | 10.45 | 79.35% | 0 | 0% | 13.17 | 10.39 | 78.89% | 0 | 0% | 13.17 | 10.42 | 79.12% | 0 | 0%
GNA_163661701_Capacity | Central Valley | Yosemite | MIWUK 1701 | 163661701 | Feeder | None | None | None | 37.9% | 0 | 0% | 12.98 | 4.92 | 37.9% | 0 | 0% | 12.98 | 4.87 | 37.52% | 0 | 0% | 12.98 | 4.84 | 37.29% | 0 | 0% | 12.98 | 4.83 | 37.21% | 0 | 0% | 12.98 | 4.88 | 37.6% | 0 | 0%
GNA_163661702_Capacity | Central Valley | Yosemite | MIWUK 1702 | 163661702 | Feeder | None | None | None | 54.58% | 0 | 0% | 12.33 | 6.73 | 54.58% | 0 | 0% | 12.33 | 6.61 | 53.61% | 0 | 0% | 12.33 | 6.54 | 53.04% | 0 | 0% | 12.33 | 6.47 | 52.47% | 0 | 0% | 12.33 | 6.46 | 52.39% | 0 | 0%
GNA_1637801_Capacity | Central Valley | Yosemite | PEORIA BANK 1 | 1637801 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_163781701_Capacity | Central Valley | Yosemite | PEORIA FLAT 1701 | 163781701 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1637802_Capacity | Central Valley | Yosemite | PEORIA BANK 2 | 1637802 | Bank | None | None | None | 58.79% | 0 | 0% | 44.5 | 25.03 | 56.25% | 0 | 0% | 44.5 | 24.92 | 56% | 0 | 0% | 44.5 | 26.16 | 58.79% | 0 | 0% | 44.5 | 26.05 | 58.54% | 0 | 0% | 44.5 | 25.99 | 58.4% | 0 | 0%
GNA_163781704_Capacity | Central Valley | Yosemite | PEORIA FLAT 1704 | 163781704 | Feeder | Demand Growth | Capacity | 2023 | 108.3% | 1.2 | 8.322% | 14.42 | 14.97 | 103.8% | 0.55 | 3.814% | 14.42 | 14.82 | 102.8% | 0.4 | 2.774% | 14.42 | 15.62 | 108.3% | 1.2 | 8.322% | 14.42 | 15.52 | 107.6% | 1.1 | 7.628% | 14.42 | 15.47 | 107.3% | 1.05 | 7.282%
GNA_163781705_Capacity | Central Valley | Yosemite | PEORIA FLAT 1705 | 163781705 | Feeder | None | None | None | 65.74% | 0 | 0% | 14.42 | 9.48 | 65.74% | 0 | 0% | 14.42 | 9.39 | 65.12% | 0 | 0% | 14.42 | 9.27 | 64.29% | 0 | 0% | 14.42 | 9.21 | 63.87% | 0 | 0% | 14.42 | 9.19 | 63.73% | 0 | 0%
GNA_1637601_Capacity | Central Valley | Yosemite | RACETRACK BANK 1 | 1637601 | Bank | None | None | None | 97.1% | 0 | 0% | 15.84 | 15.38 | 97.1% | 0 | 0% | 15.84 | 15.25 | 96.28% | 0 | 0% | 15.84 | 15.12 | 95.45% | 0 | 0% | 15.84 | 15.01 | 94.76% | 0 | 0% | 15.84 | 14.96 | 94.44% | 0 | 0%
GNA_163761703_Capacity | Central Valley | Yosemite | RACETRACK 1703 | 163761703 | Feeder | None | None | None | 86.62% | 0 | 0% | 15.84 | 13.72 | 86.62% | 0 | 0% | 15.84 | 13.57 | 85.67% | 0 | 0% | 15.84 | 13.38 | 84.47% | 0 | 0% | 15.84 | 13.29 | 83.9% | 0 | 0% | 15.84 | 13.26 | 83.71% | 0 | 0%
GNA_163761704_Capacity | Central Valley | Yosemite | RACETRACK 1704 | 163761704 | Feeder | None | None | None | 11.36% | 0 | 0% | 15.84 | 1.8 | 11.36% | 0 | 0% | 15.84 | 1.8 | 11.36% | 0 | 0% | 15.84 | 1.8 | 11.36% | 0 | 0% | 15.84 | 1.79 | 11.3% | 0 | 0% | 15.84 | 1.8 | 11.36% | 0 | 0%
GNA_162831702_Capacity | Central Valley | Yosemite | SPRING GAP 1702 | 162831702 | Feeder | None | None | None | 43.74% | 0 | 0% | 4.39 | 1.88 | 42.82% | 0 | 0% | 4.39 | 1.88 | 42.82% | 0 | 0% | 4.39 | 1.88 | 42.82% | 0 | 0% | 4.39 | 1.89 | 43.05% | 0 | 0% | 4.39 | 1.92 | 43.74% | 0 | 0%
GNA_1631601_Capacity | Central Valley | Yosemite | PINECREST BANK 1 | 1631601 | Bank | None | None | None | 48.21% | 0 | 0% | 0.56 | 0.24 | 42.86% | 0 | 0% | 0.56 | 0.24 | 42.86% | 0 | 0% | 0.56 | 0.24 | 42.86% | 0 | 0% | 0.56 | 0.25 | 44.64% | 0 | 0% | 0.56 | 0.27 | 48.21% | 0 | 0%
GNA_163160401_Capacity | Central Valley | Yosemite | PINECREST 0401 | 163160401 | Feeder | None | None | None | 45.76% | 0 | 0% | 0.59 | 0.24 | 40.68% | 0 | 0% | 0.59 | 0.24 | 40.68% | 0 | 0% | 0.59 | 0.24 | 40.68% | 0 | 0% | 0.59 | 0.25 | 42.37% | 0 | 0% | 0.59 | 0.27 | 45.76% | 0 | 0%
GNA_2553901_Capacity | Central Valley | Yosemite | BONITA BANK 1 | 2553901 | Bank | Demand Growth | Capacity | 2023 | 169.8% | 10.97 | 69.78% | 15.72 | 19.77 | 125.8% | 4.05 | 25.76% | 15.72 | 24.69 | 157.1% | 8.97 | 57.06% | 15.72 | 26.62 | 169.3% | 10.9 | 69.34% | 15.72 | 26.64 | 169.5% | 10.92 | 69.47% | 15.72 | 26.69 | 169.8% | 10.97 | 69.78%
GNA_255391101_Capacity | Central Valley | Yosemite | BONITA 1101 | 255391101 | Feeder | None | None | None | 97.19% | 0 | 0% | 9.62 | 9.35 | 97.19% | 0 | 0% | 9.62 | 9.35 | 97.19% | 0 | 0% | 9.62 | 9.35 | 97.19% | 0 | 0% | 9.62 | 9.35 | 97.19% | 0 | 0% | 9.62 | 9.35 | 97.19% | 0 | 0%
GNA_255391102_Capacity | Central Valley | Yosemite | BONITA 1102 | 255391102 | Feeder | Demand Growth | Capacity | 2024 | 142.4% | 4.08 | 42.41% | 9.62 | 6.61 | 68.71% | 0 | 0% | 9.62 | 11.64 | 121% | 2.02 | 21% | 9.62 | 13.62 | 141.6% | 4 | 41.58% | 9.62 | 13.65 | 141.9% | 4.03 | 41.89% | 9.62 | 13.7 | 142.4% | 4.08 | 42.41%
GNA_255391103_Capacity | Central Valley | Yosemite | BONITA 1103 | 255391103 | Feeder | None | None | None | 75.99% | 0 | 0% | 9.62 | 7.31 | 75.99% | 0 | 0% | 9.62 | 7.31 | 75.99% | 0 | 0% | 9.62 | 7.29 | 75.78% | 0 | 0% | 9.62 | 7.28 | 75.68% | 0 | 0% | 9.62 | 7.28 | 75.68% | 0 | 0%
GNA_2551202_Capacity | Central Valley | Yosemite | BORDEN BANK 2 | 2551202 | Bank | Demand Growth | Capacity | 2024 | 106.5% | 1.92 | 6.465% | 29.7 | 29.38 | 98.92% | 0 | 0% | 29.7 | 30.76 | 103.6% | 1.06 | 3.569% | 29.7 | 31.27 | 105.3% | 1.57 | 5.286% | 29.7 | 31.43 | 105.8% | 1.73 | 5.825% | 29.7 | 31.62 | 106.5% | 1.92 | 6.465%
GNA_255121101_Capacity | Central Valley | Yosemite | BORDEN 1101 | 255121101 | Feeder | Demand Growth | Capacity | 2023 | 106% | 0.8 | 6.033% | 13.26 | 13.95 | 105.2% | 0.69 | 5.204% | 13.26 | 13.95 | 105.2% | 0.69 | 5.204% | 13.26 | 13.95 | 105.2% | 0.69 | 5.204% | 13.26 | 14 | 105.6% | 0.74 | 5.581% | 13.26 | 14.06 | 106% | 0.8 | 6.033%
GNA_255121102_Capacity | Central Valley | Yosemite | BORDEN 1102 | 255121102 | Feeder | None | None | None | 77.15% | 0 | 0% | 13.26 | 8.24 | 62.14% | 0 | 0% | 13.26 | 9.5 | 71.64% | 0 | 0% | 13.26 | 10 | 75.41% | 0 | 0% | 13.26 | 10.1 | 76.17% | 0 | 0% | 13.26 | 10.23 | 77.15% | 0 | 0%
GNA_255121103_Capacity | Central Valley | Yosemite | BORDEN 1103 | 255121103 | Feeder | None | None | None | 89.29% | 0 | 0% | 13.26 | 11.74 | 88.54% | 0 | 0% | 13.26 | 11.84 | 89.29% | 0 | 0% | 13.26 | 11.83 | 89.22% | 0 | 0% | 13.26 | 11.83 | 89.22% | 0 | 0% | 13.26 | 11.83 | 89.22% | 0 | 0%
GNA_2539801_Capacity | Central Valley | Yosemite | EL PECO BANK 1 | 2539801 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_253981102_Capacity | Central Valley | Yosemite | EL PECO 1102 | 253981102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2539802_Capacity | Central Valley | Yosemite | EL PECO BANK 2 | 2539802 | Bank | None | None | None | 100.4% | 0.06 | 0.3785% | 15.85 | 15.91 | 100.4% | 0.06 | 0.3785% | 15.85 | 15.88 | 100.2% | 0.03 | 0.1893% | 15.85 | 15.85 | 100% | 0 | 0% | 15.85 | 15.84 | 99.94% | 0 | 0% | 15.85 | 15.82 | 99.81% | 0 | 0%
GNA_253981105_Capacity | Central Valley | Yosemite | EL PECO 1105 | 253981105 | Feeder | None | None | None | 98.13% | 0 | 0% | 12.83 | 12.59 | 98.13% | 0 | 0% | 12.83 | 12.57 | 97.97% | 0 | 0% | 12.83 | 12.56 | 97.9% | 0 | 0% | 12.83 | 12.55 | 97.82% | 0 | 0% | 12.83 | 12.52 | 97.58% | 0 | 0%
GNA_253981106_Capacity | Central Valley | Yosemite | EL PECO 1106 | 253981106 | Feeder | None | None | None | 44.26% | 0 | 0% | 10.46 | 4.63 | 44.26% | 0 | 0% | 10.46 | 4.62 | 44.17% | 0 | 0% | 10.46 | 4.6 | 43.98% | 0 | 0% | 10.46 | 4.61 | 44.07% | 0 | 0% | 10.46 | 4.61 | 44.07% | 0 | 0%
GNA_2527601_Capacity | Central Valley | Yosemite | MADERA BANK 1 | 2527601 | Bank | Demand Growth | Capacity | 2023 | 114.9% | 4 | 14.93% | 26.8 | 29.67 | 110.7% | 2.87 | 10.71% | 26.8 | 30.77 | 114.8% | 3.97 | 14.81% | 26.8 | 30.76 | 114.8% | 3.96 | 14.78% | 26.8 | 30.78 | 114.9% | 3.98 | 14.85% | 26.8 | 30.8 | 114.9% | 4 | 14.93%
GNA_252761112_Capacity | Central Valley | Yosemite | MADERA 1112 | 252761112 | Feeder | Demand Growth | Capacity | 2023 | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_252761114_Capacity | Central Valley | Yosemite | MADERA 1114 | 252761114 | Feeder | None | None | None | 95.98% | 0 | 0% | 10.46 | 10.04 | 95.98% | 0 | 0% | 10.46 | 10.01 | 95.7% | 0 | 0% | 10.46 | 9.95 | 95.12% | 0 | 0% | 10.46 | 9.89 | 94.55% | 0 | 0% | 10.46 | 9.85 | 94.17% | 0 | 0%
GNA_252761116_Capacity | Central Valley | Yosemite | MADERA 1116 | 252761116 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_2527602_Capacity | Central Valley | Yosemite | MADERA BANK 2 | 2527602 | Bank | Demand Growth | Capacity | 2026 | 121.8% | 4.3 | 21.77% | 19.75 | 19.29 | 97.67% | 0 | 0% | 19.75 | 18.64 | 94.38% | 0 | 0% | 19.75 | 19.5 | 98.73% | 0 | 0% | 19.75 | 21.26 | 107.6% | 1.51 | 7.646% | 19.75 | 24.05 | 121.8% | 4.3 | 21.77%
GNA_252761104_Capacity | Central Valley | Yosemite | MADERA 1104 | 252761104 | Feeder | None | None | None | 72.19% | 0 | 0% | 12.19 | 8.8 | 72.19% | 0 | 0% | 12.19 | 8.68 | 71.21% | 0 | 0% | 12.19 | 8.61 | 70.63% | 0 | 0% | 12.19 | 8.6 | 70.55% | 0 | 0% | 12.19 | 8.62 | 70.71% | 0 | 0%
GNA_252761106_Capacity | Central Valley | Yosemite | MADERA 1106 | 252761106 | Feeder | Demand Growth | Capacity | 2026 | 133.7% | 3.93 | 33.68% | 11.67 | 10.3 | 88.26% | 0 | 0% | 11.67 | 9.73 | 83.38% | 0 | 0% | 11.67 | 10.83 | 92.8% | 0 | 0% | 11.67 | 12.88 | 110.4% | 1.21 | 10.37% | 11.67 | 15.6 | 133.7% | 3.93 | 33.68%
GNA_2527603_Capacity | Central Valley | Yosemite | MADERA BANK 3 | 2527603 | Bank | None | None | None | 69.7% | 0 | 0% | 29.7 | 20.58 | 69.29% | 0 | 0% | 29.7 | 20.51 | 69.06% | 0 | 0% | 29.7 | 20.43 | 68.79% | 0 | 0% | 29.7 | 20.49 | 68.99% | 0 | 0% | 29.7 | 20.7 | 69.7% | 0 | 0%
GNA_252761118_Capacity | Central Valley | Yosemite | MADERA 1118 | 252761118 | Feeder | None | None | None | 89.54% | 0 | 0% | 13.19 | 11.81 | 89.54% | 0 | 0% | 13.19 | 11.7 | 88.7% | 0 | 0% | 13.19 | 11.6 | 87.95% | 0 | 0% | 13.19 | 11.52 | 87.34% | 0 | 0% | 13.19 | 11.54 | 87.49% | 0 | 0%
GNA_252761119_Capacity | Central Valley | Yosemite | MADERA 1119 | 252761119 | Feeder | None | None | None | 98.94% | 0 | 0% | 13.19 | 12.68 | 96.13% | 0 | 0% | 13.19 | 12.77 | 96.82% | 0 | 0% | 13.19 | 12.85 | 97.42% | 0 | 0% | 13.19 | 12.94 | 98.1% | 0 | 0% | 13.19 | 13.05 | 98.94% | 0 | 0%
GNA_2546101_Capacity | Central Valley | Yosemite | STOREY BANK 1 | 2546101 | Bank | Demand Growth | Capacity | 2027 | 102.3% | 1.01 | 2.265% | 44.6 | 40.91 | 91.73% | 0 | 0% | 44.6 | 42.52 | 95.34% | 0 | 0% | 44.6 | 43.31 | 97.11% | 0 | 0% | 44.6 | 44.3 | 99.33% | 0 | 0% | 44.6 | 45.61 | 102.3% | 1.01 | 2.265%
GNA_254611104_Capacity | Central Valley | Yosemite | STOREY 1104 | 254611104 | Feeder | Demand Growth | Capacity | 2023 | 121% | 3.02 | 20.96% | 14.41 | 15.92 | 110.5% | 1.51 | 10.48% | 14.41 | 16.65 | 115.5% | 2.24 | 15.54% | 14.41 | 17.15 | 119% | 2.74 | 19.01% | 14.41 | 17.29 | 120% | 2.88 | 19.99% | 14.41 | 17.43 | 121% | 3.02 | 20.96%
GNA_254611105_Capacity | Central Valley | Yosemite | STOREY 1105 | 254611105 | Feeder | Demand Growth | Capacity | 2023 | 123.6% | 3.21 | 23.6% | 13.6 | 14.11 | 103.8% | 0.51 | 3.75% | 13.6 | 14.57 | 107.1% | 0.97 | 7.132% | 13.6 | 14.58 | 107.2% | 0.98 | 7.206% | 13.6 | 15.44 | 113.5% | 1.84 | 13.53% | 13.6 | 16.81 | 123.6% | 3.21 | 23.6%
GNA_254611106_Capacity | Central Valley | Yosemite | STOREY 1106 | 254611106 | Feeder | Demand Growth | Capacity | 2023 | 104.9% | 0.6 | 4.922% | 12.19 | 12.65 | 103.8% | 0.46 | 3.774% | 12.19 | 12.7 | 104.2% | 0.51 | 4.184% | 12.19 | 12.75 | 104.6% | 0.56 | 4.594% | 12.19 | 12.79 | 104.9% | 0.6 | 4.922% | 12.19 | 12.76 | 104.7% | 0.57 | 4.676%
GNA_2546102_Capacity | Central Valley | Yosemite | STOREY BANK 2 | 2546102 | Bank | Demand Growth | Capacity | 2023 | 121.1% | 9.38 | 21.08% | 44.5 | 53.88 | 121.1% | 9.38 | 21.08% | 44.5 | 53.64 | 120.5% | 9.14 | 20.54% | 44.5 | 53.43 | 120.1% | 8.93 | 20.07% | 44.5 | 53.3 | 119.8% | 8.8 | 19.78% | 44.5 | 53.3 | 119.8% | 8.8 | 19.78%
GNA_254611107_Capacity | Central Valley | Yosemite | STOREY 1107 | 254611107 | Feeder | Demand Growth | Capacity | 2023 | 114.2% | 1.73 | 14.19% | 12.19 | 13.92 | 114.2% | 1.73 | 14.19% | 12.19 | 13.9 | 114% | 1.71 | 14.03% | 12.19 | 13.87 | 113.8% | 1.68 | 13.78% | 12.19 | 13.84 | 113.5% | 1.65 | 13.54% | 12.19 | 13.83 | 113.5% | 1.64 | 13.45%
GNA_254611108_Capacity | Central Valley | Yosemite | STOREY 1108 | 254611108 | Feeder | Demand Growth | Capacity | 2023 | 103.6% | 0.48 | 3.634% | 13.21 | 13.47 | 102% | 0.26 | 1.968% | 13.21 | 13.51 | 102.3% | 0.3 | 2.271% | 13.21 | 13.55 | 102.6% | 0.34 | 2.574% | 13.21 | 13.62 | 103.1% | 0.41 | 3.104% | 13.21 | 13.69 | 103.6% | 0.48 | 3.634%
GNA_254611109_Capacity | Central Valley | Yosemite | STOREY 1109 | 254611109 | Feeder | Demand Growth | Capacity | 2023 | 115.4% | 2.03 | 15.37% | 13.21 | 15.21 | 115.1% | 2 | 15.14% | 13.21 | 15.19 | 115% | 1.98 | 14.99% | 13.21 | 15.18 | 114.9% | 1.97 | 14.91% | 13.21 | 15.2 | 115.1% | 1.99 | 15.06% | 13.21 | 15.24 | 115.4% | 2.03 | 15.37%
GNA_254611111_Capacity | Central Valley | Yosemite | STOREY 1111 | 254611111 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1626701_Capacity | Central Valley | Yosemite | WESTLEY BANK 1 | 1626701 | Bank | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_162671101_Capacity | Central Valley | Yosemite | WESTLEY 1101 | 162671101 | Feeder | None | None | None | 94.36% | 0 | 0% | 10.46 | 9.87 | 94.36% | 0 | 0% | 10.46 | 9.86 | 94.26% | 0 | 0% | 10.46 | 9.86 | 94.26% | 0 | 0% | 10.46 | 9.86 | 94.26% | 0 | 0% | 10.46 | 9.86 | 94.26% | 0 | 0%
GNA_162671102_Capacity | Central Valley | Yosemite | WESTLEY 1102 | 162671102 | Feeder | None | None | None | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC | CC
GNA_1626702_Capacity | Central Valley | Yosemite | WESTLEY BANK 2 | 1626702 | Bank | None | None | None | 79.87% | 0 | 0% | 15.8 | 12.62 | 79.87% | 0 | 0% | 15.8 | 12.6 | 79.75% | 0 | 0% | 15.8 | 12.58 | 79.62% | 0 | 0% | 15.8 | 12.58 | 79.62% | 0 | 0% | 15.8 | 12.61 | 79.81% | 0 | 0%
GNA_162671103_Capacity | Central Valley | Yosemite | WESTLEY 1103 | 162671103 | Feeder | None | None | None | 84.17% | 0 | 0% | 12.19 | 10.26 | 84.17% | 0 | 0% | 12.19 | 10.24 | 84% | 0 | 0% | 12.19 | 10.22 | 83.84% | 0 | 0% | 12.19 | 10.22 | 83.84% | 0 | 0% | 12.19 | 10.25 | 84.09% | 0 | 0%
GNA_0120199_Capacity | Bay Area | East Bay | OAKLAND C GROUP 1,2,3,10 | 120199 | BankGroup | None | None | None | 62.19% | 0 | 0% | 133.62 | 79.86 | 59.77% | 0 | 0% | 133.62 | 82.23 | 61.54% | 0 | 0% | 133.62 | 82.34 | 61.62% | 0 | 0% | 133.62 | 82.68 | 61.88% | 0 | 0% | 133.62 | 83.1 | 62.19% | 0 | 0%
GNA_0121199_Capacity | Bay Area | East Bay | OAKLAND L GROUP 1,3,5 | 121199 | BankGroup | None | None | None | 100.1% | 0.04 | 0.05195% | 77 | 75.59 | 98.17% | 0 | 0% | 77 | 77.04 | 100.1% | 0.04 | 0.05195% | 77 | 77 | 100% | 0 | 0% | 77 | 76.92 | 99.9% | 0 | 0% | 77 | 76.98 | 99.97% | 0 | 0%
GNA_0228799_Capacity | Bay Area | San Francisco | EMBARCADERO Z GROUP 1,5 | 228799 | BankGroup | None | None | None | 51.02% | 0 | 0% | 227.8 | 116.02 | 50.93% | 0 | 0% | 227.8 | 116.22 | 51.02% | 0 | 0% | 227.8 | 115.86 | 50.86% | 0 | 0% | 227.8 | 115.76 | 50.82% | 0 | 0% | 227.8 | 115.89 | 50.87% | 0 | 0%
GNA_0228798_Capacity | Bay Area | San Francisco | EMBARCADERO Z GROUP 11,15,16 | 228798 | BankGroup | None | None | None | 53.23% | 0 | 0% | 139.9 | 74.25 | 53.07% | 0 | 0% | 139.9 | 74.47 | 53.23% | 0 | 0% | 139.9 | 74.11 | 52.97% | 0 | 0% | 139.9 | 74.03 | 52.92% | 0 | 0% | 139.9 | 74.16 | 53.01% | 0 | 0%
GNA_0228796_Capacity | Bay Area | San Francisco | EMBARCADERO Z GROUP 2,3 | 228796 | BankGroup | None | None | None | 42.04% | 0 | 0% | 297 | 124.03 | 41.76% | 0 | 0% | 297 | 124.86 | 42.04% | 0 | 0% | 297 | 124.44 | 41.9% | 0 | 0% | 297 | 124.26 | 41.84% | 0 | 0% | 297 | 124.31 | 41.86% | 0 | 0%
GNA_0228797_Capacity | Bay Area | San Francisco | EMBARCADERO Z GROUP 12,13,14 | 228797 | BankGroup | None | None | None | 49.27% | 0 | 0% | 164.35 | 80.11 | 48.74% | 0 | 0% | 164.35 | 80.97 | 49.27% | 0 | 0% | 164.35 | 80.59 | 49.04% | 0 | 0% | 164.35 | 80.41 | 48.93% | 0 | 0% | 164.35 | 80.46 | 48.96% | 0 | 0%
GNA_0228099_Capacity | Bay Area | San Francisco | LARKIN Y GROUP 1,3,5 | 228099 | BankGroup | None | None | None | 47.2% | 0 | 0% | 203.1 | 95.87 | 47.2% | 0 | 0% | 203.1 | 91.63 | 45.12% | 0 | 0% | 203.1 | 93.51 | 46.04% | 0 | 0% | 203.1 | 93.71 | 46.14% | 0 | 0% | 203.1 | 94.26 | 46.41% | 0 | 0%
GNA_0228098_Capacity | Bay Area | San Francisco | LARKIN Y GROUP 2,4,6 | 228098 | BankGroup | None | None | None | 55.68% | 0 | 0% | 183.3 | 96.53 | 52.66% | 0 | 0% | 183.3 | 102.07 | 55.68% | 0 | 0% | 183.3 | 101.45 | 55.35% | 0 | 0% | 183.3 | 101.58 | 55.42% | 0 | 0% | 183.3 | 101.96 | 55.62% | 0 | 0%
GNA_0220199_Capacity | Bay Area | San Francisco | MISSION X GROUP 1,2,3,4,5,6 | 220199 | BankGroup | None | None | None | 57.62% | 0 | 0% | 371.5 | 207.65 | 55.9% | 0 | 0% | 371.5 | 209.39 | 56.36% | 0 | 0% | 371.5 | 208.88 | 56.23% | 0 | 0% | 371.5 | 210.08 | 56.55% | 0 | 0% | 371.5 | 214.06 | 57.62% | 0 | 0%
GNA_2544201_Capacity | Central Valley | Yosemite | OAKHURST GROUP 1a,1b | 2544201 | BankGroup | Demand Growth | Capacity | 2023 | 101% | 0.12 | 1.012% | 11.86 | 11.98 | 101% | 0.12 | 1.012% | 11.86 | 11.86 | 100% | 0 | 0% | 11.86 | 11.74 | 98.99% | 0 | 0% | 11.86 | 11.68 | 98.48% | 0 | 0% | 11.86 | 11.69 | 98.57% | 0 | 0%
* Note: For the grid needs at Logan Creek Bank 1 and Logan Creek 2101, an existing large industrial customer has dropped their need for services. Given this, the Logan Bank 1 is no longer showing a grid need. The load can now be served via having the load transferred to Logan Creek 2102 and undergoing line section work. As the in service date will be in 2025, this will be listed as a planned investment in the November filing but not considered as a candidate deferral opportunity.